2016-08-22 | 257324 | DTPC-111214 | escort Central Air to 3-19 ac, and leak check. | 2016-08-22 - 18010 - Robert Bartels-Escort, assist with leak check, need another estimate to fix - Robert Bartels | escort Central Air to 3-19 ac, and leak check. 2016-08-22 - 18010 - Robert Bartels-Escort, assist with leak check, need another estimate to fix - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 67936 | TMPE-182222 | MWO INTDSB B350A After being closed up all summer we discovered water damage along the wall under the window in INTDSB 350A. There is a crack and what looks like a bubble under the paint that then collapsed - see attached photo. Can someone check to see if it is safe? and if not what would need t. . . | 2016-09-15 - 13140 - Reuben Bilducia-Completed i investigated the damage on wall pulled out old air vents on top of window ledge i did not find an entry point for moisture. it may be ductwork in wall sweating with condensate when we have high humidity.Wall needs repair and paint. - Reuben Bilducia; 2016-09-27 - 13140 - Reuben Bilducia-Needs to be turned over to paint shop and carpentry. - Reuben Bilducia | MWO INTDSB B350A After being closed up all summer we discovered water damage along the wall under the window in INTDSB 350A. There is a crack and what looks like a bubble under the paint that then collapsed - see attached photo. Can someone check to see if it is safe? and if not what would need t. . . 2016-09-15 - 13140 - Reuben Bilducia-Completed i investigated the damage on wall pulled out old air vents on top of window ledge i did not find an entry point for moisture. it may be ductwork in wall sweating with condensate when we have high humidity.Wall needs repair and paint. - Reuben Bilducia; 2016-09-27 - 13140 - Reuben Bilducia-Needs to be turned over to paint shop and carpentry. - Reuben Bilducia | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 67950 | TMPE-182208 | MWO: ADD FIRE TECH: We will be doing some metal cutting and need devices disabled. ***ORIGINAL REQUEST***!! The AC unit located near A212 has a very loud vibration as if something is loose. The vibration can be felt and heard in the hallway and within A212. Please have someone from HVAC ch. . . | 2016-08-29 - 17000 - Kevin Cunningham-Was requested by AC shop to see if there were any fire alarm devices in or around area of work that needed to be disabled. There were not. - Kevin Cunningham | MWO: ADD FIRE TECH: We will be doing some metal cutting and need devices disabled. ***ORIGINAL REQUEST***!! The AC unit located near A212 has a very loud vibration as if something is loose. The vibration can be felt and heard in the hallway and within A212. Please have someone from HVAC ch. . . 2016-08-29 - 17000 - Kevin Cunningham-Was requested by AC shop to see if there were any fire alarm devices in or around area of work that needed to be disabled. There were not. - Kevin Cunningham | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 67979 | TMPE-182179 | MWO: A/C is leaking causing a water puddle in 107U1. Please check the temperature in Room 107A also. It should be cooler than 80 degrees. | 2016-08-23 - 18010 - Called Steve. Directed me to assign request to HVAC - Michelle Ryan; 2016-08-25 - 18010 - Gail Jackson-Trouble shoot condensate pumps, found 1 bad and 1 missing, trip to Grainger for replacements. - Gail Jackson; 2016-08-25 - 18010 - Thomas Gibble-Trouble shoot condensate pumps, found 1 bad and 1 missing, trip to Grainger for replacements. - Gail Jackson; 2016-08-25 - 18010 - Gail Jackson-replaced two pumps - Thomas Gibble | MWO: A/C is leaking causing a water puddle in 107U1. Please check the temperature in Room 107A also. It should be cooler than 80 degrees. 2016-08-23 - 18010 - Called Steve. Directed me to assign request to HVAC - Michelle Ryan; 2016-08-25 - 18010 - Gail Jackson-Trouble shoot condensate pumps, found 1 bad and 1 missing, trip to Grainger for replacements. - Gail Jackson; 2016-08-25 - 18010 - Thomas Gibble-Trouble shoot condensate pumps, found 1 bad and 1 missing, trip to Grainger for replacements. - Gail Jackson; 2016-08-25 - 18010 - Gail Jackson-replaced two pumps - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-23 | 67986 | TMPE-182172 | MWO: GWC 181 is now a conference room for the Center for Bio-mediated and Bio-inspired Geotechnics (which is not listed in your Department list above). The air conditioning unit in GWC 181 is extremely noisy, distracting you when you're trying to conduct business in that room, or teleconference in . . . | 2016-11-18 - 18010 - Mitchell Andrews-used isolators on the air handler to stop vibrating - Mitchell Andrews | MWO: GWC 181 is now a conference room for the Center for Bio-mediated and Bio-inspired Geotechnics (which is not listed in your Department list above). The air conditioning unit in GWC 181 is extremely noisy, distracting you when you're trying to conduct business in that room, or teleconference in . . . 2016-11-18 - 18010 - Mitchell Andrews-used isolators on the air handler to stop vibrating - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 67993 | TMPE-182165 | SWO BKSTR EL transfer to AC: fuses are blown because the bearings on the motor are going bad add EL shop: at the motor control center there are 2 blown fuses # A6D10R at AH 5 The entire east side of the store's air handler is not turning on at all. The other air handler on the west side is no. . . | NA | SWO BKSTR EL transfer to AC: fuses are blown because the bearings on the motor are going bad add EL shop: at the motor control center there are 2 blown fuses # A6D10R at AH 5 The entire east side of the store's air handler is not turning on at all. The other air handler on the west side is no. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-23 | 67995 | TMPE-182163 | MWO: L&L - 150: There is a ceiling leak in the classroom. | 2016-08-24 - 23000 - Anthony Perez-Tony Perez- transfer Installed trash can at leak. Found leak upstairs in 250u1 ac system. also checked in ceiling and. will need to go back and fix ceiling tiles. Will use other work order to put in time for ceiling tile. 1.25 hours Materials- none - Anthony Perez | MWO: L&L - 150: There is a ceiling leak in the classroom. 2016-08-24 - 23000 - Anthony Perez-Tony Perez- transfer Installed trash can at leak. Found leak upstairs in 250u1 ac system. also checked in ceiling and. will need to go back and fix ceiling tiles. Will use other work order to put in time for ceiling tile. 1.25 hours Materials- none - Anthony Perez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 68007 | TMPE-182151 | MWO: BT to HVAC I checked 5 air handlers also the chiller I could smell the odor but couldn\\u2019t find it. ORIG REQUEST !! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above it state 301 is non-ASU, but our department. . . | NA | MWO: BT to HVAC I checked 5 air handlers also the chiller I could smell the odor but couldn\\u2019t find it. ORIG REQUEST !! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above it state 301 is non-ASU, but our department. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-23 | 68065 | TMPE-182093 | MWO: BT TO HVAC: COULD YOU SEND HVAC TO CHECK THE UNITS ON THE ROOF? THE SMELL WAS ON THE 2ND & 3RD FLOOR BUT STRONGER ON THE 3RD FLOOR. ***ORIGINAL REQUEST***!! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above . . . | 2016-08-23 - 18020 - CALLED TO BRIAN Q. - Monica Moraga; 2016-09-02 - 18020 - Oner Munoz-Investigated all three floors and found no smells coming from any ac unit. - Oner Munoz; 2016-09-02 - 18020 - Robert Ecabert-Investigated all three floors and found no smells coming from any ac unit. - Oner Munoz | MWO: BT TO HVAC: COULD YOU SEND HVAC TO CHECK THE UNITS ON THE ROOF? THE SMELL WAS ON THE 2ND & 3RD FLOOR BUT STRONGER ON THE 3RD FLOOR. ***ORIGINAL REQUEST***!! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above . . . 2016-08-23 - 18020 - CALLED TO BRIAN Q. - Monica Moraga; 2016-09-02 - 18020 - Oner Munoz-Investigated all three floors and found no smells coming from any ac unit. - Oner Munoz; 2016-09-02 - 18020 - Robert Ecabert-Investigated all three floors and found no smells coming from any ac unit. - Oner Munoz | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 68072 | TMPE-182086 | MWO: OLD MAIN 139 In the main Data Center the display on CRAC Unit #6127 reads "loss of water". Please send someone to check on this asap. | 2017-02-07 - 18010 - Gail Jackson-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-07 - 18010 - Thomas Gibble-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-07 - 18010 - Thomas Gibble-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-14 - 18010 - Thomas Gibble-flushed coil with coil cleaner - Thomas Gibble; 2017-02-14 - 18010 - Gail Jackson-flushed coil with coil cleaner - Thomas Gibble | MWO: OLD MAIN 139 In the main Data Center the display on CRAC Unit #6127 reads "loss of water". Please send someone to check on this asap. 2017-02-07 - 18010 - Gail Jackson-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-07 - 18010 - Thomas Gibble-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-07 - 18010 - Thomas Gibble-Set up Goodway Coil Machine transport to basement. No water or drainage access in basement, has to be carried in and out in buckets. Ran cleaner through coil 4 hours; very dirty. Flushed out coil, very dirty; would think heat exchange needs cleaned; this needs to be a least annual with all grime in system. Lieberts still on heat exchange, back up chiller has not ran for years, central plant provides cooling. - Gail Jackson; 2017-02-14 - 18010 - Thomas Gibble-flushed coil with coil cleaner - Thomas Gibble; 2017-02-14 - 18010 - Gail Jackson-flushed coil with coil cleaner - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 68082 | TMPE-182076 | SWO BKSTR add EL shop: at the motor control center there are 2 blown fuses # A6D10R at AH 5 The entire east side of the store's air handler is not turning on at all. The other air handler on the west side is not cooling efficiently. | 2016-08-23 - 15010 - Gary Conover-Troubleshot motor control circuit and line circuit. Found motor bearings making loud noise believe they are bad. Turned over to HVAC shop - Gary Conover; 2016-08-24 - 15010 - Gary Conover-Bought fuses - Gary Conover | SWO BKSTR add EL shop: at the motor control center there are 2 blown fuses # A6D10R at AH 5 The entire east side of the store's air handler is not turning on at all. The other air handler on the west side is not cooling efficiently. 2016-08-23 - 15010 - Gary Conover-Troubleshot motor control circuit and line circuit. Found motor bearings making loud noise believe they are bad. Turned over to HVAC shop - Gary Conover; 2016-08-24 - 15010 - Gary Conover-Bought fuses - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-23 | 68105 | TMPE-182053 | MWO CPCOM BLDG EL TO HVAC: IN THE SOUTH BASEMENT, 2 OF THE LIEBERT UNITS ARE DEAD. THE BREAKERS OVERHEATED AND CAUSED THE POWER OUTAGE. PLEASE SEND HVAC BEFORE WE LOSE POWER AGAIN. ***ORIGINAL REQUEST***!! Lights wouldn't turn on in the caf\\xe9 area. Seems like there's no power. 4NNE49C | 2016-08-23 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-08-24 - 18010 - Gail Jackson-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson; 2016-08-24 - 18010 - Zhi Yu-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson; 2016-08-24 - 18010 - Thomas Gibble-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson | MWO CPCOM BLDG EL TO HVAC: IN THE SOUTH BASEMENT, 2 OF THE LIEBERT UNITS ARE DEAD. THE BREAKERS OVERHEATED AND CAUSED THE POWER OUTAGE. PLEASE SEND HVAC BEFORE WE LOSE POWER AGAIN. ***ORIGINAL REQUEST***!! Lights wouldn't turn on in the caf\\xe9 area. Seems like there's no power. 4NNE49C 2016-08-23 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-08-24 - 18010 - Gail Jackson-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson; 2016-08-24 - 18010 - Zhi Yu-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson; 2016-08-24 - 18010 - Thomas Gibble-Found both units low charge, leaks in evap. coils. Added 1 lb R22 to unit on right and 7 lbs to unit on left leaking core and swivel tee replaced. Units are 1989 models , 26 years old in need of replacement, past useful life. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-08-23 | 68120 | TMPE-182038 | MWO: !! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above it state 301 is non-ASU, but our department is part of ASU. Thank you! 42CAE8J | 2016-08-23 - 18020 - CALLED TO BT JEFF A. - Monica Moraga; 2016-08-23 - 18020 - Jeffery Armstrong-Transfer to. HVAC I looked at 5 air handlers &amp; the chiller. I could smell the odor but not find the source. - Jeffery Armstrong | MWO: !! The AC vents, especially the vent near desk 301CJ has a burning smell. Can you please send someone to come take a look? Also, above it state 301 is non-ASU, but our department is part of ASU. Thank you! 42CAE8J 2016-08-23 - 18020 - CALLED TO BT JEFF A. - Monica Moraga; 2016-08-23 - 18020 - Jeffery Armstrong-Transfer to. HVAC I looked at 5 air handlers &amp; the chiller. I could smell the odor but not find the source. - Jeffery Armstrong | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-23 | 68126 | TMPE-182032 | MWO: Ceiling leak at LSA room 311. Add CA: possible roof repair needed PL transfer to AC: 2 AC units on the roof with water, needs to be vacuumed out | 2016-08-31 - 13120 - Timothy Grabowski-found four different areas that had come apart , sealed all four areas - Timothy Grabowski; 2016-09-26 - 13120 - Timothy Grabowski-In progress. Found the ceiling tile newly stained. I will refer this to the roofer for further inspection. This may be residual leaking that has been repaired. I will return to check on. - David Brady; 2016-09-28 - 13120 - Timothy Grabowski-checked green room and plant trays have been replaced with new , water was coming from experiments being done , water is on a timer system . i will have to get with the student in charge to get permission to move a couple tables out away from wall in order to seal cracks in concrete curb - Timothy Grabowski; 2016-09-29 - 13120 - Timothy Grabowski-swept water away from corner of greenhouse , water for experiment on a timer , water all over the floor where the leak originates , trying to locate person in charge of project to get problem taken care of . - Timothy Grabowski; 2016-10-07 - 13120 - Timothy Grabowski-In progress. Met with the occupant to go over the repair to this point and find out di the leak has persisted. I will return after talking with the roofers to confirm the repair is complete. - David Brady; 2016-10-07 - 13120 - David Brady-In progress. Met with the occupant to go over the repair to this point and find out di the leak has persisted. I will return after talking with the roofers to confirm the repair is complete. - David Brady; 2016-10-18 - 13120 - Timothy Grabowski-removed light fixture from mounting plate at wall , on both sides of the doorway to green room , sealed behind fixtures before reinstalling them , caulked around outside perimeter of fixture after install . Also did the same thing with the cover plate for outside wall receptacle . Allowed water trapped inside wall cavity to dry before doing final water test . - Timothy Grabowski; 2016-10-18 - 13120 - Timothy Grabowski-checked rm A-311 to see if water had stopped dripping , down to a slow steady drip , filled 1/3 of a five gallon bucket , emptied bucket - Timothy Grabowski; 2016-10-18 - 13120 - Timothy Grabowski-checked rm 311 , water still dripping from ceiling , removed expanded foam from around pipe at base of concrete ceiling , a 1/3 of a bucket of water came out of the ceiling . I stopped back at rm before end of day , water had stopped dripping . - Timothy Grabowski; 2016-10-19 - 13120 - David Brady-Complete. The leak has been addressed,the ceiling has been repaired, and the damaged, unwanted cabinets and debris have been removed. - David Brady | MWO: Ceiling leak at LSA room 311. Add CA: possible roof repair needed PL transfer to AC: 2 AC units on the roof with water, needs to be vacuumed out 2016-08-31 - 13120 - Timothy Grabowski-found four different areas that had come apart , sealed all four areas - Timothy Grabowski; 2016-09-26 - 13120 - Timothy Grabowski-In progress. Found the ceiling tile newly stained. I will refer this to the roofer for further inspection. This may be residual leaking that has been repaired. I will return to check on. - David Brady; 2016-09-28 - 13120 - Timothy Grabowski-checked green room and plant trays have been replaced with new , water was coming from experiments being done , water is on a timer system . i will have to get with the student in charge to get permission to move a couple tables out away from wall in order to seal cracks in concrete curb - Timothy Grabowski; 2016-09-29 - 13120 - Timothy Grabowski-swept water away from corner of greenhouse , water for experiment on a timer , water all over the floor where the leak originates , trying to locate person in charge of project to get problem taken care of . - Timothy Grabowski; 2016-10-07 - 13120 - Timothy Grabowski-In progress. Met with the occupant to go over the repair to this point and find out di the leak has persisted. I will return after talking with the roofers to confirm the repair is complete. - David Brady; 2016-10-07 - 13120 - David Brady-In progress. Met with the occupant to go over the repair to this point and find out di the leak has persisted. I will return after talking with the roofers to confirm the repair is complete. - David Brady; 2016-10-18 - 13120 - Timothy Grabowski-removed light fixture from mounting plate at wall , on both sides of the doorway to green room , sealed behind fixtures before reinstalling them , caulked around outside perimeter of fixture after install . Also did the same thing with the cover plate for outside wall receptacle . Allowed water trapped inside wall cavity to dry before doing final water test . - Timothy Grabowski; 2016-10-18 - 13120 - Timothy Grabowski-checked rm A-311 to see if water had stopped dripping , down to a slow steady drip , filled 1/3 of a five gallon bucket , emptied bucket - Timothy Grabowski; 2016-10-18 - 13120 - Timothy Grabowski-checked rm 311 , water still dripping from ceiling , removed expanded foam from around pipe at base of concrete ceiling , a 1/3 of a bucket of water came out of the ceiling . I stopped back at rm before end of day , water had stopped dripping . - Timothy Grabowski; 2016-10-19 - 13120 - David Brady-Complete. The leak has been addressed,the ceiling has been repaired, and the damaged, unwanted cabinets and debris have been removed. - David Brady | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 68156 | TMPE-182002 | MWO: !! ATTENTION: Plumbers - the outside sub-pump for the fountains in the vault is not working. It may need to be replaced. thank you for your assistance 42B20BB | 2016-09-27 - 23100 - Michael Kelley-Complete; Found bad check valve cleaned. tested - Michael Kelley | MWO: !! ATTENTION: Plumbers - the outside sub-pump for the fountains in the vault is not working. It may need to be replaced. thank you for your assistance 42B20BB 2016-09-27 - 23100 - Michael Kelley-Complete; Found bad check valve cleaned. tested - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-08-23 | 68193 | TMPE-181965 | SWO: MU - Dock Freezer: The condenser fan needs to be cleaned and it is not working | 2016-08-29 - 18180 - Thomas Gibble-replaced cond fan and deiced coil - Thomas Gibble | SWO: MU - Dock Freezer: The condenser fan needs to be cleaned and it is not working 2016-08-29 - 18180 - Thomas Gibble-replaced cond fan and deiced coil - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-23 | 68210 | TMPE-181948 | MWO: SDFC - 107 EL to HVAC Please add HVAC to W.O. 176863, the cable needs to be repaired. Thank you ORIG REQUEST The West hoop will not go up or down. 4ND9CGF | 2016-09-13 - 18010 - Mitchell Andrews-cable for basketball hoop was wrapped around a bolt freed the cable and replaced the belt on motor - Mitchell Andrews | MWO: SDFC - 107 EL to HVAC Please add HVAC to W.O. 176863, the cable needs to be repaired. Thank you ORIG REQUEST The West hoop will not go up or down. 4ND9CGF 2016-09-13 - 18010 - Mitchell Andrews-cable for basketball hoop was wrapped around a bolt freed the cable and replaced the belt on motor - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 68238 | TMPE-181920 | Cooling coil on compressor Y#08536 is leaking. | NA | Cooling coil on compressor Y#08536 is leaking. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-23 | 178103 | RFMT-130228 | !! Repeat Request. Please drain the water from the air conditioning unit in the bathroom. The water drips steadily, constantly into the sink as has since I moved in over three weeks ago. I never turn the air lower than 75 degrees so it is not the pipes freezing. The unit has been drained before and . . . | 2016-08-29 - 18010 - Wrong Part number used - Santino Aguilar; 2016-08-31 - 18010 - David Cates-8/23 - Shop vacced AC condensation drain and requested that we have Simon and Thor check it out, because this was a reoccurring issue. -8/29 - Simon and Thor had to snake out the condensation drain line in order to clear it. -8/31 - I replaced the sink and faucet - David Cates | !! Repeat Request. Please drain the water from the air conditioning unit in the bathroom. The water drips steadily, constantly into the sink as has since I moved in over three weeks ago. I never turn the air lower than 75 degrees so it is not the pipes freezing. The unit has been drained before and . . . 2016-08-29 - 18010 - Wrong Part number used - Santino Aguilar; 2016-08-31 - 18010 - David Cates-8/23 - Shop vacced AC condensation drain and requested that we have Simon and Thor check it out, because this was a reoccurring issue. -8/29 - Simon and Thor had to snake out the condensation drain line in order to clear it. -8/31 - I replaced the sink and faucet - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 178148 | RFMT-130183 | Request for Estimate. AC MAKING NOISE NEED HELP FIXING IT. UPDATE: PROBLEM HAS BEEN SOLVED NOW 4NMDL2E | 2016-08-24 - 18010 - Salvatore Marasco Jr-Found A.C. unit rattling, making a constant banging noise when blower was in low speed only. Tightened up loose motor housing and pipes. Stopped rattling noise. - Salvatore Marasco Jr | Request for Estimate. AC MAKING NOISE NEED HELP FIXING IT. UPDATE: PROBLEM HAS BEEN SOLVED NOW 4NMDL2E 2016-08-24 - 18010 - Salvatore Marasco Jr-Found A.C. unit rattling, making a constant banging noise when blower was in low speed only. Tightened up loose motor housing and pipes. Stopped rattling noise. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 178154 | RFMT-130177 | !! The ac is not working in the room. It's not cooling. Please send someone to make repairs. Submitted by 4NID637 | 2016-08-24 - 18010 - Salvatore Marasco Jr-Checked on room Hayden East 315's A.C. unit. Room was cool, A.C. was working fine. Room temp. was in the mid to upper 70's, temp. at the fan coil was 61 degrees. Student stated that the unit was repaired during the night shift. - Salvatore Marasco Jr | !! The ac is not working in the room. It's not cooling. Please send someone to make repairs. Submitted by 4NID637 2016-08-24 - 18010 - Salvatore Marasco Jr-Checked on room Hayden East 315's A.C. unit. Room was cool, A.C. was working fine. Room temp. was in the mid to upper 70's, temp. at the fan coil was 61 degrees. Student stated that the unit was repaired during the night shift. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 178159 | RFMT-130172 | Please vacuum for insects on the carpet, clean the air vents to remove mildew and dust, remove the newspaper in the window. 4NN8N7B | NA | Please vacuum for insects on the carpet, clean the air vents to remove mildew and dust, remove the newspaper in the window. 4NN8N7B NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 178164 | RFMT-130167 | Hello, this is Omar Alvarez, my phone number is (602) 931-1249. I live in University Towers, room number 7/11. Maintenance Request: I am not sure that the AC is working properly in our room. I get back from classes and it is warm inside dorm. I would like for the issue to be resolved as soon as p. . . | 2016-08-23 - 18010 - Thomas Zambrano-flushed unit. 76\\xb0-58\\xb0 - Thomas Zambrano | Hello, this is Omar Alvarez, my phone number is (602) 931-1249. I live in University Towers, room number 7/11. Maintenance Request: I am not sure that the AC is working properly in our room. I get back from classes and it is warm inside dorm. I would like for the issue to be resolved as soon as p. . . 2016-08-23 - 18010 - Thomas Zambrano-flushed unit. 76\\xb0-58\\xb0 - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 217046 | RACC-111564 | Repeat Request. A/C panel is locked. We are unable to change the temperature. There is a schedule in the system that does not work for us. We need the system unlocked to change these settings. 4NF0H40 | NA | Repeat Request. A/C panel is locked. We are unable to change the temperature. There is a schedule in the system that does not work for us. We need the system unlocked to change these settings. 4NF0H40 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-08-23 | 217073 | RACC-111537 | !! Clothes washing machine broken. Shakes violently when running and damages walls and surroundings. 4NIIJD9 | NA | !! Clothes washing machine broken. Shakes violently when running and damages walls and surroundings. 4NIIJD9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-23 | 217085 | RACC-111525 | !! The Air Conditioning in the CD room does not work. Living room and other rooms work fine. Temperature in CD room stays warm Vent works but blows warm air 4NJ2H9G | NA | !! The Air Conditioning in the CD room does not work. Living room and other rooms work fine. Temperature in CD room stays warm Vent works but blows warm air 4NJ2H9G NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 217090 | RACC-111520 | !! Dust is in the vents. Causes residents discomfort. 4NJ62D0 | NA | !! Dust is in the vents. Causes residents discomfort. 4NJ62D0 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-23 | 235731 | POLY-112468 | !! Update on the AC unit, I went out to check on it and the fan stops spinning after making the noise and now the air is not working as well 4NF0F97 | NA | !! Update on the AC unit, I went out to check on it and the fan stops spinning after making the noise and now the air is not working as well 4NF0F97 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-23 | 235764 | POLY-112435 | !! Repeat Request. AC is broken. its really hot in my home. 4NFCCJJ | NA | !! Repeat Request. AC is broken. its really hot in my home. 4NFCCJJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-23 | 235772 | POLY-112427 | !! First, the refrigerator doesn't get cold enough to refrigerate the items inside, our shower head stays extremely hot and doesn't get colder, and lastly the air conditioning doesn't get the room cooler. 4N2EFGA | NA | !! First, the refrigerator doesn't get cold enough to refrigerate the items inside, our shower head stays extremely hot and doesn't get colder, and lastly the air conditioning doesn't get the room cooler. 4N2EFGA NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-24 | 67704 | TMPE-182454 | MWO MANZH EXT Please cut bike lock at main entrance near Jamba Juice. Please call and cut the lock after 2pm as the student has classes. If not able to reach student, please contact Donna (mother) 954-931-2886. The student has been running to class since she can't use her bike and it has caused h. . . | 2016-08-26 - 11010 - CALLED TO STEVE. - Monica Moraga; 2016-08-28 - 11010 - Robert Dauscher-cut and removed lock for customer - Robert Dauscher | MWO MANZH EXT Please cut bike lock at main entrance near Jamba Juice. Please call and cut the lock after 2pm as the student has classes. If not able to reach student, please contact Donna (mother) 954-931-2886. The student has been running to class since she can't use her bike and it has caused h. . . 2016-08-26 - 11010 - CALLED TO STEVE. - Monica Moraga; 2016-08-28 - 11010 - Robert Dauscher-cut and removed lock for customer - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-08-24 | 67771 | TMPE-182387 | VFD Reads "fault 9-MOT Overheat" Pump not running, Investigate motor. | NA | VFD Reads "fault 9-MOT Overheat" Pump not running, Investigate motor. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-24 | 67789 | TMPE-182369 | MWO: !! It is hot and muggy in the room. 4NO7K8D | 2016-08-25 - 18290 - Michael Cozens-AC unit down due to a broken shaft. Parts are on order. HVAC says repairs should be done by next week. - Mike Cozens | MWO: !! It is hot and muggy in the room. 4NO7K8D 2016-08-25 - 18290 - Michael Cozens-AC unit down due to a broken shaft. Parts are on order. HVAC says repairs should be done by next week. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-24 | 67799 | TMPE-182359 | MWO: DISCOVERY 123 The ac unit is very loud. Please send someone to check it. | 2017-02-17 - 18010 - Mitchell Andrews-replaced blower motor found in shop stock - Mitchell Andrews | MWO: DISCOVERY 123 The ac unit is very loud. Please send someone to check it. 2017-02-17 - 18010 - Mitchell Andrews-replaced blower motor found in shop stock - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-24 | 67904 | TMPE-182254 | MWO: PEBW 240 The ac has not been working since last week and it's well over 90 degrees. Please repair asap! | 2016-10-12 - 18290 - Roque Garcia-The room had two tstats on the northside wall. They were wired together and was causing the transformer to trip and also at times need replacement. The ACs are currently wired separately with one tstat on the northside and southside walls controlling the ACs independently. - Roque Garcia | MWO: PEBW 240 The ac has not been working since last week and it's well over 90 degrees. Please repair asap! 2016-10-12 - 18290 - Roque Garcia-The room had two tstats on the northside wall. They were wired together and was causing the transformer to trip and also at times need replacement. The ACs are currently wired separately with one tstat on the northside and southside walls controlling the ACs independently. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-24 | 178091 | RFMT-130240 | There is a weird smell that emanates from the AC unit when turned on but when off, the smell goes away. Thank you for all that you do! Contact Name: Center Front Desk Contact Phone Number: 480-965-4308 Contact Email: 4NG0KM1 | 2016-08-26 - 18050 - Eric Miller-Cleaned coil, and vent cover. Advised Greg and student to have carpet cleaned. - Eric Miller; 2016-08-26 - 18050 - Carpet cleaning requested submitted. - Gregory Stetka | There is a weird smell that emanates from the AC unit when turned on but when off, the smell goes away. Thank you for all that you do! Contact Name: Center Front Desk Contact Phone Number: 480-965-4308 Contact Email: 4NG0KM1 2016-08-26 - 18050 - Eric Miller-Cleaned coil, and vent cover. Advised Greg and student to have carpet cleaned. - Eric Miller; 2016-08-26 - 18050 - Carpet cleaning requested submitted. - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-24 | 178093 | RFMT-130238 | The Air Conditioning is not working properly and the air filter is clogged with dirt and dust and the vent in the bathroom is full of dirt too. 4O1JIO2 | 2016-08-25 - 18010 - Thomas Zambrano-replaced air filter,cleaned return duct and checked temp. 56\\xb0at living room vent. - Thomas Zambrano | The Air Conditioning is not working properly and the air filter is clogged with dirt and dust and the vent in the bathroom is full of dirt too. 4O1JIO2 2016-08-25 - 18010 - Thomas Zambrano-replaced air filter,cleaned return duct and checked temp. 56\\xb0at living room vent. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-08-24 | 217054 | RACC-111556 | B4005 Kitchen Area Ice Maker in refrigerator has just snapped a large piece off. Shut off to keep water from pouring into freezer unit. 4NKBO9H | NA | B4005 Kitchen Area Ice Maker in refrigerator has just snapped a large piece off. Shut off to keep water from pouring into freezer unit. 4NKBO9H NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-24 | 235667 | POLY-112532 | Need someone to come and check the hvac system. The thermometer says one temp and the hvac system shuts off, even if the thermostat is set at a lower setting. Some rooms don't get cool. Contact Name: Ronald Pongratz Contact Phone Number: Contact Email: | NA | Need someone to come and check the hvac system. The thermometer says one temp and the hvac system shuts off, even if the thermostat is set at a lower setting. Some rooms don't get cool. Contact Name: Ronald Pongratz Contact Phone Number: Contact Email: NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-24 | 257259 | DTPC-111279 | !! Mercado Building \\u2013 C / ASU DTPC Building # 152C / 502 E. Monroe Street / Phoenix, AZ / 85004 / Roof Condensate Unit #319 : Emergency repair of HVAC condensate unit #319 on Mercado Building-C roof. The unit is no longer operational and will require braizing of refrigerant tubing. Please expedi. . . | NA | !! Mercado Building \\u2013 C / ASU DTPC Building # 152C / 502 E. Monroe Street / Phoenix, AZ / 85004 / Roof Condensate Unit #319 : Emergency repair of HVAC condensate unit #319 on Mercado Building-C roof. The unit is no longer operational and will require braizing of refrigerant tubing. Please expedi. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 67553 | TMPE-182605 | Repipe condensate trap(3/4" copper)with x2 unions, and a clean out plug allowing removal for cleaning. | 2016-10-14 - 23050 - Pete Sandoval-there is no room to installed a trap with two unions and a clean out plug unless you move the unit - Pete Sandoval | Repipe condensate trap(3/4" copper)with x2 unions, and a clean out plug allowing removal for cleaning. 2016-10-14 - 23050 - Pete Sandoval-there is no room to installed a trap with two unions and a clean out plug unless you move the unit - Pete Sandoval | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 67601 | TMPE-182557 | MWO PSYN 210 Person in the room says there is a lot of noise coming from the air vent Please check out. 42B97E1 | 2016-09-14 - 18010 - DUPLICATE TO WO #180965 - Monica Moraga | MWO PSYN 210 Person in the room says there is a lot of noise coming from the air vent Please check out. 42B97E1 2016-09-14 - 18010 - DUPLICATE TO WO #180965 - Monica Moraga | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 67629 | TMPE-182529 | MWO: Repeat Request. There continues to be debris ejected from the ventilation system in this office on a daily basis following the cleaning of the ducts conducted on Work Order TMPE-179561. Photographs of the debris found this morning are attached. The technician who conducted the original cle. . . | 2016-09-06 - 18010 - Jennifer Moyer-Examined air handler and duct work. Cleaned 2 additional return air registers. Unit is operating normally. The customer's office does not have a return air duct inside the room. The return is outside her door. Dust is being pulled through the duct work when the door is opened. I will send an email describing the problem and possible solutions to my supervisor for consideration. - Jennifer Moyer; 2016-09-06 - 18010 - Filter media was installed in her supply register to temporarily solve the problem. 10 minutes or so was spent in traffic. University was backed up. - Jennifer Moyer [Modified: 2016-09-06 Jennifer Moyer] | MWO: Repeat Request. There continues to be debris ejected from the ventilation system in this office on a daily basis following the cleaning of the ducts conducted on Work Order TMPE-179561. Photographs of the debris found this morning are attached. The technician who conducted the original cle. . . 2016-09-06 - 18010 - Jennifer Moyer-Examined air handler and duct work. Cleaned 2 additional return air registers. Unit is operating normally. The customer's office does not have a return air duct inside the room. The return is outside her door. Dust is being pulled through the duct work when the door is opened. I will send an email describing the problem and possible solutions to my supervisor for consideration. - Jennifer Moyer; 2016-09-06 - 18010 - Filter media was installed in her supply register to temporarily solve the problem. 10 minutes or so was spent in traffic. University was backed up. - Jennifer Moyer [Modified: 2016-09-06 Jennifer Moyer] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2016-08-25 | 67678 | TMPE-182480 | University Center C - Roof Electric Shop to check out bad mag starter. HVAC WO#182479, EL WO#182480. Cooling tower spray pump has failed and is putting out 137 deg condenser water temperatures. No cooling to the C - wing | 2016-08-25 - 15000 - Gary Conover-Troubleshoot magnetic starter to cooling tower and replaced same. - Gary Conover; 2016-08-25 - 15000 - Arthur Gonzales-Troubleshoot and repair magnetic starter to cooling tower - Gary Conover | University Center C - Roof Electric Shop to check out bad mag starter. HVAC WO#182479, EL WO#182480. Cooling tower spray pump has failed and is putting out 137 deg condenser water temperatures. No cooling to the C - wing 2016-08-25 - 15000 - Gary Conover-Troubleshoot magnetic starter to cooling tower and replaced same. - Gary Conover; 2016-08-25 - 15000 - Arthur Gonzales-Troubleshoot and repair magnetic starter to cooling tower - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 67691 | TMPE-182467 | MWO University Center C: Tower pump not running, need AC to make repairs ASAP. Cooling tower spray pump has failed and is putting out 137 deg condenser water temperatures. No cooling to the C - wing EL WO 182480 | 2016-08-30 - 23100 - Robert Ecabert-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Oner Munoz-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Oner Munoz-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Robert Ecabert-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-09-02 - 23100 - Robert Ecabert-Came in early to work on water source heat pump in the training room of Xerox on the second floor. - Oner Munoz; 2016-09-02 - 23100 - Oner Munoz-Came in early to work on water source heat pump in the training room of Xerox on the second floor. - Oner Munoz; 2016-09-09 - 23100 - 9/1/16 Oner Munoz 1.5 hr. CE work on heat pump in training room ceiling - Juliana Blusiewicz | MWO University Center C: Tower pump not running, need AC to make repairs ASAP. Cooling tower spray pump has failed and is putting out 137 deg condenser water temperatures. No cooling to the C - wing EL WO 182480 2016-08-30 - 23100 - Robert Ecabert-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Oner Munoz-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Oner Munoz-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-08-30 - 23100 - Robert Ecabert-Checked system found a bad starter for the tower pump, called out the electrical shop. Starter was replaced; systems (units) reset. While resetting unit we found (4) four units which were inaccessible. - Oner Munoz; 2016-09-02 - 23100 - Robert Ecabert-Came in early to work on water source heat pump in the training room of Xerox on the second floor. - Oner Munoz; 2016-09-02 - 23100 - Oner Munoz-Came in early to work on water source heat pump in the training room of Xerox on the second floor. - Oner Munoz; 2016-09-09 - 23100 - 9/1/16 Oner Munoz 1.5 hr. CE work on heat pump in training room ceiling - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 177986 | RFMT-130345 | AC not working. Air blower motor need replacement. | 2016-08-26 - 18010 - John Romero-this is a duplicate w/o - John Romero | AC not working. Air blower motor need replacement. 2016-08-26 - 18010 - John Romero-this is a duplicate w/o - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 178003 | RFMT-130328 | My air conditioning unit is leaking a lot of water. 4NE72B4 | 2016-08-26 - 18010 - Eric Miller-Cleared blocked drain pan. - Eric Miller | My air conditioning unit is leaking a lot of water. 4NE72B4 2016-08-26 - 18010 - Eric Miller-Cleared blocked drain pan. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-08-25 | 178018 | RFMT-130313 | !! Repeat Request. Leak coming from the ceiling. It has been "fixed" 4 times and still leaks. 4N103HN | 2016-08-29 - 13050 - Eric Miller-Vacuumed pan, blew out drain line with compressor. - Eric Miller | !! Repeat Request. Leak coming from the ceiling. It has been "fixed" 4 times and still leaks. 4N103HN 2016-08-29 - 13050 - Eric Miller-Vacuumed pan, blew out drain line with compressor. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-25 | 178023 | RFMT-130308 | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O | 2016-08-30 - 18010 - Unit is cooling for now. Repair parts on order. - Gregory Stetka; 2016-10-19 - 18010 - Simon Fernandez-removed and replaced compressor,liquid line filter,run cap. Recharged unit,unit checked okay. - Simon Fernandez | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O 2016-08-30 - 18010 - Unit is cooling for now. Repair parts on order. - Gregory Stetka; 2016-10-19 - 18010 - Simon Fernandez-removed and replaced compressor,liquid line filter,run cap. Recharged unit,unit checked okay. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-25 | 178024 | RFMT-130307 | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O | 2016-08-25 - 18010 - Thor Millsaps-Adjusted refrigerant charge. Compressor valves are worn out. System up and running and cooling, but compressor should be replaced. Compressor under warranty. - Thor Millsaps | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O 2016-08-25 - 18010 - Thor Millsaps-Adjusted refrigerant charge. Compressor valves are worn out. System up and running and cooling, but compressor should be replaced. Compressor under warranty. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-08-25 | 178027 | RFMT-130304 | !! Please inspect J 210's a/c unit. Residents are reporting it's not cooling properly. Set on 73, registering 80. Thanks, Carli 4NF4L2O | 2016-08-25 - 18010 - Thor Millsaps-Replaced condenser fan motor. System up and running. - Thor Millsaps | !! Please inspect J 210's a/c unit. Residents are reporting it's not cooling properly. Set on 73, registering 80. Thanks, Carli 4NF4L2O 2016-08-25 - 18010 - Thor Millsaps-Replaced condenser fan motor. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-25 | 178028 | RFMT-130303 | The AC is not cold anymore. I think it broke during the night. Only warm air is coming out of the vent. Thank you! Amanda Wong 4NCIB8I | 2016-08-25 - 18010 - Scott Berndt-flushed - Scott Berndt | The AC is not cold anymore. I think it broke during the night. Only warm air is coming out of the vent. Thank you! Amanda Wong 4NCIB8I 2016-08-25 - 18010 - Scott Berndt-flushed - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-08-25 | 178030 | RFMT-130301 | !! AC vent in the bathroom is leaking a lot. Must fix ASAP. 4NL8G44 | 2016-08-25 - 18010 - David Cates-cleared condensation drain - David Cates | !! AC vent in the bathroom is leaking a lot. Must fix ASAP. 4NL8G44 2016-08-25 - 18010 - David Cates-cleared condensation drain - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-25 | 216913 | RACC-111697 | !! Air Conditioning Unit is broken and will not cool air. Please fix as soon as possible, since it gets especially hot on the 7th floor. Thank you! 4NG2G2D | NA | !! Air Conditioning Unit is broken and will not cool air. Please fix as soon as possible, since it gets especially hot on the 7th floor. Thank you! 4NG2G2D NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-25 | 216914 | RACC-111696 | !! Repeat Request. Bathroom vent in K5147 A has been removed since move in, the AC in the hall between A and B leaks, the microwave does NOT heat food even though it turns on and rotates food. 4NEI116 | NA | !! Repeat Request. Bathroom vent in K5147 A has been removed since move in, the AC in the hall between A and B leaks, the microwave does NOT heat food even though it turns on and rotates food. 4NEI116 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-25 | 216916 | RACC-111694 | !! Air filter needs changing 4NG1M7O | NA | !! Air filter needs changing 4NG1M7O NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 216922 | RACC-111688 | !! AC fan is making a large noise whenever it shuts off. There may be something stuck in the fan. 4NK4A8A | NA | !! AC fan is making a large noise whenever it shuts off. There may be something stuck in the fan. 4NK4A8A NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 216936 | RACC-111674 | !! We need an air filter for our air conditioning unit. None was found when we moved in. 4NCH2E6 | NA | !! We need an air filter for our air conditioning unit. None was found when we moved in. 4NCH2E6 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 235631 | POLY-112568 | CALLED STEVE !!Air conditioning does not work in this classroom. It is well into the mid 80s and pressing firmly and holding on the thermostat does not manually start the air conditioning. There is a class of 70 students from 3:00pm-4:15pm that is requesting that the a/c be turned down because it. . . | NA | CALLED STEVE !!Air conditioning does not work in this classroom. It is well into the mid 80s and pressing firmly and holding on the thermostat does not manually start the air conditioning. There is a class of 70 students from 3:00pm-4:15pm that is requesting that the a/c be turned down because it. . . NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-25 | 257043 | DTPC-111495 | A/C vendor fixing condensate leaks at grant street. | 2016-08-31 - 10010 - Bruce Pickford-A/C vendor fixing condensate leaks at grant street took chief engineer to check work being done. - Bruce Pickford | A/C vendor fixing condensate leaks at grant street. 2016-08-31 - 10010 - Bruce Pickford-A/C vendor fixing condensate leaks at grant street took chief engineer to check work being done. - Bruce Pickford | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-26 | 65538 | TMPE-184620 | SWO: estimate request: PS H: replacement of ice machine in room 336 | 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Thomas Gibble-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Robert Dauscher-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-16 - 18210 - Gail Jackson-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Thomas Gibble-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Thomas Gibble-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Robert Dauscher-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson | SWO: estimate request: PS H: replacement of ice machine in room 336 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Thomas Gibble-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Gail Jackson-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-12 - 18210 - Robert Dauscher-Trip to warehouse and ACE for needed material. Transport ice machine to Phy Sci H rm 336 for install; installed new filter system, new drain line and machine, test run. Requires 3 workers to safely remove from pallet and install legs. Difficult to access bldg. E. university is backed up past College. Will need to remove old unit from EQ room. - Gail Jackson; 2016-09-16 - 18210 - Gail Jackson-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Thomas Gibble-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Thomas Gibble-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson; 2016-09-16 - 18210 - Robert Dauscher-Lift truck to Phi Sci H to haul off old ice machine. Check new machine, ok. Transported to shop , recovered refrigerant, removed compressor and ready for recycled. COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-26 | 67264 | TMPE-182894 | SWO: Please open a work order for the HVAC Shop to assess a -80 chest freezer in LSE 447 which began losing temperature so has been emptied and is being shut down. We would like their expertise as to whether the unit is repairable or should be slavaged. Assessment charges up to $250.00 may be bill. . . | 2016-11-15 - 18180 - Good afternoon, This work order may be cancelled. The researcher has decided to salvage the unit without inspection. Thank you, Judy - Amanda Thomas | SWO: Please open a work order for the HVAC Shop to assess a -80 chest freezer in LSE 447 which began losing temperature so has been emptied and is being shut down. We would like their expertise as to whether the unit is repairable or should be slavaged. Assessment charges up to $250.00 may be bill. . . 2016-11-15 - 18180 - Good afternoon, This work order may be cancelled. The researcher has decided to salvage the unit without inspection. Thank you, Judy - Amanda Thomas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-26 | 67287 | TMPE-182871 | MWO: The occupant in Dixie 145 says her A/C is not working and sounds horrible. Kris Kreutz looked at it and said the squirrel cage is rubbing on the housing. Can this please be looked at ASAP? Thank you. 42C04M9 | 2016-08-31 - 18010 - Zhi Yu-We diagnose the blower motor bad bearing. Replaced blower motor. - Zhi Yu; 2016-09-08 - 18010 - Zhi Yu-Replaced blower motor. - Zhi Yu | MWO: The occupant in Dixie 145 says her A/C is not working and sounds horrible. Kris Kreutz looked at it and said the squirrel cage is rubbing on the housing. Can this please be looked at ASAP? Thank you. 42C04M9 2016-08-31 - 18010 - Zhi Yu-We diagnose the blower motor bad bearing. Replaced blower motor. - Zhi Yu; 2016-09-08 - 18010 - Zhi Yu-Replaced blower motor. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-26 | 67349 | TMPE-182809 | The discharge on the reservoir is broken and the overflow/bin drain needs to lengthened to drain directly into the floor drain. The water to the unit is off at the ball valve in the ceiling and the power is off at the unit. The Ice machine is located in the south hallway on the 4th FL. | 2016-09-02 - 18210 - Thomas Gibble-replaced belt and float - Thomas Gibble; 2016-09-02 - 18210 - Gail Jackson-replaced belt and float - Thomas Gibble | The discharge on the reservoir is broken and the overflow/bin drain needs to lengthened to drain directly into the floor drain. The water to the unit is off at the ball valve in the ceiling and the power is off at the unit. The Ice machine is located in the south hallway on the 4th FL. 2016-09-02 - 18210 - Thomas Gibble-replaced belt and float - Thomas Gibble; 2016-09-02 - 18210 - Gail Jackson-replaced belt and float - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2
2016-08-26 | 177907 | RFMT-130424 | !! Repeat Request. The Air Conditioning isn't working. It is blowing air but the room isn't being cooled. Contact Name: Contact Phone Number: 5207093652 Contact Email: 4NO9ENA | 2016-08-29 - 18010 - Salvatore Marasco Jr-Checked on A.C. complaint finding room cool at @ 75 degrees in room and @ 64 degrees at the fan coil. The student whom was present in the room stated that he knew nothing of any complaint but his room mate may have filed the TMA. Student had door open upon my arrival and room was still cool. This TMA may have been a misprint being confused with the TMA filed for room (E223). - Salvatore Marasco Jr | !! Repeat Request. The Air Conditioning isn't working. It is blowing air but the room isn't being cooled. Contact Name: Contact Phone Number: 5207093652 Contact Email: 4NO9ENA 2016-08-29 - 18010 - Salvatore Marasco Jr-Checked on A.C. complaint finding room cool at @ 75 degrees in room and @ 64 degrees at the fan coil. The student whom was present in the room stated that he knew nothing of any complaint but his room mate may have filed the TMA. Student had door open upon my arrival and room was still cool. This TMA may have been a misprint being confused with the TMA filed for room (E223). - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-26 | 177918 | RFMT-130413 | !! The air conditinoing in the room doesn't appear to be working. The air is blowing but the room is not being cooled. Contact Name: Contact Phone Number: 5207093652 Contact Email: 4NO9ENA | 2016-08-29 - 18010 - Salvatore Marasco Jr-Upon arriving to room E223, found room at a good temperature comfortable to the student present in the room and to myself. She stated that a maint. mech. was there last night and "did something." Checked A.C. thermostat finding it set in the off position for the heating and cooling, and the fan switch was set to the on position, resulting in the blower only recirculating room air and not cooling it. Set thermostat to normal cooling position and will check back again to make sure room stayed cool. - Salvatore Marasco Jr | !! The air conditinoing in the room doesn't appear to be working. The air is blowing but the room is not being cooled. Contact Name: Contact Phone Number: 5207093652 Contact Email: 4NO9ENA 2016-08-29 - 18010 - Salvatore Marasco Jr-Upon arriving to room E223, found room at a good temperature comfortable to the student present in the room and to myself. She stated that a maint. mech. was there last night and "did something." Checked A.C. thermostat finding it set in the off position for the heating and cooling, and the fan switch was set to the on position, resulting in the blower only recirculating room air and not cooling it. Set thermostat to normal cooling position and will check back again to make sure room stayed cool. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-26 | 177989 | RFMT-130342 | HDMichael Description - air conditioning is out Time of dispatch - 10:02 pm Dispatched to - Joe Swan | 2016-08-30 - 18010 - Repair parts on order - Gregory Stetka; 2016-09-08 - 18010 - Thor Millsaps-Replaced reversing valve. Charged 6 lbs R-22. System up and running. - Thor Millsaps | HDMichael Description - air conditioning is out Time of dispatch - 10:02 pm Dispatched to - Joe Swan 2016-08-30 - 18010 - Repair parts on order - Gregory Stetka; 2016-09-08 - 18010 - Thor Millsaps-Replaced reversing valve. Charged 6 lbs R-22. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-08-26 | 208733 | RAMA-100531 | !! *toilet on C/D side stopped flushing *fan in bedroom D is missing a cord *filter for air conditioning in bedroom D was never changed--filter is very dirty *dish in microwave does not spin 4NL2626 | NA | !! *toilet on C/D side stopped flushing *fan in bedroom D is missing a cord *filter for air conditioning in bedroom D was never changed--filter is very dirty *dish in microwave does not spin 4NL2626 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-26 | 216784 | RACC-111826 | !! I believe our air conditioner is broken. It is blowing out warm air and is set to 70 degrees but the room is at 80 degrees and rising. 4NG2B8B | NA | !! I believe our air conditioner is broken. It is blowing out warm air and is set to 70 degrees but the room is at 80 degrees and rising. 4NG2B8B NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-08-26 | 216811 | RACC-111799 | The air conditioning vent on the ceiling of the short "hallway" between rooms A and B, right above the thermostat, sometimes drips water when the fan is not blowing. Please fix. 4ND6D19 | NA | The air conditioning vent on the ceiling of the short "hallway" between rooms A and B, right above the thermostat, sometimes drips water when the fan is not blowing. Please fix. 4ND6D19 NA | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-26 | 235614 | POLY-112585 | . last night we started to smell something burning and traced it to find that the AC randomly kicked on the heater. Now whenever we turn on the AC or fan in any way it also engages the heater, and leaves the spark ignition on the whole time. We have it turned off now but would like somebody to come . . . | NA | . last night we started to smell something burning and traced it to find that the AC randomly kicked on the heater. Now whenever we turn on the AC or fan in any way it also engages the heater, and leaves the spark ignition on the whole time. We have it turned off now but would like somebody to come . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-26 | 257142 | DTPC-111396 | Collect HVAC information from the Westward Ho and assemble a spreadsheet with unit ID's and create a numbering system for unit identification. | 2016-08-26 - 10000 - James Hermann-Unit identification is incomplete. I will assemble all information into a single page spreadsheet for easy identification. This will require looking at each unit individually. - James Hermann; 2016-09-02 - 10000 - James Hermann-work on spreadsheet for Westward Ho - James Hermann; 2016-09-03 - 10000 - James Hermann-structure information format and enter data from rounds and photos. - James Hermann; 2016-09-08 - 10000 - James Hermann-build-out new spreadsheet from old equipment list. Pair up evaps with Condensers. - James Hermann; 2016-09-14 - 10000 - James Hermann-Walk throughout the collaboratory (Westward Ho)and gather filter sizes then also go to the roof and gather filter sizes from the package units. Enter all information on a spreadsheet and send to the chief. - James Hermann; 2016-09-27 - 10000 - James Hermann-Information is collected as well as filter sizing. - James Hermann | Collect HVAC information from the Westward Ho and assemble a spreadsheet with unit ID's and create a numbering system for unit identification. 2016-08-26 - 10000 - James Hermann-Unit identification is incomplete. I will assemble all information into a single page spreadsheet for easy identification. This will require looking at each unit individually. - James Hermann; 2016-09-02 - 10000 - James Hermann-work on spreadsheet for Westward Ho - James Hermann; 2016-09-03 - 10000 - James Hermann-structure information format and enter data from rounds and photos. - James Hermann; 2016-09-08 - 10000 - James Hermann-build-out new spreadsheet from old equipment list. Pair up evaps with Condensers. - James Hermann; 2016-09-14 - 10000 - James Hermann-Walk throughout the collaboratory (Westward Ho)and gather filter sizes then also go to the roof and gather filter sizes from the package units. Enter all information on a spreadsheet and send to the chief. - James Hermann; 2016-09-27 - 10000 - James Hermann-Information is collected as well as filter sizing. - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-26 | 257189 | DTPC-111349 | Mercado F Building West side of building/602-252-4461 - Blue light is out | 2016-08-26 - 15040 - Robert Bartels-Took light apart and found blown fuse, part on order. - Robert Bartels; 2016-08-30 - 15040 - Robert Bartels-Replaced light - Robert Bartels | Mercado F Building West side of building/602-252-4461 - Blue light is out 2016-08-26 - 15040 - Robert Bartels-Took light apart and found blown fuse, part on order. - Robert Bartels; 2016-08-30 - 15040 - Robert Bartels-Replaced light - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-27 | 177896 | RFMT-130435 | !! Air conditioner rattles when turning on and off 4NJCC2B | 2016-08-29 - 18010 - David Cates-Turned AC on and off multiple times but wasn't able to replicate the noise. Checked AC motor, and zip tied all of the wiring away in case they might be getting hit by the fan blades. Replaced AC filters in both rooms. - David Cates | !! Air conditioner rattles when turning on and off 4NJCC2B 2016-08-29 - 18010 - David Cates-Turned AC on and off multiple times but wasn't able to replicate the noise. Checked AC motor, and zip tied all of the wiring away in case they might be getting hit by the fan blades. Replaced AC filters in both rooms. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-27 | 235577 | POLY-112622 | !! Shower head in "A" space is broken, water leaks out of side of head when water is turned on. Space behind lower cabinet between sink and dishwasher lets in cockroaches and crickets, resident can show/explain, 443-949-6076 water occasionally leaks into "B" space under tiles from the A/C uni. . . | NA | !! Shower head in "A" space is broken, water leaks out of side of head when water is turned on. Space behind lower cabinet between sink and dishwasher lets in cockroaches and crickets, resident can show/explain, 443-949-6076 water occasionally leaks into "B" space under tiles from the A/C uni. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-08-27 | 235587 | POLY-112612 | *THIS WAS A CALL-OUT TO RAY FROM SATURDAY 8/27/16* Check circuit breakers, one circuit went out that ran the portable AC unit and computors. 42B20MM | 2016-09-29 - 15000 - Reynaldo Martinez-8/29 - Ray reset the breaker (CALL OUT) - Gayle Swenson | *THIS WAS A CALL-OUT TO RAY FROM SATURDAY 8/27/16* Check circuit breakers, one circuit went out that ran the portable AC unit and computors. 42B20MM 2016-09-29 - 15000 - Reynaldo Martinez-8/29 - Ray reset the breaker (CALL OUT) - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-28 | 177886 | RFMT-130445 | !! We have a leak in our room when the fan in our room isn't running. 4O1HA85 | 2016-08-29 - 18010 - David Cates-Cleared AC condensation drain - David Cates | !! We have a leak in our room when the fan in our room isn't running. 4O1HA85 2016-08-29 - 18010 - David Cates-Cleared AC condensation drain - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-28 | 177912 | RFMT-130419 | !! Repeat Request. My air conditioner is blowing air but not cooling the room down. I have it set to 65 and its blowing 80+ degrees. My air conditioner did this same thing not even two days ago. 4NO9ENA | 2016-08-29 - 18010 - Salvatore Marasco Jr-Repeat request. Already repaired and checked up on. - Salvatore Marasco Jr | !! Repeat Request. My air conditioner is blowing air but not cooling the room down. I have it set to 65 and its blowing 80+ degrees. My air conditioner did this same thing not even two days ago. 4NO9ENA 2016-08-29 - 18010 - Salvatore Marasco Jr-Repeat request. Already repaired and checked up on. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-28 | 177921 | RFMT-130410 | !! AC unit leaking. Please fix ASAP Contact Name: Cortez Davis Contact Phone Number: Contact Email: 4NGO9MA | 2016-08-29 - 18010 - Thomas Zambrano-cleaned out pan,wrap pipes, tighten down hose clamps. pan is loose and falling. called Tony M. and he put in work order for ac techs. - Thomas Zambrano | !! AC unit leaking. Please fix ASAP Contact Name: Cortez Davis Contact Phone Number: Contact Email: 4NGO9MA 2016-08-29 - 18010 - Thomas Zambrano-cleaned out pan,wrap pipes, tighten down hose clamps. pan is loose and falling. called Tony M. and he put in work order for ac techs. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-29 | 5025 | WEST-106224 | Drinking Fountain Maintenence-Monthly | 2016-08-29 - xPM-WC-DRINK-M - Daniel Tanner-Walked the building and check all the drinking fountains to make sure they were all in good working condition. - Daniel Tanner | Drinking Fountain Maintenence-Monthly 2016-08-29 - xPM-WC-DRINK-M - Daniel Tanner-Walked the building and check all the drinking fountains to make sure they were all in good working condition. - Daniel Tanner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 63558 | TMPE-186600 | FACTORY MOTOR PARTS CCA585 RC95 TOTAL: 73.44 | NA | FACTORY MOTOR PARTS CCA585 RC95 TOTAL: 73.44 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 65569 | TMPE-184589 | MWO: PEBW ASUHC-Agent: Ahmed Khalil Description: Main gym is hot. Who was dispatched: Mike Cozens Time of dispatch: 7:24PM Mike said he will check and if the fans are already on he might call back for us to dispatch HVAC to check on the cooler. gave Roque Garcia call, LM advising Mike C. . . | 2016-08-30 - 18290 - 8-29-16 When I checked, I found that 5 evap coolers were showing on and 3 evap coolers were off. Space temperature showed 95 degrees. I requested HVAC tech check out operation of evap coolers. sb - Mike Cozens | MWO: PEBW ASUHC-Agent: Ahmed Khalil Description: Main gym is hot. Who was dispatched: Mike Cozens Time of dispatch: 7:24PM Mike said he will check and if the fans are already on he might call back for us to dispatch HVAC to check on the cooler. gave Roque Garcia call, LM advising Mike C. . . 2016-08-30 - 18290 - 8-29-16 When I checked, I found that 5 evap coolers were showing on and 3 evap coolers were off. Space temperature showed 95 degrees. I requested HVAC tech check out operation of evap coolers. sb - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-29 | 65606 | TMPE-184552 | SWO: Please issue a work order for the HVAC Shop for no cooling of the AC in suites 120,121, 122 per John Howell. PO is YG202004971. Thank you. 42BDEDF | 2016-08-29 - 18290 - This is being actively worked on by our techs as it came into our work order bucket. - Brian Qualls; 2016-09-01 - 18290 - Roque Garcia-120, 121, and 122 are repaired and running. 122 needed the actuator valve replaced. done. - Brian Qualls; 2016-09-01 - 18290 - Midhat Mukanovic-120, 121, and 122 are repaired and running. 122 needed the actuator valve replaced. done. - Brian Qualls | SWO: Please issue a work order for the HVAC Shop for no cooling of the AC in suites 120,121, 122 per John Howell. PO is YG202004971. Thank you. 42BDEDF 2016-08-29 - 18290 - This is being actively worked on by our techs as it came into our work order bucket. - Brian Qualls; 2016-09-01 - 18290 - Roque Garcia-120, 121, and 122 are repaired and running. 122 needed the actuator valve replaced. done. - Brian Qualls; 2016-09-01 - 18290 - Midhat Mukanovic-120, 121, and 122 are repaired and running. 122 needed the actuator valve replaced. done. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-08-29 | 65622 | TMPE-184536 | SWO: !! University Club Attic HVAC to reinsulate valves on AH#G (Y#304) & AH#F cooling valves on both units, after valves have been replaced. Please contact PL shop to see if the valves have been replaced. PL shop added to install a 1 1/2" cooling valve on AH#G (Y#304) & cooling valve on AH. . . | 2017-03-23 - 18220 - Michael Longtin-complete - Michael Longtin | SWO: !! University Club Attic HVAC to reinsulate valves on AH#G (Y#304) & AH#F cooling valves on both units, after valves have been replaced. Please contact PL shop to see if the valves have been replaced. PL shop added to install a 1 1/2" cooling valve on AH#G (Y#304) & cooling valve on AH. . . 2017-03-23 - 18220 - Michael Longtin-complete - Michael Longtin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-08-29 | 65647 | TMPE-184511 | MWO: Remove controls enclosure from air compressor, build frame and set off unit on concrete to alleviate vibration in controls. | 2016-10-05 - 18010 - Jose Lopez-remove control panel install pads put panel back in placed check unit working @ this time. - Jose Lopez | MWO: Remove controls enclosure from air compressor, build frame and set off unit on concrete to alleviate vibration in controls. 2016-10-05 - 18010 - Jose Lopez-remove control panel install pads put panel back in placed check unit working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-29 | 65648 | TMPE-184510 | MWO: In reference to WO# TMPE-184510. To clarify, the entire third floor has a decibel range from 75 to over 85 caused from some machinery located on the roof. They described the noise as metal to metal sounds and several offices are vacant because it is too disturbing. Can someone please be sent. . . | 2016-09-26 - 18010 - Jose Lopez-inspect air handlers on roof found no problems change speed on motors from low to hi no problems so far - Jose Lopez | MWO: In reference to WO# TMPE-184510. To clarify, the entire third floor has a decibel range from 75 to over 85 caused from some machinery located on the roof. They described the noise as metal to metal sounds and several offices are vacant because it is too disturbing. Can someone please be sent. . . 2016-09-26 - 18010 - Jose Lopez-inspect air handlers on roof found no problems change speed on motors from low to hi no problems so far - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-29 | 65743 | TMPE-184415 | MWO: CTRPT: !! Repeat Request. The AC in room 214-11 is not working again. Can someone please service the AC. AC is currently set at 77 but there is hot air coming from the vents. When AC turns off temperature rises into 80s. EMS WO#184415, HVAC WO#185390. 4MO5454 | 2016-09-02 - 18290 - CALLED TO EMS &amp; JOHN H. - Monica Moraga; 2016-09-02 - 18290 - Cheryl St. John-09.02.16 Checked HP2-8 for RM 114-11 on the Metasys system, found the unit off line. I contacted Mitch from the HVAC shop to see if he knew of any issues with the unit. This is a new unit and has been tripping off, he believes it may be something with the wiring. He stated it runs about three weeks then turns off. Ish and I went over to and checked out the space, it was 85 deg, Ish reset the unit, we waited for the compressor to come on and once on the temperature started to cool down (80deg when we left). I followed up with Mitch to let him know the air was on an gave him the temperature etc. on the space. I spoke with the occupant and per her request put the space temperature at 76 deg (it was set for 78 deg). I let her know Mitch would be back this afternoon to look at the HP. Created work order for HVAC (185390) and sent email to shop acting supervisor, ems supervisor, occupant and Clint Lord. Posted labor and finished work order. - Cheryl St. John | MWO: CTRPT: !! Repeat Request. The AC in room 214-11 is not working again. Can someone please service the AC. AC is currently set at 77 but there is hot air coming from the vents. When AC turns off temperature rises into 80s. EMS WO#184415, HVAC WO#185390. 4MO5454 2016-09-02 - 18290 - CALLED TO EMS &amp; JOHN H. - Monica Moraga; 2016-09-02 - 18290 - Cheryl St. John-09.02.16 Checked HP2-8 for RM 114-11 on the Metasys system, found the unit off line. I contacted Mitch from the HVAC shop to see if he knew of any issues with the unit. This is a new unit and has been tripping off, he believes it may be something with the wiring. He stated it runs about three weeks then turns off. Ish and I went over to and checked out the space, it was 85 deg, Ish reset the unit, we waited for the compressor to come on and once on the temperature started to cool down (80deg when we left). I followed up with Mitch to let him know the air was on an gave him the temperature etc. on the space. I spoke with the occupant and per her request put the space temperature at 76 deg (it was set for 78 deg). I let her know Mitch would be back this afternoon to look at the HP. Created work order for HVAC (185390) and sent email to shop acting supervisor, ems supervisor, occupant and Clint Lord. Posted labor and finished work order. - Cheryl St. John | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-29 | 65746 | TMPE-184412 | MWO: !! Please create service request for HVAC shop to restart control air compressor for pneumatic stats for temp control thanks Jeffrey 4N00ABB | 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-disconnect motor #1,remove control panel,install pads in the back of control panel to prevent vibration re connect motor adjust belts working @ this time - Jose Lopez | MWO: !! Please create service request for HVAC shop to restart control air compressor for pneumatic stats for temp control thanks Jeffrey 4N00ABB 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18010 - Jose Lopez-disconnect motor #1,remove control panel,install pads in the back of control panel to prevent vibration re connect motor adjust belts working @ this time - Jose Lopez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2016-08-29 | 65747 | TMPE-184411 | MWO: Please adjust the temperature in room 130 at Art Warehouse!! It is over 90 degrees during the day! Class is intolerable at that temperature. | 2016-09-01 - 18290 - Thomas Gibble-reset unit and put batteries in t-stat - Thomas Gibble; 2016-09-01 - 18290 - Gail Jackson-reset unit and put batteries in t-stat - Thomas Gibble | MWO: Please adjust the temperature in room 130 at Art Warehouse!! It is over 90 degrees during the day! Class is intolerable at that temperature. 2016-09-01 - 18290 - Thomas Gibble-reset unit and put batteries in t-stat - Thomas Gibble; 2016-09-01 - 18290 - Gail Jackson-reset unit and put batteries in t-stat - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 65785 | TMPE-184373 | MWO: HVAC Shop- On the roof there is a roof top unit that is squealing really bad. 4NNI9H6 | 2016-11-02 - 18010 - Gail Jackson-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Thomas Gibble-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Carl Karr-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Midhat Mukanovic-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Gail Jackson-Trip to Webb Phx and Warehouse for parts. Start to Chisel out pads. - Gail Jackson; 2016-11-02 - 18010 - Thomas Gibble-Trip to Webb Phx and Warehouse for parts. Start to Chisel out pads. - Gail Jackson; 2016-11-28 - 18010 - Gail Jackson-Replaced water line and run tested. Will need to return to clean old pads off roof. - Gail Jackson; 2016-12-05 - 18010 - Gail Jackson-Pick up and clean up old pads and parts from roof area and transport to dumpster. COMPLETE. - Gail Jackson | MWO: HVAC Shop- On the roof there is a roof top unit that is squealing really bad. 4NNI9H6 2016-11-02 - 18010 - Gail Jackson-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Thomas Gibble-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Carl Karr-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Midhat Mukanovic-installed belts, floats, pumps, pads, and cleaned coolers, oiled bearings. After start up discovered no water to south cooler; H20 line plugged; will need replaced. - Gail Jackson; 2016-11-02 - 18010 - Gail Jackson-Trip to Webb Phx and Warehouse for parts. Start to Chisel out pads. - Gail Jackson; 2016-11-02 - 18010 - Thomas Gibble-Trip to Webb Phx and Warehouse for parts. Start to Chisel out pads. - Gail Jackson; 2016-11-28 - 18010 - Gail Jackson-Replaced water line and run tested. Will need to return to clean old pads off roof. - Gail Jackson; 2016-12-05 - 18010 - Gail Jackson-Pick up and clean up old pads and parts from roof area and transport to dumpster. COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-29 | 65811 | TMPE-184347 | MWO: Request to Jason (supervisor in electric shop): Jason, Room 120 in Matthews Center has an active leak from an AC unit. Jennifer Moyer (ASU HVAC) has been to the room to look at the problem. She requested an electrician to handle the electrical aspect of the job----the AC unit is too hazardo. . . | 2016-11-07 - 15000 - Samuel Gladden-Job finished. - Samuel Gladden | MWO: Request to Jason (supervisor in electric shop): Jason, Room 120 in Matthews Center has an active leak from an AC unit. Jennifer Moyer (ASU HVAC) has been to the room to look at the problem. She requested an electrician to handle the electrical aspect of the job----the AC unit is too hazardo. . . 2016-11-07 - 15000 - Samuel Gladden-Job finished. - Samuel Gladden | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177796 | RFMT-130535 | David, The requester has requested a call back mentioning, that they think the wrong vent was checked yesterday and have asked the vents be rechecked. I have already scheduled the carpet cleaning with Olympus. Please recheck. Thank you. !! Please address foul odor in room. It may be coming fr. . . | 2016-08-30 - 18020 - David Cates-***NOTE*** Can we please schedule Olympus to clean the carpet in the room? Checked bathroom, and up in AC vent. Smell is not present in the bathroom at all which shares the same AC unit, and I could not smell it in the vents either. Recommended that we have Olympus clean the carpet to see if that is source of the odor. - David Cates; 2016-08-31 - 18020 - David Cates-Checked all vents but found nothing. Air coming out of vent smelled fine, and smell was much stronger when standing in the room compared to being up by the vent. Opened up vent anyway and sprayed disinfecting spray into it and replaced filer. - David Cates | David, The requester has requested a call back mentioning, that they think the wrong vent was checked yesterday and have asked the vents be rechecked. I have already scheduled the carpet cleaning with Olympus. Please recheck. Thank you. !! Please address foul odor in room. It may be coming fr. . . 2016-08-30 - 18020 - David Cates-***NOTE*** Can we please schedule Olympus to clean the carpet in the room? Checked bathroom, and up in AC vent. Smell is not present in the bathroom at all which shares the same AC unit, and I could not smell it in the vents either. Recommended that we have Olympus clean the carpet to see if that is source of the odor. - David Cates; 2016-08-31 - 18020 - David Cates-Checked all vents but found nothing. Air coming out of vent smelled fine, and smell was much stronger when standing in the room compared to being up by the vent. Opened up vent anyway and sprayed disinfecting spray into it and replaced filer. - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177807 | RFMT-130524 | !! Lots of dust coming out of the vents 4NO395H | 2016-08-31 - 18010 - Casey Faultner-Replaced the air filter. The air filter was extremely dirty. - Casey Faultner | !! Lots of dust coming out of the vents 4NO395H 2016-08-31 - 18010 - Casey Faultner-Replaced the air filter. The air filter was extremely dirty. - Casey Faultner | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-29 | 177820 | RFMT-130511 | !! This room is very hot and humid, please come repair ac asap. Thank you. Submitted by 4O077C3 | 2016-08-30 - 18010 - Thomas Zambrano-second time in two week i had to flush unit. sttart temp. was 83\\xb0 at living room vent and 57\\xb0 after i flushed unit. - Thomas Zambrano | !! This room is very hot and humid, please come repair ac asap. Thank you. Submitted by 4O077C3 2016-08-30 - 18010 - Thomas Zambrano-second time in two week i had to flush unit. sttart temp. was 83\\xb0 at living room vent and 57\\xb0 after i flushed unit. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177830 | RFMT-130501 | !! Dirty air vents - unhealthy to breath 4NKDEMG | NA | !! Dirty air vents - unhealthy to breath 4NKDEMG NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177835 | RFMT-130496 | !! Repeat Request. Please drain the water from the air conditioning unit in the bathroom. The water drips steadily, constantly into the sink as has since I moved in over three weeks ago. I never turn the air lower than 75 degrees so it is not the pipes freezing. The unit has been drained before and . . . | 2016-08-30 - 18010 - Thor Millsaps-opened condensate drain line, ran hand snake through drain line. Flushed drain line . Line cleared with water. closed drain, cleared,and no leaks found. - Simon Fernandez | !! Repeat Request. Please drain the water from the air conditioning unit in the bathroom. The water drips steadily, constantly into the sink as has since I moved in over three weeks ago. I never turn the air lower than 75 degrees so it is not the pipes freezing. The unit has been drained before and . . . 2016-08-30 - 18010 - Thor Millsaps-opened condensate drain line, ran hand snake through drain line. Flushed drain line . Line cleared with water. closed drain, cleared,and no leaks found. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-29 | 177836 | RFMT-130495 | !! the air vent in our room is not doing its job, our room is hotter than our suite mates and we are all on the same settings. We are wondering if someone could take a look at it and get it fixed cause my roommate and I both like the room very cold! 4O0J2I0 | 2016-08-30 - 18010 - Chester Duncan-8/29: Inspected system and adjusted vent fins to direct air into room 8/30 replaced robe hook in 416-2 - Chester Duncan | !! the air vent in our room is not doing its job, our room is hotter than our suite mates and we are all on the same settings. We are wondering if someone could take a look at it and get it fixed cause my roommate and I both like the room very cold! 4O0J2I0 2016-08-30 - 18010 - Chester Duncan-8/29: Inspected system and adjusted vent fins to direct air into room 8/30 replaced robe hook in 416-2 - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177839 | RFMT-130492 | Please replace the pan and the splash guard in University Towers room 119 because it is leaking bad. Simon RFS) | 2016-08-30 - 18010 - Simon Fernandez-removed and replaced bad condensate pan.checked for leaks none found. - Simon Fernandez | Please replace the pan and the splash guard in University Towers room 119 because it is leaking bad. Simon RFS) 2016-08-30 - 18010 - Simon Fernandez-removed and replaced bad condensate pan.checked for leaks none found. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 177841 | RFMT-130490 | Please the pan and splash guard in room 407, because they are leaking bad. (Simon from RFS) | 2016-08-30 - 23000 - Simon Fernandez-removed and replaced bad condensate pan. checked for leaks none found, - Simon Fernandez | Please the pan and splash guard in room 407, because they are leaking bad. (Simon from RFS) 2016-08-30 - 23000 - Simon Fernandez-removed and replaced bad condensate pan. checked for leaks none found, - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-29 | 235519 | POLY-112680 | *This was a call out on 8/30 No A/C, replaced condenser fan motor | NA | *This was a call out on 8/30 No A/C, replaced condenser fan motor NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-29 | 235532 | POLY-112667 | !! Repeat Request. Our AC unit went out again. Somebody came by to fix it and it was broken again less than 24 hours later. Won't turn on. This is now the third time I have requested service... 4NAE2G7 | NA | !! Repeat Request. Our AC unit went out again. Somebody came by to fix it and it was broken again less than 24 hours later. Won't turn on. This is now the third time I have requested service... 4NAE2G7 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-29 | 235571 | POLY-112628 | !! The air conditioner is blowing warm air. The Patio door does not have weather-stripping/insulation. Mosquitos are coming inside because of the gap in the door frame. Contact Name: DJ Payton Contact Phone Number: Contact Email: dj.payton@asu.edu 4NB67BE | NA | !! The air conditioner is blowing warm air. The Patio door does not have weather-stripping/insulation. Mosquitos are coming inside because of the gap in the door frame. Contact Name: DJ Payton Contact Phone Number: Contact Email: dj.payton@asu.edu 4NB67BE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 4898 | WEST-106351 | Chiller 4 Abnormal noise check out and call AZ Trane for Service. | 2016-09-01 - 18080 - AZ Trane started tear down on 8/29/16 estimated completion is 9/30/2016 - Thomas Wienand; 2016-10-07 - 18080 - Thomas Wienand-Trane update, They will be on site on 10\\\\10/16 to continue work on chiller 4 - Thomas Wienand; 2016-10-17 - 18080 - Thomas Wienand-UPDATE: Chiller being reassembled should be complete by 10/21/16 - Thomas Wienand; 2016-10-21 - 18080 - Thomas Wienand-Repairs complete chiller four back on line, no cost covered under the service agreement. unit rebuilt new factory motor due to open rotor bar again. - Thomas Wienand | Chiller 4 Abnormal noise check out and call AZ Trane for Service. 2016-09-01 - 18080 - AZ Trane started tear down on 8/29/16 estimated completion is 9/30/2016 - Thomas Wienand; 2016-10-07 - 18080 - Thomas Wienand-Trane update, They will be on site on 10\\\\10/16 to continue work on chiller 4 - Thomas Wienand; 2016-10-17 - 18080 - Thomas Wienand-UPDATE: Chiller being reassembled should be complete by 10/21/16 - Thomas Wienand; 2016-10-21 - 18080 - Thomas Wienand-Repairs complete chiller four back on line, no cost covered under the service agreement. unit rebuilt new factory motor due to open rotor bar again. - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 4905 | WEST-106344 | Fan coil unit needs filters changed. | 2016-09-02 - 18170 - Chad T Ball-Replaced 20x20x2 filters (2) - Chad T Ball | Fan coil unit needs filters changed. 2016-09-02 - 18170 - Chad T Ball-Replaced 20x20x2 filters (2) - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-30 | 65412 | TMPE-184746 | MWO TOWERA 131A1 HVAC TOWER A 131A1: A/C blows cool but not enough to cool down room. 42B1A9B | 2016-09-02 - 18290 - Thomas Gibble-pump was getting fix and everything is cooling - Thomas Gibble; 2016-09-02 - 18290 - Gail Jackson-pump was getting fix and everything is cooling - Thomas Gibble | MWO TOWERA 131A1 HVAC TOWER A 131A1: A/C blows cool but not enough to cool down room. 42B1A9B 2016-09-02 - 18290 - Thomas Gibble-pump was getting fix and everything is cooling - Thomas Gibble; 2016-09-02 - 18290 - Gail Jackson-pump was getting fix and everything is cooling - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 65448 | TMPE-184710 | MWO: need electrical to install on and off switches for controls !! Please create service request for HVAC shop to restart control air compressor for pneumatic stats for temp control thanks Jeffrey 4N00ABB | 2016-09-02 - 15000 - Arthur Gonzales-trblsht mi 1 and m2 mags and alt. mech jose will order a starter for m1. suspect it is defective. - Arthur Gonzales | MWO: need electrical to install on and off switches for controls !! Please create service request for HVAC shop to restart control air compressor for pneumatic stats for temp control thanks Jeffrey 4N00ABB 2016-09-02 - 15000 - Arthur Gonzales-trblsht mi 1 and m2 mags and alt. mech jose will order a starter for m1. suspect it is defective. - Arthur Gonzales | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-08-30 | 65452 | TMPE-184706 | FIRST CALL HVAC SHOP MWO: !! Classroom 202 is HOT. Please send someone out to correct the situation ASAP because we hold classes in this room. Thanks for the support, George Harris 42AMFKL | 2016-09-02 - 18290 - Gail Jackson-pump is fix and everything is cooling - Thomas Gibble; 2016-09-02 - 18290 - Thomas Gibble-pump is fix and everything is cooling - Thomas Gibble | FIRST CALL HVAC SHOP MWO: !! Classroom 202 is HOT. Please send someone out to correct the situation ASAP because we hold classes in this room. Thanks for the support, George Harris 42AMFKL 2016-09-02 - 18290 - Gail Jackson-pump is fix and everything is cooling - Thomas Gibble; 2016-09-02 - 18290 - Thomas Gibble-pump is fix and everything is cooling - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 65457 | TMPE-184701 | MWO: The fan motor is seized. | NA | MWO: The fan motor is seized. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65458 | TMPE-184700 | MWO: The fan motor is seized. | NA | MWO: The fan motor is seized. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65459 | TMPE-184699 | MWO: The fan motor is seized and the cover is missing from the bottom of the unit. | NA | MWO: The fan motor is seized and the cover is missing from the bottom of the unit. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65461 | TMPE-184697 | MWO: The fan motor is seized and was found disconnected from its power source. | NA | MWO: The fan motor is seized and was found disconnected from its power source. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65463 | TMPE-184695 | MWO: The fan motor is seized. | NA | MWO: The fan motor is seized. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65471 | TMPE-184687 | MWO: The fan on the unit isn't working. The fan coil is located in the ceiling next to the west stairwell on the 2nd fl. | NA | MWO: The fan on the unit isn't working. The fan coil is located in the ceiling next to the west stairwell on the 2nd fl. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-30 | 65472 | TMPE-184686 | MWO: !! This is Prof. Jones' lab. The vents are extremely dirty and need to be cleaned, particles are starting to fall and interferring with equipment and experiments. Before you do anything please contact Dr. Jones. All equipment will need to be covered by tarp/plastic prior to any cleaning. Co. . . | 2016-10-05 - 18010 - Jennifer Moyer-Assessed job. This is a lab with lots of exhaust fans that have the potential to pull air from the hall and outside. Customer informed me that the windows were recently sealed to help keep dust out. It has been determined that the best course of action for our shop is to clean the registers and install additional filter material over the supplies. Sheet metal shop is currently measuring for filter racks. - Jennifer Moyer; 2016-10-05 - 18010 - Midhat Mukanovic-Assessed job. This is a lab with lots of exhaust fans that have the potential to pull air from the hall and outside. Customer informed me that the windows were recently sealed to help keep dust out. It has been determined that the best course of action for our shop is to clean the registers and install additional filter material over the supplies. Sheet metal shop is currently measuring for filter racks. - Jennifer Moyer; 2016-10-18 - 18010 - Carl Karr-Measure duct for new registers. - Carl Karr; 2016-11-02 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-02 - 18010 - Carl Karr-Fabricate filter box. - Carl Karr; 2016-11-04 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-07 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-18 - 18010 - Carl Karr-Install new registers to filter boxes. - Carl Karr; 2016-11-21 - 18010 - Carl Karr-Fabricate and install two filter boxes and two new registers. - Carl Karr; 2016-11-21 - 18010 - Gail Jackson-Fabricate and install two filter boxes and two new registers. - Carl Karr; 2016-11-21 - 18010 - Zhi Yu-Fabricate and install two filter boxes and two new registers. - Carl Karr | MWO: !! This is Prof. Jones' lab. The vents are extremely dirty and need to be cleaned, particles are starting to fall and interferring with equipment and experiments. Before you do anything please contact Dr. Jones. All equipment will need to be covered by tarp/plastic prior to any cleaning. Co. . . 2016-10-05 - 18010 - Jennifer Moyer-Assessed job. This is a lab with lots of exhaust fans that have the potential to pull air from the hall and outside. Customer informed me that the windows were recently sealed to help keep dust out. It has been determined that the best course of action for our shop is to clean the registers and install additional filter material over the supplies. Sheet metal shop is currently measuring for filter racks. - Jennifer Moyer; 2016-10-05 - 18010 - Midhat Mukanovic-Assessed job. This is a lab with lots of exhaust fans that have the potential to pull air from the hall and outside. Customer informed me that the windows were recently sealed to help keep dust out. It has been determined that the best course of action for our shop is to clean the registers and install additional filter material over the supplies. Sheet metal shop is currently measuring for filter racks. - Jennifer Moyer; 2016-10-18 - 18010 - Carl Karr-Measure duct for new registers. - Carl Karr; 2016-11-02 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-02 - 18010 - Carl Karr-Fabricate filter box. - Carl Karr; 2016-11-04 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-07 - 18010 - Carl Karr-Fabricate filter boxes. - Carl Karr; 2016-11-18 - 18010 - Carl Karr-Install new registers to filter boxes. - Carl Karr; 2016-11-21 - 18010 - Carl Karr-Fabricate and install two filter boxes and two new registers. - Carl Karr; 2016-11-21 - 18010 - Gail Jackson-Fabricate and install two filter boxes and two new registers. - Carl Karr; 2016-11-21 - 18010 - Zhi Yu-Fabricate and install two filter boxes and two new registers. - Carl Karr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2016-08-30 | 65509 | TMPE-184649 | MWO LSD: !! attn HVAC shop - Evap cooler for this room/mini greenhouse is not blowing cool air. Suspect pump is down since pads do not appear wet from outside. Please repair ASAP. Contact Name: Mike Comroe Contact Phone Number: 480-965-2166 Contact Email: mcomroe@asu.edu 4NBKECM | 2016-09-13 - 18150 - Jennifer Moyer-Replaced pump (did not work), so I got another pump from maintenance stores and it did work. I cleaned all the debris from the inside of this unit. This job takes a good amount of time because you have to set up an extension ladder and take your time hauling the wet vacuum, tools, and parts up the ladder. Also, you have to get staff to open the door to turn off/on a breaker if you need to. - Jennifer Moyer | MWO LSD: !! attn HVAC shop - Evap cooler for this room/mini greenhouse is not blowing cool air. Suspect pump is down since pads do not appear wet from outside. Please repair ASAP. Contact Name: Mike Comroe Contact Phone Number: 480-965-2166 Contact Email: mcomroe@asu.edu 4NBKECM 2016-09-13 - 18150 - Jennifer Moyer-Replaced pump (did not work), so I got another pump from maintenance stores and it did work. I cleaned all the debris from the inside of this unit. This job takes a good amount of time because you have to set up an extension ladder and take your time hauling the wet vacuum, tools, and parts up the ladder. Also, you have to get staff to open the door to turn off/on a breaker if you need to. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-08-30 | 177770 | RFMT-130561 | RES LIFE / Paint: Please patch and paint ceiling damage over entry desk by a/c vent | 2016-09-07 - 22000 - James Evans-ceiling repair complete - James Evans | RES LIFE / Paint: Please patch and paint ceiling damage over entry desk by a/c vent 2016-09-07 - 22000 - James Evans-ceiling repair complete - James Evans | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 216719 | RACC-111891 | !! I believe there is mold in my air conditioning vent and would really like this checked out as soon as possible. There is both a smell and brown dots on the blades of the vent. 4NNCMGC | NA | !! I believe there is mold in my air conditioning vent and would really like this checked out as soon as possible. There is both a smell and brown dots on the blades of the vent. 4NNCMGC NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 235471 | POLY-112728 | !! Air conditioner isn't working and it makes a screeching noise while on the low setting. Contact Name: Tara Tingey Contact Phone Number: 4802541058 Contact Email: Tmtingey@asu.edu 4NEAL36 | NA | !! Air conditioner isn't working and it makes a screeching noise while on the low setting. Contact Name: Tara Tingey Contact Phone Number: 4802541058 Contact Email: Tmtingey@asu.edu 4NEAL36 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-30 | 235488 | POLY-112711 | !! A/C broken, blows air but only warm air. Kept the temp. between 71-80 since move in date. 4NI1GN5 | NA | !! A/C broken, blows air but only warm air. Kept the temp. between 71-80 since move in date. 4NI1GN5 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-08-30 | 257056 | DTPC-111482 | Move air return to other side of room 4N5G1LJ | 2016-08-30 - 18010 - Richard Noland-Went by and spoke with tenet, will move vent on WED. - Richard Noland; 2016-09-01 - 18010 - Richard Noland-Got ladder, moved return grill from s/e corner of room to n/e corner. WO is complete. - Richard Noland | Move air return to other side of room 4N5G1LJ 2016-08-30 - 18010 - Richard Noland-Went by and spoke with tenet, will move vent on WED. - Richard Noland; 2016-09-01 - 18010 - Richard Noland-Got ladder, moved return grill from s/e corner of room to n/e corner. WO is complete. - Richard Noland | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 63544 | TMPE-186614 | FACTORY MOTOR PARTS CCA585 RC95 TOTAL 73.44 | NA | FACTORY MOTOR PARTS CCA585 RC95 TOTAL 73.44 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 65119 | TMPE-185039 | MWO: PEBW ASUHC-Agent: Ahmed Khalil Description: AC is not working in main gym Who was dispatched: Roque Garcia Time of dispatch: 7:29PM Initially called EMS Robert Zaller. He referred me to HVAC to take a look at the issue since he thought the main gym might use swamp coolers. Called Roque . . . | 2016-09-01 - 18290 - Robert Zaller-Looked up the system. It is cooled by evap units. Coordinated with call center. - Robert Zaller | MWO: PEBW ASUHC-Agent: Ahmed Khalil Description: AC is not working in main gym Who was dispatched: Roque Garcia Time of dispatch: 7:29PM Initially called EMS Robert Zaller. He referred me to HVAC to take a look at the issue since he thought the main gym might use swamp coolers. Called Roque . . . 2016-09-01 - 18290 - Robert Zaller-Looked up the system. It is cooled by evap units. Coordinated with call center. - Robert Zaller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 65145 | TMPE-185013 | SWO: !! There is no AC at the Concierge area on the 3rd floor of the Suites in SDS. PO is YG202004971. This is urgent with a football game in 3 days. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF | 2016-08-31 - 18290 - CALLED TO BRIAN. - Monica Moraga; 2016-09-01 - 18290 - Dispatched to techs this morning. Was priortized as emergency due to stadium issues. Changed to urgent status. - Brian Qualls; 2016-09-06 - 18290 - Zhi Yu-On Aug 29,16. We set-up all Refrigerator, ice Machine, Condensation pump, Clean bin and A/C. We isolate problem room to room with notices. from Room 306 to 212. - Zhi Yu; 2016-09-06 - 18290 - Zhi Yu-Addressing the problem lists. Replaced condensate 1,2,3 floor. ON the third floor area 323 no a/c. We flush 3 water coil, and replace 1 blower motor.. - Zhi Yu [Modified: 2016-09-06 Zhi Yu]; 2016-09-06 - 18290 - Zhi Yu-Concierge Area water coil located in the server room 323 Actuator clog-up. We flushing and flushing able to drop temp to 68 deg. Will need to replace new actuator. Catering kitchen 1st and 2nd floor no A/C. Replaced blower motor 1/3hp in second floor, and replaced t/sat first floor... In Room 122 Charge up 10oz R134a - Zhi Yu | SWO: !! There is no AC at the Concierge area on the 3rd floor of the Suites in SDS. PO is YG202004971. This is urgent with a football game in 3 days. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF 2016-08-31 - 18290 - CALLED TO BRIAN. - Monica Moraga; 2016-09-01 - 18290 - Dispatched to techs this morning. Was priortized as emergency due to stadium issues. Changed to urgent status. - Brian Qualls; 2016-09-06 - 18290 - Zhi Yu-On Aug 29,16. We set-up all Refrigerator, ice Machine, Condensation pump, Clean bin and A/C. We isolate problem room to room with notices. from Room 306 to 212. - Zhi Yu; 2016-09-06 - 18290 - Zhi Yu-Addressing the problem lists. Replaced condensate 1,2,3 floor. ON the third floor area 323 no a/c. We flush 3 water coil, and replace 1 blower motor.. - Zhi Yu [Modified: 2016-09-06 Zhi Yu]; 2016-09-06 - 18290 - Zhi Yu-Concierge Area water coil located in the server room 323 Actuator clog-up. We flushing and flushing able to drop temp to 68 deg. Will need to replace new actuator. Catering kitchen 1st and 2nd floor no A/C. Replaced blower motor 1/3hp in second floor, and replaced t/sat first floor... In Room 122 Charge up 10oz R134a - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-31 | 65152 | TMPE-185006 | MWO: A/C not working. 4NIL577 | 2016-08-31 - 18290 - CALLED TO STANDBY MIKE C @4:14PM. - Monica Moraga; 2016-09-01 - 18290 - 8-31-16 I came in, found faulty fan coil relay. I made temporary adjustment to start fan. sb - Mike Cozens | MWO: A/C not working. 4NIL577 2016-08-31 - 18290 - CALLED TO STANDBY MIKE C @4:14PM. - Monica Moraga; 2016-09-01 - 18290 - 8-31-16 I came in, found faulty fan coil relay. I made temporary adjustment to start fan. sb - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-31 | 65165 | TMPE-184993 | SWO: 8/31/16 The bathroom fan in room # 132a is not working. Bill to TL502001138. Please remember nap time. 42A042B | 2016-10-21 - 18010 - Gail Jackson-removed ex fan motor - Thomas Gibble; 2016-10-21 - 18010 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18010 - Gail Jackson-replaced motor - Thomas Gibble | SWO: 8/31/16 The bathroom fan in room # 132a is not working. Bill to TL502001138. Please remember nap time. 42A042B 2016-10-21 - 18010 - Gail Jackson-removed ex fan motor - Thomas Gibble; 2016-10-21 - 18010 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18010 - Gail Jackson-replaced motor - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-31 | 65169 | TMPE-184989 | **Insurance Claim** Insurance Claim: Wilson Hall: 5 x 3 bell reducer on chilled water 2nd floor next to room 242 failed, and water flooded down to the 1st floor lobby. Plumbing and Carpentry will be involved and ATI restoration company was called for clean up. | 2016-09-08 - 10090 - 8/30/16 Jennifer Moyer .75 OT needs emergency AC 8/30/16 Roque Garcia 4 hr. OT install portable AC units. bldg. chilled water off 8/30/16 Michael Kelley 2.5 hr. CTE install portable AC units, building chilled water off emergency shutdown, 5 inch line broken 8/31/16 Michael Kelley 5 hr. OT emergency shutdown chilled water/installed portable /AC units, assisted PL shop 9/1/16 Michael Kelley 5 hr. OT emergency repair on chilled water line, assist PL shop, packed up portable AC units 9/1/16 Roque Garcia 5 hr. OT emergency chilled water repair, packed up portable units 9/4/16 Brian Qualls 2.5 hr. OT helped Robert with chilled water pump motor - Juliana Blusiewicz; 2016-09-26 - 10090 - 8/30/2016 2.5 OT 6:30am-9am Michael Kelley - WILSON Install portable A/C units. Building chilled water off. Emergency shutdown - Kerri Perkins | **Insurance Claim** Insurance Claim: Wilson Hall: 5 x 3 bell reducer on chilled water 2nd floor next to room 242 failed, and water flooded down to the 1st floor lobby. Plumbing and Carpentry will be involved and ATI restoration company was called for clean up. 2016-09-08 - 10090 - 8/30/16 Jennifer Moyer .75 OT needs emergency AC 8/30/16 Roque Garcia 4 hr. OT install portable AC units. bldg. chilled water off 8/30/16 Michael Kelley 2.5 hr. CTE install portable AC units, building chilled water off emergency shutdown, 5 inch line broken 8/31/16 Michael Kelley 5 hr. OT emergency shutdown chilled water/installed portable /AC units, assisted PL shop 9/1/16 Michael Kelley 5 hr. OT emergency repair on chilled water line, assist PL shop, packed up portable AC units 9/1/16 Roque Garcia 5 hr. OT emergency chilled water repair, packed up portable units 9/4/16 Brian Qualls 2.5 hr. OT helped Robert with chilled water pump motor - Juliana Blusiewicz; 2016-09-26 - 10090 - 8/30/2016 2.5 OT 6:30am-9am Michael Kelley - WILSON Install portable A/C units. Building chilled water off. Emergency shutdown - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-08-31 | 65174 | TMPE-184984 | MWO: White noise sound and/or air conditioning fans in the staff work area and the front desk, disappeared this afternoon (all of a sudden), and we can hear everything across the work space. 4NNE49C | 2016-08-31 - 10010 - John Snider-Work In Progress Called Requester, left message for a call back to get more info and a time to meet. 0.25 Hours Materials: None. - John Snider; 2016-09-08 - 10010 - John Crocker-Tech Assist - John Crocker; 2016-09-16 - 10010 - John Snider-Work In Progress Investigated speakers in ceiling tried to trace conduit to controller. Asked occupant in supply room and was given contact info for the old building manager that explained the issue on why the noise was shut off. 1.0 Hours Materials: None - John Snider; 2016-09-16 - 10010 - John Snider-Work In Progress Located White Noise Box called to get Key and will be out of town until Wednesday 9/7. 0.5 Hours. Materials: None. - John Snider; 2016-09-16 - 10010 - John Snider-Work In Progress Get Box unlocked reviewed how system was wired. Will return with Tech assist to find the wire for the 3rd floor only. 0.5 Hours. Materials: None. - John Snider; 2016-09-16 - 10010 - John Snider-Completed With Tech Assist confirmed wire for 3rd Floor. Double checked 4th Floor that if was clear of noise. Reviewed with Requester and with his help adjusted final volume. 1.5 Hours. Materials: None. - John Snider | MWO: White noise sound and/or air conditioning fans in the staff work area and the front desk, disappeared this afternoon (all of a sudden), and we can hear everything across the work space. 4NNE49C 2016-08-31 - 10010 - John Snider-Work In Progress Called Requester, left message for a call back to get more info and a time to meet. 0.25 Hours Materials: None. - John Snider; 2016-09-08 - 10010 - John Crocker-Tech Assist - John Crocker; 2016-09-16 - 10010 - John Snider-Work In Progress Investigated speakers in ceiling tried to trace conduit to controller. Asked occupant in supply room and was given contact info for the old building manager that explained the issue on why the noise was shut off. 1.0 Hours Materials: None - John Snider; 2016-09-16 - 10010 - John Snider-Work In Progress Located White Noise Box called to get Key and will be out of town until Wednesday 9/7. 0.5 Hours. Materials: None. - John Snider; 2016-09-16 - 10010 - John Snider-Work In Progress Get Box unlocked reviewed how system was wired. Will return with Tech assist to find the wire for the 3rd floor only. 0.5 Hours. Materials: None. - John Snider; 2016-09-16 - 10010 - John Snider-Completed With Tech Assist confirmed wire for 3rd Floor. Double checked 4th Floor that if was clear of noise. Reviewed with Requester and with his help adjusted final volume. 1.5 Hours. Materials: None. - John Snider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-08-31 | 65220 | TMPE-184938 | SWO: !! It is hot in suite 108 in the Suites. PO for HVAC is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Pete.Wozniak@asu.edu 42BDEDF | 2016-08-31 - 18290 - Called Pete Wozniak at 2:56pm. Thru conversation we determined this is not an Emergency, but can be addressed Thursday morning 9/1/16. Will make our techs aware of urgency as wallpaper is affected. - Brian Qualls; 2016-09-02 - 18290 - Derek Gittings-cleaning coils, water lines, replacing motors. - Melanie Lamm; 2016-09-27 - 18290 - Roque Garcia-Assisted and repaired the list of problems submitted by Pete. Derek, MIT, Michael and I were at the stadium. - Roque Garcia | SWO: !! It is hot in suite 108 in the Suites. PO for HVAC is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Pete.Wozniak@asu.edu 42BDEDF 2016-08-31 - 18290 - Called Pete Wozniak at 2:56pm. Thru conversation we determined this is not an Emergency, but can be addressed Thursday morning 9/1/16. Will make our techs aware of urgency as wallpaper is affected. - Brian Qualls; 2016-09-02 - 18290 - Derek Gittings-cleaning coils, water lines, replacing motors. - Melanie Lamm; 2016-09-27 - 18290 - Roque Garcia-Assisted and repaired the list of problems submitted by Pete. Derek, MIT, Michael and I were at the stadium. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-31 | 65244 | TMPE-184914 | Found the compressor locked up and the crankcase full of water. Drained the water, flushed and filled the case with oil. the pump is still locked up. | NA | Found the compressor locked up and the crankcase full of water. Drained the water, flushed and filled the case with oil. the pump is still locked up. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-08-31 | 65310 | TMPE-184848 | MWO IRISHA 121 There is black mold growing out of the ac unit hanging from the ceiling in this room. EH&S has been notified. Please inspect and service asap, thank you. | 2016-08-31 - 18010 - Per John Howell, put technician on hold for this to speak with EH&amp;S. Spoke with John Lemanski @ EH&amp;S, they will look into. - Brian Qualls; 2016-09-13 - 18010 - Jennifer Moyer just stopped by Jen Gorney's desk regarding the call below. I called the customer directly and informed her that it wasn\\u2019t black mold; the filters are disintegrating. I also told her that we\\u2019ve asked Custodial to mop up the debris on the floor. She still may go ahead with the air quality testing, which I told her is fine, and she does that at her own discretion. - Jennifer Gorney; 2016-09-13 - 18010 - Jennifer Moyer-Removed disintegrated foam filter from the coils, drain pan, and condensate drain with portable coil cleaner and a vacuum. This black filter plugged the coils and plugged the drain. Reinstalled motor assembly, cleaned the outside of the unit, and installed a new filter. - Jennifer Moyer; 2016-09-13 - 18010 - Jennifer Moyer-Removed grill, blower assembly, and dirty filter. Blew out blower assembly with air and washed grill with cleaning agent with bleach additive. Sprayed foam coil cleaner on coils to soak. - Jennifer Moyer; 2016-09-13 - 18010 - Jennifer Moyer-Looked at unit. Instructed to wait on EHS determination. - Jennifer Moyer | MWO IRISHA 121 There is black mold growing out of the ac unit hanging from the ceiling in this room. EH&S has been notified. Please inspect and service asap, thank you. 2016-08-31 - 18010 - Per John Howell, put technician on hold for this to speak with EH&amp;S. Spoke with John Lemanski @ EH&amp;S, they will look into. - Brian Qualls; 2016-09-13 - 18010 - Jennifer Moyer just stopped by Jen Gorney's desk regarding the call below. I called the customer directly and informed her that it wasn\\u2019t black mold; the filters are disintegrating. I also told her that we\\u2019ve asked Custodial to mop up the debris on the floor. She still may go ahead with the air quality testing, which I told her is fine, and she does that at her own discretion. - Jennifer Gorney; 2016-09-13 - 18010 - Jennifer Moyer-Removed disintegrated foam filter from the coils, drain pan, and condensate drain with portable coil cleaner and a vacuum. This black filter plugged the coils and plugged the drain. Reinstalled motor assembly, cleaned the outside of the unit, and installed a new filter. - Jennifer Moyer; 2016-09-13 - 18010 - Jennifer Moyer-Removed grill, blower assembly, and dirty filter. Blew out blower assembly with air and washed grill with cleaning agent with bleach additive. Sprayed foam coil cleaner on coils to soak. - Jennifer Moyer; 2016-09-13 - 18010 - Jennifer Moyer-Looked at unit. Instructed to wait on EHS determination. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-08-31 | 65314 | TMPE-184844 | SWO: !! The AC is out at the Soccer Facility. Need someone out ASAP. PO is YG202004940. Thank you. Contact Name: Josh Perry Contact Phone Number: 480-544-8549 Contact Email: Joshua.Perry@asu.edu 42BDEDF | 2016-09-02 - 18010 - Carl Karr-Fabricate duct. Disconnect two spot coolers. - Carl Karr; 2016-09-02 - 18010 - Carl Karr-Fabricate duct. Hook up two spot coolers. - Carl Karr; 2016-09-08 - 18010 - Zhi Yu-arrived resetting the alarm couple time . unit off on alarm error. Turn out to be bad condenser fan motor. - Zhi Yu | SWO: !! The AC is out at the Soccer Facility. Need someone out ASAP. PO is YG202004940. Thank you. Contact Name: Josh Perry Contact Phone Number: 480-544-8549 Contact Email: Joshua.Perry@asu.edu 42BDEDF 2016-09-02 - 18010 - Carl Karr-Fabricate duct. Disconnect two spot coolers. - Carl Karr; 2016-09-02 - 18010 - Carl Karr-Fabricate duct. Hook up two spot coolers. - Carl Karr; 2016-09-08 - 18010 - Zhi Yu-arrived resetting the alarm couple time . unit off on alarm error. Turn out to be bad condenser fan motor. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2016-08-31 | 65326 | TMPE-184832 | MWO: !! The brand new bottle filler water cooler outside of PSH349W1 is not working. Please fix ASAP. 42AE9GB | NA | MWO: !! The brand new bottle filler water cooler outside of PSH349W1 is not working. Please fix ASAP. 42AE9GB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 177696 | RFMT-130635 | !! Repeat Request. ac not working properly. 4O0LMJ9 | 2016-09-01 - 18010 - Joe Swan-A/C working fine, opened up vents more in bedroom. Temp was 62 coming out of vent. complete - Joe Swan | !! Repeat Request. ac not working properly. 4O0LMJ9 2016-09-01 - 18010 - Joe Swan-A/C working fine, opened up vents more in bedroom. Temp was 62 coming out of vent. complete - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 177703 | RFMT-130628 | !! A/C unit makes loud banging noise when turning off/on. Has gotten progressively louder and longer over last few weeks. Contact Name: Contact Phone Number: 5207302331 Contact Email: 4NC34LN | 2016-09-01 - 18010 - Simon Fernandez-removed blower assemble, cleaned motor and blower assemble, reinstalled assembly. Unit did not make any unusual noises at this time. Also checked vents and return air vent. - Simon Fernandez | !! A/C unit makes loud banging noise when turning off/on. Has gotten progressively louder and longer over last few weeks. Contact Name: Contact Phone Number: 5207302331 Contact Email: 4NC34LN 2016-09-01 - 18010 - Simon Fernandez-removed blower assemble, cleaned motor and blower assemble, reinstalled assembly. Unit did not make any unusual noises at this time. Also checked vents and return air vent. - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-31 | 177704 | RFMT-130627 | !! Repeat Request. Resident called and said their roof is leaking. 4NL0LGG | 2016-09-01 - 13120 - Simon Fernandez-checked ceiling found a/c condensate drain line clogged. Cleared clog flushed with water,checked okay. - Simon Fernandez | !! Repeat Request. Resident called and said their roof is leaking. 4NL0LGG 2016-09-01 - 13120 - Simon Fernandez-checked ceiling found a/c condensate drain line clogged. Cleared clog flushed with water,checked okay. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 235429 | POLY-112770 | We need our dryer vent cleared out please. I have cleared out our dryer and hose to the wall 4N8D9OL | NA | We need our dryer vent cleared out please. I have cleared out our dryer and hose to the wall 4N8D9OL NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 235463 | POLY-112736 | BILLED CALLED FLOYD !! Lights and air conditioning are out in our work area. Wall sockets have power. 42AEL8D BILL TO MOHAMMAD'S ULA PROJECT PER FLOYD. USE BLANKET PO #PM602000290 | NA | BILLED CALLED FLOYD !! Lights and air conditioning are out in our work area. Wall sockets have power. 42AEL8D BILL TO MOHAMMAD'S ULA PROJECT PER FLOYD. USE BLANKET PO #PM602000290 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-08-31 | 256991 | DTPC-111547 | Call Baldor Motor and talk to tech about pump motors for PM's | 2016-09-01 - 18230 - Thomas Klein-Called Baldor Motor and talk to tech about pump motors for PM's - Thomas Klein | Call Baldor Motor and talk to tech about pump motors for PM's 2016-09-01 - 18230 - Thomas Klein-Called Baldor Motor and talk to tech about pump motors for PM's - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-08-31 | 257020 | DTPC-111518 | Collect information and clean filter on evaporator units. Capture info on a spreadsheet. | 2016-08-31 - 10000 - James Hermann-clean filter and capture unit information. Needed to make several trips with the cart as well. - James Hermann; 2016-08-31 - 10000 - Robert Bartels-assist with work - James Hermann; 2016-09-01 - 10000 - James Hermann-collect information inside the building and on the roof. Enter into spreadsheet. - James Hermann; 2016-09-01 - 10000 - Robert Bartels-collect information with the interior units. - James Hermann; 2016-09-01 - 10000 - Bruce Pickford-Assisted with collection of HVAC information per Stephen - James Hermann; 2016-09-08 - 10000 - James Hermann-Go to GSS with Jose to further identify HVAC equipment and filters. Spend time inside as well as on the roof - James Hermann; 2016-09-08 - 10000 - Jose Acero-Go to GSS with Jim to further identify HVAC equipment and filters. Spend time inside as well as on the roof - James Hermann; 2016-09-08 - 10000 - James Hermann-Went to GSS with Stephen and collected the final equipment information for inclusion on the spreadsheet or equipment list. Also created a filter list and submitted for TMA PM workorders - James Hermann | Collect information and clean filter on evaporator units. Capture info on a spreadsheet. 2016-08-31 - 10000 - James Hermann-clean filter and capture unit information. Needed to make several trips with the cart as well. - James Hermann; 2016-08-31 - 10000 - Robert Bartels-assist with work - James Hermann; 2016-09-01 - 10000 - James Hermann-collect information inside the building and on the roof. Enter into spreadsheet. - James Hermann; 2016-09-01 - 10000 - Robert Bartels-collect information with the interior units. - James Hermann; 2016-09-01 - 10000 - Bruce Pickford-Assisted with collection of HVAC information per Stephen - James Hermann; 2016-09-08 - 10000 - James Hermann-Go to GSS with Jose to further identify HVAC equipment and filters. Spend time inside as well as on the roof - James Hermann; 2016-09-08 - 10000 - Jose Acero-Go to GSS with Jim to further identify HVAC equipment and filters. Spend time inside as well as on the roof - James Hermann; 2016-09-08 - 10000 - James Hermann-Went to GSS with Stephen and collected the final equipment information for inclusion on the spreadsheet or equipment list. Also created a filter list and submitted for TMA PM workorders - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 4960 | WEST-106289 | Pump-DIP-001 | 2016-09-16 - 23100 - Randy Randell-pump motor may need bearings. - Randy Randell | Pump-DIP-001 2016-09-16 - 23100 - Randy Randell-pump motor may need bearings. - Randy Randell | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-01 | 5078 | WEST-106171 | Exhaust Fan-EFU-004 | 2016-10-15 - 18160 - Ronald Chaffee-Checked v-belt, OK. Greased blower shaft bearings. Could not get grease to go into the upper bearing. It will need a new alemite fitting. - Ronald Chaffee; 2016-10-17 - 18160 - Ronald Chaffee-Replaced upper grease fitting and greased bearing. - Ronald Chaffee | Exhaust Fan-EFU-004 2016-10-15 - 18160 - Ronald Chaffee-Checked v-belt, OK. Greased blower shaft bearings. Could not get grease to go into the upper bearing. It will need a new alemite fitting. - Ronald Chaffee; 2016-10-17 - 18160 - Ronald Chaffee-Replaced upper grease fitting and greased bearing. - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 62014 | TMPE-188143 | Water Filter Replacement | 2016-09-21 - xPM-2202 - Gail Jackson-Trip to ACE for filters, install filters. - Gail Jackson; 2016-09-21 - xPM-2202 - Thomas Gibble-Trip to ACE for filters, install filters. - Gail Jackson; 2016-09-23 - xPM-2202 - Gail Jackson-Trip to warehouse for cleaner and clean ice machine. Install new filters. Sanitize. Complete - Gail Jackson; 2016-09-23 - xPM-2202 - Thomas Gibble-Trip to warehouse for cleaner and clean ice machine. Install new filters. Sanitize. Complete - Gail Jackson | Water Filter Replacement 2016-09-21 - xPM-2202 - Gail Jackson-Trip to ACE for filters, install filters. - Gail Jackson; 2016-09-21 - xPM-2202 - Thomas Gibble-Trip to ACE for filters, install filters. - Gail Jackson; 2016-09-23 - xPM-2202 - Gail Jackson-Trip to warehouse for cleaner and clean ice machine. Install new filters. Sanitize. Complete - Gail Jackson; 2016-09-23 - xPM-2202 - Thomas Gibble-Trip to warehouse for cleaner and clean ice machine. Install new filters. Sanitize. Complete - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 62015 | TMPE-188142 | Water Filter Replacement | 2016-09-20 - xPM-2202 - Gail Jackson-Cleaned machine, trip to Tru-Temp for parts. Found leak in dump line and machine very dirty. Run test COMPLETE - Gail Jackson; 2016-09-20 - xPM-2202 - Thomas Gibble-Cleaned machine, trip to Tru-Temp for parts. Found leak in dump line and machine very dirty. Run test COMPLETE - Gail Jackson | Water Filter Replacement 2016-09-20 - xPM-2202 - Gail Jackson-Cleaned machine, trip to Tru-Temp for parts. Found leak in dump line and machine very dirty. Run test COMPLETE - Gail Jackson; 2016-09-20 - xPM-2202 - Thomas Gibble-Cleaned machine, trip to Tru-Temp for parts. Found leak in dump line and machine very dirty. Run test COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 64890 | TMPE-185268 | MWO Music W121: Please have HVAC shop flush this fan coil. It seems clogged. Thanks. 42C3NC4 | 2017-05-10 - 18090 - Jennifer Moyer-Talked to Requester. Problem was not a clogged coil and it has been resolved. - Jennifer Moyer | MWO Music W121: Please have HVAC shop flush this fan coil. It seems clogged. Thanks. 42C3NC4 2017-05-10 - 18090 - Jennifer Moyer-Talked to Requester. Problem was not a clogged coil and it has been resolved. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 64933 | TMPE-185225 | MWO USE 103 HVAC added to check out HP5, the cooling unit is not working. EMS WO#185142, HVAC WO# Please lower the temperature in this room. It is too warm, thank you! | 2016-09-13 - 18290 - Roque Garcia-Reset the condensate overflow switch located in the AHU which caused the power loss to the tstat. - Roque Garcia | MWO USE 103 HVAC added to check out HP5, the cooling unit is not working. EMS WO#185142, HVAC WO# Please lower the temperature in this room. It is too warm, thank you! 2016-09-13 - 18290 - Roque Garcia-Reset the condensate overflow switch located in the AHU which caused the power loss to the tstat. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 64954 | TMPE-185204 | MWO: CSB 308C, 309, 310A There's little air conditioning in these rooms and it's pretty warm. Please adjust asap. | 2016-09-02 - 18290 - Robert Zaller-Diagnosed the HVAC and pneumatic systems. Found the Chillers are not working properly. Coordinated with HVAC shop, Brian. - Robert Zaller | MWO: CSB 308C, 309, 310A There's little air conditioning in these rooms and it's pretty warm. Please adjust asap. 2016-09-02 - 18290 - Robert Zaller-Diagnosed the HVAC and pneumatic systems. Found the Chillers are not working properly. Coordinated with HVAC shop, Brian. - Robert Zaller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 64969 | TMPE-185189 | MWO BA 449U1 BT to HVAC- AC unit is leaking causing the water flow There is active water coming out of this room, possibly from the floor drain/sink? Please inspect. Water is running into 318J, which is below it. | 2016-09-01 - 18010 - Called out to John Howell - Amanda Thomas; 2016-09-02 - 18010 - Carl Karr-Clear condensate lines. Fabricate drain pan and trough,and connect to drain. - Carl Karr; 2016-09-15 - 18010 - Carl Karr-Fabricate condensate pans. - Carl Karr; 2016-09-16 - 18010 - Carl Karr-Fabricate and install condensate pans. - Carl Karr | MWO BA 449U1 BT to HVAC- AC unit is leaking causing the water flow There is active water coming out of this room, possibly from the floor drain/sink? Please inspect. Water is running into 318J, which is below it. 2016-09-01 - 18010 - Called out to John Howell - Amanda Thomas; 2016-09-02 - 18010 - Carl Karr-Clear condensate lines. Fabricate drain pan and trough,and connect to drain. - Carl Karr; 2016-09-15 - 18010 - Carl Karr-Fabricate condensate pans. - Carl Karr; 2016-09-16 - 18010 - Carl Karr-Fabricate and install condensate pans. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 64970 | TMPE-185188 | MWO: CSB: Very hot in room 146!!! No airflow!! This is the preschool room!! | 2016-09-01 - 18290 - CALLED TO EMS. ROBERT Z. MM - Monica Moraga; 2016-09-13 - 18290 - Roque Garcia-Replaced blower motor and unit tested normal and cooling - Roque Garcia | MWO: CSB: Very hot in room 146!!! No airflow!! This is the preschool room!! 2016-09-01 - 18290 - CALLED TO EMS. ROBERT Z. MM - Monica Moraga; 2016-09-13 - 18290 - Roque Garcia-Replaced blower motor and unit tested normal and cooling - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 64991 | TMPE-185167 | MWO: Towers A - There is no A/C in the building | 2016-09-01 - 18290 - Emailed to HVAC - Jeri Zappanti; 2016-09-01 - 18290 - Jennifer Moyer-found coupling shredded. Replaced coupling. Found pump side coupling half set screw stripped. Will need new pump side coupling half. upon completion chiller needs to be re-started.(Comp time) - Brian Qualls [Modified: 2016-09-06 Jennifer Moyer]; 2016-09-07 - 18290 - 9/1/16 Jennifer Moyer .5 CTE pump down, hot call, no AC in bldg. , shut motor off, install rubber coupling 9/2/16 Mitchell Andrews 2 hr. OT chilled water pump went down, restarted pump and chiller - Juliana Blusiewicz; 2016-09-08 - 18290 - 9/2/16 Mitchell Andrews 1.25 hr. OT restarted chiller - Juliana Blusiewicz; 2016-09-14 - 18290 - 9/1/2016 .5 CE 5pm-5:30pm Jennifer Moyer - Towers A Tower Center A/ Pump down hot call. NO A/C in building. Shut motor off, install rubber coupling. - Kerri Perkins; 2016-09-23 - 18290 - Mitchell Andrews-11:45 - 2:00 - Jeri Zappanti; 2016-09-26 - 18290 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18290 - Jose Lopez-coupling was broken disconnect motor from pump install new coupling reconnect motor to pump realign pump/motor working @ this time - Jose Lopez; 2016-09-29 - 18290 - Mitchell Andrews-Restarted Chiller - 9/5 called in by Clint Lord &amp; Mike Cozens. Call did not go through 5-3633 3.0 OT - Francesca Fernandez [Modified: 2016-09-29 Francesca Fernandez]; 2016-10-12 - 18290 - Mitchell Andrews-3.00 credited as per payroll - reentered as OTS. - Jeri Zappanti | MWO: Towers A - There is no A/C in the building 2016-09-01 - 18290 - Emailed to HVAC - Jeri Zappanti; 2016-09-01 - 18290 - Jennifer Moyer-found coupling shredded. Replaced coupling. Found pump side coupling half set screw stripped. Will need new pump side coupling half. upon completion chiller needs to be re-started.(Comp time) - Brian Qualls [Modified: 2016-09-06 Jennifer Moyer]; 2016-09-07 - 18290 - 9/1/16 Jennifer Moyer .5 CTE pump down, hot call, no AC in bldg. , shut motor off, install rubber coupling 9/2/16 Mitchell Andrews 2 hr. OT chilled water pump went down, restarted pump and chiller - Juliana Blusiewicz; 2016-09-08 - 18290 - 9/2/16 Mitchell Andrews 1.25 hr. OT restarted chiller - Juliana Blusiewicz; 2016-09-14 - 18290 - 9/1/2016 .5 CE 5pm-5:30pm Jennifer Moyer - Towers A Tower Center A/ Pump down hot call. NO A/C in building. Shut motor off, install rubber coupling. - Kerri Perkins; 2016-09-23 - 18290 - Mitchell Andrews-11:45 - 2:00 - Jeri Zappanti; 2016-09-26 - 18290 - Jose Lopez-work in progress - Jose Lopez; 2016-09-26 - 18290 - Jose Lopez-coupling was broken disconnect motor from pump install new coupling reconnect motor to pump realign pump/motor working @ this time - Jose Lopez; 2016-09-29 - 18290 - Mitchell Andrews-Restarted Chiller - 9/5 called in by Clint Lord &amp; Mike Cozens. Call did not go through 5-3633 3.0 OT - Francesca Fernandez [Modified: 2016-09-29 Francesca Fernandez]; 2016-10-12 - 18290 - Mitchell Andrews-3.00 credited as per payroll - reentered as OTS. - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-09-01 | 65001 | TMPE-185157 | MWO: The a/c in 145 is still not working properly. It switches off by itself in 5 or 10 mins (esp. if running on high). It has to \\u201crest\\u201d for 5 mins before it will turn back on. Plus it has a funny smell. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 | 2016-09-13 - 18010 - Roque Garcia-The unit was working and found that Zhi had replaced the blower motor and Chris from building facilities confirmed and he said unit is working. - Roque Garcia | MWO: The a/c in 145 is still not working properly. It switches off by itself in 5 or 10 mins (esp. if running on high). It has to \\u201crest\\u201d for 5 mins before it will turn back on. Plus it has a funny smell. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 2016-09-13 - 18010 - Roque Garcia-The unit was working and found that Zhi had replaced the blower motor and Chris from building facilities confirmed and he said unit is working. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 65068 | TMPE-185090 | MWO: It has been reported that the walk-in chamber in LSE 438 is not holding temp. Please open a WO for the HVAC shop to address this issue accordingly. Thank you. 4NLGBH4 | 2016-10-13 - 18010 - Oner Munoz-Replaced condenser fan motor; and cycled unit. all good. - Oner Munoz; 2016-10-13 - 18010 - Robert Ecabert-Replaced condenser fan motor; and cycled unit. all good. - Oner Munoz | MWO: It has been reported that the walk-in chamber in LSE 438 is not holding temp. Please open a WO for the HVAC shop to address this issue accordingly. Thank you. 4NLGBH4 2016-10-13 - 18010 - Oner Munoz-Replaced condenser fan motor; and cycled unit. all good. - Oner Munoz; 2016-10-13 - 18010 - Robert Ecabert-Replaced condenser fan motor; and cycled unit. all good. - Oner Munoz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 65080 | TMPE-185078 | SWO SDS 306 !! Please have the HVAC Shop check the ice machine in suite 306 in SDS. It is currently turned off, but we believed it was leaking. PO is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF | 2016-09-01 - 18210 - Dispatched to tech at 11am. They are in area working on another job and will attend to this also. Changed status to urgent. - Brian Qualls; 2016-09-26 - 18210 - Derek Gittings-We Diagnose the cubelet cutter grids not working and water pump acting-up. Do to the age of Unit all parts are obsolete. - Zhi Yu | SWO SDS 306 !! Please have the HVAC Shop check the ice machine in suite 306 in SDS. It is currently turned off, but we believed it was leaking. PO is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF 2016-09-01 - 18210 - Dispatched to tech at 11am. They are in area working on another job and will attend to this also. Changed status to urgent. - Brian Qualls; 2016-09-26 - 18210 - Derek Gittings-We Diagnose the cubelet cutter grids not working and water pump acting-up. Do to the age of Unit all parts are obsolete. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 67071 | TMPE-183087 | Equipment Room Inspection-Monthly | 2016-09-22 - xPM-EQR-M - Lance Tapia-Inspection Complete. Failed. The mini split a/c unit that mounts to the south wall was leaking water. Called service center and reported the issue. I meet with HVAC Tech and showed him the a/c unit that was leaking. - Lance Tapia | Equipment Room Inspection-Monthly 2016-09-22 - xPM-EQR-M - Lance Tapia-Inspection Complete. Failed. The mini split a/c unit that mounts to the south wall was leaking water. Called service center and reported the issue. I meet with HVAC Tech and showed him the a/c unit that was leaking. - Lance Tapia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 177651 | RFMT-130680 | Can Olympus clean the air conditioning vents in our office 106B and next door in 107B? They are extremely dirty. 4MM5538 | NA | Can Olympus clean the air conditioning vents in our office 106B and next door in 107B? They are extremely dirty. 4MM5538 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 177660 | RFMT-130671 | Air conditioner unit is dripping into office onto table. Need to have it checked or a larger drip pan installed. 4MM5538 | 2016-09-01 - 18010 - Mike Guckian-cleared condensate drain. - Mike Guckian | Air conditioner unit is dripping into office onto table. Need to have it checked or a larger drip pan installed. 4MM5538 2016-09-01 - 18010 - Mike Guckian-cleared condensate drain. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 177665 | RFMT-130666 | !! AC not working -- apartment extremely hot. 4NOF205 | 2016-09-01 - 18010 - Simon Fernandez-checked a/c unit, found supply air at 60F. checked air filter, motor, all okay room at 75F and cool. - Simon Fernandez | !! AC not working -- apartment extremely hot. 4NOF205 2016-09-01 - 18010 - Simon Fernandez-checked a/c unit, found supply air at 60F. checked air filter, motor, all okay room at 75F and cool. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-01 | 235324 | POLY-112875 | Gayla Marsh requested water to be turned on at the swamp cooler in hangar area. 42B97GA | NA | Gayla Marsh requested water to be turned on at the swamp cooler in hangar area. 42B97GA NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 235333 | POLY-112866 | Per Henry A. Please purchase 2ea. 1 ton portable A/C units for emergency use at FMPD. Thanks 4NF4KMJ | 2016-10-13 - 18010 - Jesse Deanda-9/1 - Jesse searched online for A/C units to pick up at the Home Depot today, but they did not have anything. He gave over to Steve with HVAC department. - Gayle Swenson | Per Henry A. Please purchase 2ea. 1 ton portable A/C units for emergency use at FMPD. Thanks 4NF4KMJ 2016-10-13 - 18010 - Jesse Deanda-9/1 - Jesse searched online for A/C units to pick up at the Home Depot today, but they did not have anything. He gave over to Steve with HVAC department. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 235335 | POLY-112864 | !! HVAC unit leaking onto floor underneath, seeping into other rooms. 4NE2L94 | NA | !! HVAC unit leaking onto floor underneath, seeping into other rooms. 4NE2L94 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 235356 | POLY-112843 | !! Is it possible to have a allergy or hepa filter installed in our house. I have really bad allergys and I really need a house that I can breathe in. Also the closet door next to the bathroom came off. Thanks in advance for all the hard work. 4NCEEOE | NA | !! Is it possible to have a allergy or hepa filter installed in our house. I have really bad allergys and I really need a house that I can breathe in. Also the closet door next to the bathroom came off. Thanks in advance for all the hard work. 4NCEEOE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-01 | 256846 | DTPC-111692 | Air Compressor | 2016-09-21 - 18030 - Robert Bartels-PM checked amp and volt draw, blow tank, air filter, belt,pressure, oil level - Keith Griffin | Air Compressor 2016-09-21 - 18030 - Robert Bartels-PM checked amp and volt draw, blow tank, air filter, belt,pressure, oil level - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-02 | 64762 | TMPE-185396 | MWO: WILSON WRR 319 BT transfer to AC: pan is leaking, there is an active leak, ceiling tile is out Olympus is needed for water clean up There's a ceiling leak in the women's restroom and the ceiling tile is buckled and about to fall. | 2016-09-13 - 18010 - Thomas Gibble-cleared drain line with wet-vac. did it two days in a row . - Thomas Gibble; 2016-09-13 - 18010 - Gail Jackson-cleared drain line with wet-vac. did it two days in a row . - Thomas Gibble | MWO: WILSON WRR 319 BT transfer to AC: pan is leaking, there is an active leak, ceiling tile is out Olympus is needed for water clean up There's a ceiling leak in the women's restroom and the ceiling tile is buckled and about to fall. 2016-09-13 - 18010 - Thomas Gibble-cleared drain line with wet-vac. did it two days in a row . - Thomas Gibble; 2016-09-13 - 18010 - Gail Jackson-cleared drain line with wet-vac. did it two days in a row . - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-02 | 64783 | TMPE-185375 | MWO PSF F232 The fan of the air conditioning unit is so loud that work cannot be done. We are not sure if it is broken or needs service Contact Name: Huyue Song Contact Phone Number: Contact Email: hsong41@asu.edu 42A213M | 2016-09-09 - 18010 - Michael Cozens-Made adjustments to decrease airflow and noise - Mike Cozens | MWO PSF F232 The fan of the air conditioning unit is so loud that work cannot be done. We are not sure if it is broken or needs service Contact Name: Huyue Song Contact Phone Number: Contact Email: hsong41@asu.edu 42A213M 2016-09-09 - 18010 - Michael Cozens-Made adjustments to decrease airflow and noise - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-02 | 64786 | TMPE-185372 | SWO: !! There is no A/ C to the catering kitchens on the first and second floor of the Suites Complex. There are no room numbers. They are in front of you as you exit the press elevator. This is urgent. PO is YG202004971. Thank you. Contact Name: Regina Walker Contact Phone Number: 702-374. . . | 2016-09-06 - 18010 - Changed priority to urgent. Call was not scheduled on 9/2 now 9/6. Assigned to tech will check this week. - Brian Qualls; 2016-09-15 - 18010 - Gail Jackson-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson; 2016-09-15 - 18010 - Gail Jackson-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson; 2016-09-15 - 18010 - Thomas Gibble-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson | SWO: !! There is no A/ C to the catering kitchens on the first and second floor of the Suites Complex. There are no room numbers. They are in front of you as you exit the press elevator. This is urgent. PO is YG202004971. Thank you. Contact Name: Regina Walker Contact Phone Number: 702-374. . . 2016-09-06 - 18010 - Changed priority to urgent. Call was not scheduled on 9/2 now 9/6. Assigned to tech will check this week. - Brian Qualls; 2016-09-15 - 18010 - Gail Jackson-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson; 2016-09-15 - 18010 - Gail Jackson-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson; 2016-09-15 - 18010 - Thomas Gibble-Change batteries 2nd floor catering kitchen and filters in all units. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-02 | 64856 | TMPE-185302 | MWO: Please clean the coils and diffuser louvers on the A/C fan coil unit that is located in the reception area. The coils are pretty dirty and need cleaning. 42C5AE4 | 2016-09-14 - 18090 - All work completed under TMPE-184848.Duplicate work order. - Jennifer Moyer | MWO: Please clean the coils and diffuser louvers on the A/C fan coil unit that is located in the reception area. The coils are pretty dirty and need cleaning. 42C5AE4 2016-09-14 - 18090 - All work completed under TMPE-184848.Duplicate work order. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-02 | 64859 | TMPE-185299 | SWO TYLER CANTINA add PA shop need Roofer: Tim see Joel Please place a work order to rehang the ceiling outside Tyler Cantina where the water cooler was. It is in need of some work, there also seems to be some water damage going on in the ceiling as well Charge this to ARAMARK | 2017-02-06 - 22000 - 1/2 gallon of SS Pearl white. - Rose Barton | SWO TYLER CANTINA add PA shop need Roofer: Tim see Joel Please place a work order to rehang the ceiling outside Tyler Cantina where the water cooler was. It is in need of some work, there also seems to be some water damage going on in the ceiling as well Charge this to ARAMARK 2017-02-06 - 22000 - 1/2 gallon of SS Pearl white. - Rose Barton | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-02 | 64863 | TMPE-185295 | SWO: MU POD: Please create a work order to unplug a evaporator pan under the air screen in the MU POD This is located first floor of the MU building in the Market. The unit has standing water under it and is leaking to the lower level Please charge to this to ARAMARK GN7 | 2016-09-13 - 18010 - Midhat Mukanovic-Repaired the float in the drain pan causing it to not activate the heater causing it to overflow. Carl welded the float together. - Roque Garcia | SWO: MU POD: Please create a work order to unplug a evaporator pan under the air screen in the MU POD This is located first floor of the MU building in the Market. The unit has standing water under it and is leaking to the lower level Please charge to this to ARAMARK GN7 2016-09-13 - 18010 - Midhat Mukanovic-Repaired the float in the drain pan causing it to not activate the heater causing it to overflow. Carl welded the float together. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-02 | 64879 | TMPE-185279 | MWO: Old Main. PL needs to transfer to HVAC - Leak is coming from under the A/C unit. ASU HD - Steven M. Description - Ceiling leak on 3rd floor causing flood. Who was dispatched - Pete Sandoval Time of dispatch - 11:02 PM 12:05 AM: Pete called back, leak taken care of, 3rd floor wate. . . | 2016-09-06 - 18010 - Carl Karr-Clear condensate lines on air handlers. Left message with debbie. - Carl Karr; 2016-09-07 - 18010 - Carl Karr-Install drain on pan. Clear condensate line on A/H #3. - Carl Karr; 2016-09-08 - 18010 - Carl Karr-Pick up metal. Fabricate condensate pans. - Carl Karr; 2016-09-14 - 18010 - Carl Karr-Install pans. - Carl Karr; 2016-09-16 - 18010 - Carl Karr-Install condensate pans. - Carl Karr | MWO: Old Main. PL needs to transfer to HVAC - Leak is coming from under the A/C unit. ASU HD - Steven M. Description - Ceiling leak on 3rd floor causing flood. Who was dispatched - Pete Sandoval Time of dispatch - 11:02 PM 12:05 AM: Pete called back, leak taken care of, 3rd floor wate. . . 2016-09-06 - 18010 - Carl Karr-Clear condensate lines on air handlers. Left message with debbie. - Carl Karr; 2016-09-07 - 18010 - Carl Karr-Install drain on pan. Clear condensate line on A/H #3. - Carl Karr; 2016-09-08 - 18010 - Carl Karr-Pick up metal. Fabricate condensate pans. - Carl Karr; 2016-09-14 - 18010 - Carl Karr-Install pans. - Carl Karr; 2016-09-16 - 18010 - Carl Karr-Install condensate pans. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-02 | 177603 | RFMT-130728 | !! Our air conditioning is not working. The fan is constantly running but cold air is not coming out of it. Wondering if there is anyway to fix this or if someone could come look at it. 4NO64CJ | 2016-09-06 - 18010 - Eric Miller-Checked room talked to student, everything OK. - Eric Miller | !! Our air conditioning is not working. The fan is constantly running but cold air is not coming out of it. Wondering if there is anyway to fix this or if someone could come look at it. 4NO64CJ 2016-09-06 - 18010 - Eric Miller-Checked room talked to student, everything OK. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-02 | 177614 | RFMT-130717 | !! Repeat Request. LAUNDRY ROOM Ceiling is leaking PLEASE FIX 4NK5D1E | 2016-09-08 - 23000 - Simon Fernandez-Checked A/C unit found clogged condensate line. cleared drain line.Rechecked no leaks found - Simon Fernandez | !! Repeat Request. LAUNDRY ROOM Ceiling is leaking PLEASE FIX 4NK5D1E 2016-09-08 - 23000 - Simon Fernandez-Checked A/C unit found clogged condensate line. cleared drain line.Rechecked no leaks found - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-02 | 256947 | DTPC-111591 | Dispatched to Cronkite for an HVAC alarm for Fan Coil on unit 1-G. | 2016-09-02 - 18010 - James Hermann-Went to EMS and found unit in alarm. laddered up the actual unit in the Cronkite dock area. Found no water flow to the coil. Could not check voltage on the stat as it was lock in the BOG storage room. Contacted Ross for the key and he and Jay (BOG owner) said it could wait until next Tuesday. Put back equipment and reset alarms. - James Hermann; 2016-09-08 - 18010 - James Hermann-Ross made repairs with Jay BOG owner as he has the only key. Work-order complete. - James Hermann | Dispatched to Cronkite for an HVAC alarm for Fan Coil on unit 1-G. 2016-09-02 - 18010 - James Hermann-Went to EMS and found unit in alarm. laddered up the actual unit in the Cronkite dock area. Found no water flow to the coil. Could not check voltage on the stat as it was lock in the BOG storage room. Contacted Ross for the key and he and Jay (BOG owner) said it could wait until next Tuesday. Put back equipment and reset alarms. - James Hermann; 2016-09-08 - 18010 - James Hermann-Ross made repairs with Jay BOG owner as he has the only key. Work-order complete. - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-09-03 | 177586 | RFMT-130745 | !! The leak from the air unit in the bathroom has returned. Please drain the unit again and look into why the leak has returned. Thank you. 4N5M7K5 | 2016-09-06 - 18010 - David Cates-Simon is replacing condensation pan. Please create TMA for him if he doesn't already have one for T305. - David Cates | !! The leak from the air unit in the bathroom has returned. Please drain the unit again and look into why the leak has returned. Thank you. 4N5M7K5 2016-09-06 - 18010 - David Cates-Simon is replacing condensation pan. Please create TMA for him if he doesn't already have one for T305. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-03 | 216498 | RACC-112112 | Requesting to get air conditioning filters replaced-Rooms A and B are constantly dusty. 4NK7OAE | NA | Requesting to get air conditioning filters replaced-Rooms A and B are constantly dusty. 4NK7OAE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-03 | 235401 | POLY-112798 | Exhaust Fan | NA | Exhaust Fan NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-04 | 177578 | RFMT-130753 | !! Found bugs in my room such as spiders and crickets, but also found a spider crawled into a hole in my ceiling between the wall and air conditioner. 4NG9A6H | 2016-09-06 - 19080 - Eric Miller-Sprayed room for bugs. - Eric Miller | !! Found bugs in my room such as spiders and crickets, but also found a spider crawled into a hole in my ceiling between the wall and air conditioner. 4NG9A6H 2016-09-06 - 19080 - Eric Miller-Sprayed room for bugs. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-04 | 216555 | RACC-112055 | !! In our shared bathroom, the panel (where I believe the air conditioning unit is kept) is leaking water onto our floor. 4NO6IK0 | NA | !! In our shared bathroom, the panel (where I believe the air conditioning unit is kept) is leaking water onto our floor. 4NO6IK0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-05 | 64403 | TMPE-185755 | MWO: ASUHD-Jason / NO DISPATCH TOC-944am SW- Clint Mgr 6023146082 Towers Center Building #23A has no AC to entire building. 946am-Mike Cozins: SW- This building needs HVAC not EMS due to the unit set up 950am- 480-689-0362 - Times 2 attmepts to call Robert Dauscher that Mike said shoul. . . | 2017-02-17 - 18010 - Mitchell Andrews-was called in to restart the chiller was not getting voltage to the contactor corrected the problem and chiller is now cooling the building - Mitchell Andrews | MWO: ASUHD-Jason / NO DISPATCH TOC-944am SW- Clint Mgr 6023146082 Towers Center Building #23A has no AC to entire building. 946am-Mike Cozins: SW- This building needs HVAC not EMS due to the unit set up 950am- 480-689-0362 - Times 2 attmepts to call Robert Dauscher that Mike said shoul. . . 2017-02-17 - 18010 - Mitchell Andrews-was called in to restart the chiller was not getting voltage to the contactor corrected the problem and chiller is now cooling the building - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-05 | 64406 | TMPE-185752 | MWO: ISTB4: The 4 celcius walk in cooler in the long equipment room (LER) behind the lab in ISTB4 231 has been registering a humidity of over 90% for at least the last week. The dehumidifier light is on, but it has not gone down. We have it set at 50%, so it is quite off our target. In addition, the. . . | 2016-09-09 - 18100 - Duane Rider-Troubleshoot unit, found bad wiring on control switch, repaired - Duane Rider | MWO: ISTB4: The 4 celcius walk in cooler in the long equipment room (LER) behind the lab in ISTB4 231 has been registering a humidity of over 90% for at least the last week. The dehumidifier light is on, but it has not gone down. We have it set at 50%, so it is quite off our target. In addition, the. . . 2016-09-09 - 18100 - Duane Rider-Troubleshoot unit, found bad wiring on control switch, repaired - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-05 | 177569 | RFMT-130762 | !! AC Medium Level doesn't work. Contact Name: Contact Phone Number: 9186888341 Contact Email: 4NDK207 | 2016-09-12 - 18010 - Thomas Zambrano-meed motor replaced and re wired. Can this be sent to AC techs? - Thomas Zambrano; 2016-10-07 - 18010 - Thomas Zambrano-need hvac tech to help with problem. - Thomas Zambrano | !! AC Medium Level doesn't work. Contact Name: Contact Phone Number: 9186888341 Contact Email: 4NDK207 2016-09-12 - 18010 - Thomas Zambrano-meed motor replaced and re wired. Can this be sent to AC techs? - Thomas Zambrano; 2016-10-07 - 18010 - Thomas Zambrano-need hvac tech to help with problem. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-06 | 64173 | TMPE-185985 | MWO MHALL 2 !! I have reported a problem with the A/C in the basement of Matthews Hall before. Our Forensics Squad room is there and there are always team members in and out preparing for debate competition. The A/C is not working and it is 85+ in that area. No air coming out of the vents even. . . | 2016-09-09 - 18290 - Oner Munoz-Checked system, found bad contactor, dirty air filter, weak run capacitor, and low on refrigerant. All issues were addressed. Tried calling the requester, but the number on the work order was wrong. - Oner Munoz; 2016-09-09 - 18290 - Robert Ecabert-Checked system, found bad contactor, dirty air filter, weak run capacitor, and low on refrigerant. All issues were addressed. Tried calling the requester, but the number on the work order was wrong. - Oner Munoz | MWO MHALL 2 !! I have reported a problem with the A/C in the basement of Matthews Hall before. Our Forensics Squad room is there and there are always team members in and out preparing for debate competition. The A/C is not working and it is 85+ in that area. No air coming out of the vents even. . . 2016-09-09 - 18290 - Oner Munoz-Checked system, found bad contactor, dirty air filter, weak run capacitor, and low on refrigerant. All issues were addressed. Tried calling the requester, but the number on the work order was wrong. - Oner Munoz; 2016-09-09 - 18290 - Robert Ecabert-Checked system, found bad contactor, dirty air filter, weak run capacitor, and low on refrigerant. All issues were addressed. Tried calling the requester, but the number on the work order was wrong. - Oner Munoz | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-06 | 64209 | TMPE-185949 | MWO ECF F120 & F122 Transfer to HVAC both fan coils are calling for cooling, however, F120 is 73 deg and F122 is 85 deg. EMS WO# 185815, HVAC WO#185949. HVAC-This room is far too hot. Please adjust asap. Thank you! | 2016-09-08 - 18290 - Zhi Yu-Arrived Unit blower running compressor not. open the panel the 3pole contactor burn-out. we replaced the 3pole contactor, check cap and pressure. - Zhi Yu | MWO ECF F120 & F122 Transfer to HVAC both fan coils are calling for cooling, however, F120 is 73 deg and F122 is 85 deg. EMS WO# 185815, HVAC WO#185949. HVAC-This room is far too hot. Please adjust asap. Thank you! 2016-09-08 - 18290 - Zhi Yu-Arrived Unit blower running compressor not. open the panel the 3pole contactor burn-out. we replaced the 3pole contactor, check cap and pressure. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-06 | 64215 | TMPE-185943 | MWO PSH H147U1 TRANSFER EL TO HVAC bad bearing on motor. ORIG REQUEST AHU 17 is not responding to commands Please create a MWO to have Electricians Troubleshoot the VFD in room H147 U1. Will not respond to commands Stays in minimum speed 42DIM5O | 2016-09-16 - 18230 - Derek-checked motor bearings, electrical-stayed with electricians to make sure VFD was working properly. Complete - Melanie Lamm | MWO PSH H147U1 TRANSFER EL TO HVAC bad bearing on motor. ORIG REQUEST AHU 17 is not responding to commands Please create a MWO to have Electricians Troubleshoot the VFD in room H147 U1. Will not respond to commands Stays in minimum speed 42DIM5O 2016-09-16 - 18230 - Derek-checked motor bearings, electrical-stayed with electricians to make sure VFD was working properly. Complete - Melanie Lamm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-06 | 64220 | TMPE-185938 | MWO: LSD - 101: REPEAT REQUEST! This is still not repaired and is sounding like it is about to explode. We need to have someone look at this asap today! Thank you!!This was worked on yesterday afternoon and was supposed to have been working, but it\\u2019s still not cooling properly. We need a return vis. . . | 2016-09-06 - 18290 - added comments from email: This is still not repaired and is sounding like it is about to explode. We need to have someone look at this asap today! Thank you - Michelle Ryan; 2016-09-13 - 18290 - Gail Jackson-Found condenser fan blade had broke and damaged motor shaft. Trip to Tempe Trane and Tempe ARS for new motor and blade. Installed parts; test run. - Gail Jackson; 2016-09-13 - 18290 - Thomas Gibble-Found condenser fan blade had broke and damaged motor shaft. Trip to Tempe Trane and Tempe ARS for new motor and blade. Installed parts; test run. - Gail Jackson | MWO: LSD - 101: REPEAT REQUEST! This is still not repaired and is sounding like it is about to explode. We need to have someone look at this asap today! Thank you!!This was worked on yesterday afternoon and was supposed to have been working, but it\\u2019s still not cooling properly. We need a return vis. . . 2016-09-06 - 18290 - added comments from email: This is still not repaired and is sounding like it is about to explode. We need to have someone look at this asap today! Thank you - Michelle Ryan; 2016-09-13 - 18290 - Gail Jackson-Found condenser fan blade had broke and damaged motor shaft. Trip to Tempe Trane and Tempe ARS for new motor and blade. Installed parts; test run. - Gail Jackson; 2016-09-13 - 18290 - Thomas Gibble-Found condenser fan blade had broke and damaged motor shaft. Trip to Tempe Trane and Tempe ARS for new motor and blade. Installed parts; test run. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-09-06 | 64222 | TMPE-185936 | MWO: ED 250 The fan or a/c is too loud and making it hard for students to hear. | NA | MWO: ED 250 The fan or a/c is too loud and making it hard for students to hear. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-06 | 64317 | TMPE-185841 | MWO ECF F103 The exhaust fan #1 is not working. Please inspect/repair asap, thank you! | 2016-09-19 - 18160 - Michael Kelley-job completed. Tested Motor. found bad fuses. Check unit. Could not find reason for blown fuses. - Michael Kelley | MWO ECF F103 The exhaust fan #1 is not working. Please inspect/repair asap, thank you! 2016-09-19 - 18160 - Michael Kelley-job completed. Tested Motor. found bad fuses. Check unit. Could not find reason for blown fuses. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-06 | 64358 | TMPE-185800 | MWO: Please check the fountain motor outside Gammage. Fountain is not working. | 2016-09-27 - 23080 - Michael Kelley-Talk to Brian. The motor is on order. Did not give a date. - Michael Kelley; 2017-04-28 - 23080 - Michael Kelley-job not complete contractor work still working on area - Michael Kelley | MWO: Please check the fountain motor outside Gammage. Fountain is not working. 2016-09-27 - 23080 - Michael Kelley-Talk to Brian. The motor is on order. Did not give a date. - Michael Kelley; 2017-04-28 - 23080 - Michael Kelley-job not complete contractor work still working on area - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-06 | 64372 | TMPE-185786 | MWO: !! Faculty member Heather Switzer's office temperature is in the 80s. Please check out AC and bring a fan our cooling system for her office so that she is able to work in it. 4N63726 | 2016-09-07 - 18290 - Gail Jackson-replaced motor - Thomas Gibble; 2016-09-07 - 18290 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-09-16 - 18290 - Gail Jackson-Credit back, duplicated entry (FF) - Francesca Fernandez | MWO: !! Faculty member Heather Switzer's office temperature is in the 80s. Please check out AC and bring a fan our cooling system for her office so that she is able to work in it. 4N63726 2016-09-07 - 18290 - Gail Jackson-replaced motor - Thomas Gibble; 2016-09-07 - 18290 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-09-16 - 18290 - Gail Jackson-Credit back, duplicated entry (FF) - Francesca Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-06 | 64379 | TMPE-185779 | SWO: !! The fridge is not working. Contact Name: Jacqueline Benhoff Contact Phone Number: 480-965-2202 Contact Email: Jacqueline.Benhoff@asu.edu 4NDCIJF Emailed Customer for a blanket PO $250 | 2016-09-06 - 18240 - called to request PO in the amount of $250 - Michelle Ryan; 2016-09-09 - 18240 - Thomas Gibble-reset breaker and cleaned coil - Thomas Gibble; 2016-09-09 - 18240 - Thomas Gibble-reset breaker and cleaned coil - Thomas Gibble; 2016-09-09 - 18240 - Gail Jackson-reset breaker and cleaned coil - Thomas Gibble | SWO: !! The fridge is not working. Contact Name: Jacqueline Benhoff Contact Phone Number: 480-965-2202 Contact Email: Jacqueline.Benhoff@asu.edu 4NDCIJF Emailed Customer for a blanket PO $250 2016-09-06 - 18240 - called to request PO in the amount of $250 - Michelle Ryan; 2016-09-09 - 18240 - Thomas Gibble-reset breaker and cleaned coil - Thomas Gibble; 2016-09-09 - 18240 - Thomas Gibble-reset breaker and cleaned coil - Thomas Gibble; 2016-09-09 - 18240 - Gail Jackson-reset breaker and cleaned coil - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-06 | 177538 | RFMT-130793 | !! The leak from the air unit in the bathroom has returned. Please drain the unit again and look into why the leak has returned. Thank you. 4N5M7K5 | 2016-09-08 - 18010 - Simon Fernandez-Rechecked a/c unit found bad splash guard. Removed and replaced splash guard.Rechecked drain line clear. - Simon Fernandez | !! The leak from the air unit in the bathroom has returned. Please drain the unit again and look into why the leak has returned. Thank you. 4N5M7K5 2016-09-08 - 18010 - Simon Fernandez-Rechecked a/c unit found bad splash guard. Removed and replaced splash guard.Rechecked drain line clear. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-06 | 216445 | RACC-112165 | There has been an awful smell in my room for a while now, and after eliminating all sources from my room I had the thought that there could be something wrong with the vents. I heard that sometimes if the air filters aren't replaced they can start to smell. I really need this to be fixed. Also the s. . . | NA | There has been an awful smell in my room for a while now, and after eliminating all sources from my room I had the thought that there could be something wrong with the vents. I heard that sometimes if the air filters aren't replaced they can start to smell. I really need this to be fixed. Also the s. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-06 | 235227 | POLY-112972 | !! Air conditioning broken. Fan seems to be working, but AC won't blow air or cool air at all. Called on 9/6 at around 9:00pm to alert Housing of the situation. House is livable for tonight, but we would like it fixed as soon as possible before it gets too hot. Contact Name: Contact Phone Number. . . | NA | !! Air conditioning broken. Fan seems to be working, but AC won't blow air or cool air at all. Called on 9/6 at around 9:00pm to alert Housing of the situation. House is livable for tonight, but we would like it fixed as soon as possible before it gets too hot. Contact Name: Contact Phone Number. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-06 | 235271 | POLY-112928 | !! Air conditioner is not working correctly. Resident believes it is a frozen condenser. Also fire alarm needs battery replaced Contact Name: Daniel Sora Contact Phone Number: Contact Email: 4NG9B74 | NA | !! Air conditioner is not working correctly. Resident believes it is a frozen condenser. Also fire alarm needs battery replaced Contact Name: Daniel Sora Contact Phone Number: Contact Email: 4NG9B74 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-06 | 235272 | POLY-112927 | !! Air Conditioner is acting up. Making weird noise. 4NIHHKH | NA | !! Air Conditioner is acting up. Making weird noise. 4NIHHKH NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-06 | 235273 | POLY-112926 | !! The AC unit has stopped working. yesterday the air was working fine but last night when I went to bed it was 78 degrees and the air was set to 73. This morning the air is still set to 73 but it is 82 in the house. The vents are blowing warm air like the heat is on even though it's not. They are a. . . | NA | !! The AC unit has stopped working. yesterday the air was working fine but last night when I went to bed it was 78 degrees and the air was set to 73. This morning the air is still set to 73 but it is 82 in the house. The vents are blowing warm air like the heat is on even though it's not. They are a. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-06 | 256760 | DTPC-111778 | Exhaust fan 7B not working. 4NC09F9 | 2016-09-06 - 18160 - Ross Hossack-Checked exhaust fan and found that it had a broken belt. Replaced belt,fan now working. - Ross Hossack | Exhaust fan 7B not working. 4NC09F9 2016-09-06 - 18160 - Ross Hossack-Checked exhaust fan and found that it had a broken belt. Replaced belt,fan now working. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-07 | 63907 | TMPE-186251 | !! Please send to Electrical shop Please send to A.C. /mechanical shop We recently had to VFD replaced that serves chilled water pump # 2 . Upon start up it was not able to run. Need electrician ASAP to check that motor is ok or mechanical to determine if the pump is the problem. This is very . . . | 2016-09-09 - 23100 - Wilford Brown-new vfd installed, setup, checked, wired ctrls, jeff bas, sitmon assisted ,put on line. also chk wo 169591 same job. - Arthur Gonzales; 2016-09-30 - 23100 - Wilford Brown-3.000 credited as per payroll - reentered as 2 hours OTS and 1 hour OTP - Jeri Zappanti | !! Please send to Electrical shop Please send to A.C. /mechanical shop We recently had to VFD replaced that serves chilled water pump # 2 . Upon start up it was not able to run. Need electrician ASAP to check that motor is ok or mechanical to determine if the pump is the problem. This is very . . . 2016-09-09 - 23100 - Wilford Brown-new vfd installed, setup, checked, wired ctrls, jeff bas, sitmon assisted ,put on line. also chk wo 169591 same job. - Arthur Gonzales; 2016-09-30 - 23100 - Wilford Brown-3.000 credited as per payroll - reentered as 2 hours OTS and 1 hour OTP - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-07 | 63925 | TMPE-186233 | MWO: ECD 101U1 The evap cooler has bad bearings and it's making a loud noise. | 2016-10-11 - 18100 - Evap cooler no longer making loud noise. Old belt and pump located next to unit. Probably duplicate work order. - Jennifer Moyer | MWO: ECD 101U1 The evap cooler has bad bearings and it's making a loud noise. 2016-10-11 - 18100 - Evap cooler no longer making loud noise. Old belt and pump located next to unit. Probably duplicate work order. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-07 | 63936 | TMPE-186222 | MWO: !! please check all AC in the SHESC area of Matthews Center. 4O3A12D | 2016-09-16 - 18010 - Oner Munoz-Cleaned condenser coils and replaced bad electrical contactor, and replaced schrader because the unit was low on freon. Indoor coil was also dirty and iced up air filter was also replaced. - Oner Munoz; 2016-09-16 - 18010 - Robert Ecabert-Cleaned condenser coils and replaced bad electrical contactor, and replaced schrader because the unit was low on freon. Indoor coil was also dirty and iced up air filter was also replaced. - Oner Munoz; 2016-09-16 - 18010 - Oner Munoz-Checked on unit. - Oner Munoz | MWO: !! please check all AC in the SHESC area of Matthews Center. 4O3A12D 2016-09-16 - 18010 - Oner Munoz-Cleaned condenser coils and replaced bad electrical contactor, and replaced schrader because the unit was low on freon. Indoor coil was also dirty and iced up air filter was also replaced. - Oner Munoz; 2016-09-16 - 18010 - Robert Ecabert-Cleaned condenser coils and replaced bad electrical contactor, and replaced schrader because the unit was low on freon. Indoor coil was also dirty and iced up air filter was also replaced. - Oner Munoz; 2016-09-16 - 18010 - Oner Munoz-Checked on unit. - Oner Munoz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-07 | 63937 | TMPE-186221 | MWO CNTRPT 101-01 !! The Old Childcare Area at Centerpoint 1st floor is under renovation (project # 11311). Today we were having a Fire sprinkler shut down and they noticed a AC unit leaking heavily. This unit has been in place prior the start of renovation. Could we have that looked. Daniel Cle. . . | 2017-02-17 - 18010 - Mitchell Andrews-checked the units on the first floor before the ti...fund 3 units that's need repair bad blower motors - Mitchell Andrews | MWO CNTRPT 101-01 !! The Old Childcare Area at Centerpoint 1st floor is under renovation (project # 11311). Today we were having a Fire sprinkler shut down and they noticed a AC unit leaking heavily. This unit has been in place prior the start of renovation. Could we have that looked. Daniel Cle. . . 2017-02-17 - 18010 - Mitchell Andrews-checked the units on the first floor before the ti...fund 3 units that's need repair bad blower motors - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 63970 | TMPE-186188 | SWO ISTB1 332 TRANSFER HVAC TO CRT Please open a work order for HVAC to perform a PM on the -80 freezer in ISTB1 room 332 at their earliest opportunity. The freezer has been emptied and is currently defrosting. The contact for this request is Jonathan Bobek - 570.259.4841 cell, Text: 570259484. . . | 2016-09-29 - 18180 - Duane Rider-PM unit. completed - Duane Rider | SWO ISTB1 332 TRANSFER HVAC TO CRT Please open a work order for HVAC to perform a PM on the -80 freezer in ISTB1 room 332 at their earliest opportunity. The freezer has been emptied and is currently defrosting. The contact for this request is Jonathan Bobek - 570.259.4841 cell, Text: 570259484. . . 2016-09-29 - 18180 - Duane Rider-PM unit. completed - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 63986 | TMPE-186172 | MWO: Pipe is leaking over handicapped toilet area in restroom. 4N63726 | 2016-09-07 - 23000 - Carlos Felix-Transferred to HVAC. AC unit has a drip. - Carlos Felix; 2016-09-08 - 23000 - Carlos Felix-Transferred to HVAC. - Carlos Felix | MWO: Pipe is leaking over handicapped toilet area in restroom. 4N63726 2016-09-07 - 23000 - Carlos Felix-Transferred to HVAC. AC unit has a drip. - Carlos Felix; 2016-09-08 - 23000 - Carlos Felix-Transferred to HVAC. - Carlos Felix | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 64049 | TMPE-186109 | SWO: Repair Ice machine in PSH-232 Contact Name: Contact Phone Number: Contact Email: melinda.schermerhorn@asu.edu 42AIG49 | 2016-09-12 - 18210 - Emailed AC/WCT that work order was funded (FF) - Francesca Fernandez; 2016-10-03 - 18210 - Thomas Gibble-Found 2 ice machines in need of service, replaced the bin stat on #1 and cleaned. Trip to True Temp for stat. #2 machine Clean and replaced water pressure switch, found switch in shop. #1 unit cond filter was clogged, float was leaking water; adj. Unit is leaking water and oil out evap, informed staff machine will need repaired or soon replaced for lack of maintenance. Replaced both H2O filters. - Gail Jackson; 2016-10-03 - 18210 - Gail Jackson-Found 2 ice machines in need of service, replaced the bin stat on #1 and cleaned. Trip to True Temp for stat. #2 machine Clean and replaced water pressure switch, found switch in shop. #1 unit cond filter was clogged, float was leaking water; adj. Unit is leaking water and oil out evap, informed staff machine will need repaired or soon replaced for lack of maintenance. Replaced both H2O filters. - Gail Jackson | SWO: Repair Ice machine in PSH-232 Contact Name: Contact Phone Number: Contact Email: melinda.schermerhorn@asu.edu 42AIG49 2016-09-12 - 18210 - Emailed AC/WCT that work order was funded (FF) - Francesca Fernandez; 2016-10-03 - 18210 - Thomas Gibble-Found 2 ice machines in need of service, replaced the bin stat on #1 and cleaned. Trip to True Temp for stat. #2 machine Clean and replaced water pressure switch, found switch in shop. #1 unit cond filter was clogged, float was leaking water; adj. Unit is leaking water and oil out evap, informed staff machine will need repaired or soon replaced for lack of maintenance. Replaced both H2O filters. - Gail Jackson; 2016-10-03 - 18210 - Gail Jackson-Found 2 ice machines in need of service, replaced the bin stat on #1 and cleaned. Trip to True Temp for stat. #2 machine Clean and replaced water pressure switch, found switch in shop. #1 unit cond filter was clogged, float was leaking water; adj. Unit is leaking water and oil out evap, informed staff machine will need repaired or soon replaced for lack of maintenance. Replaced both H2O filters. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-07 | 64051 | TMPE-186107 | SWO: Please have the HVAC Shop Check the AC and replace the thermostat knob in Suite 301 in the Suites in SDS. I was told that something is backwards and the knob was written on as to how to adjust temperature. This needs to be completed before the football game on 9/10. PO is YG202004971. Th. . . | 2016-09-26 - 18010 - Midhat Mukanovic-Checked and repaired the suites with problems and made sure they were working before the game Saturday - Roque Garcia | SWO: Please have the HVAC Shop Check the AC and replace the thermostat knob in Suite 301 in the Suites in SDS. I was told that something is backwards and the knob was written on as to how to adjust temperature. This needs to be completed before the football game on 9/10. PO is YG202004971. Th. . . 2016-09-26 - 18010 - Midhat Mukanovic-Checked and repaired the suites with problems and made sure they were working before the game Saturday - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 64053 | TMPE-186105 | MWO: I received the following from someone in Tempe Center 195: "The Binary Space is very warm, even with the A/C on yesterday. We left it on over night as well, hoping it would cool overnight without bodies in it, but it was still close to 85 degrees when we got there today. Or is there a trick. . . | 2016-09-08 - 18290 - Zhi Yu-We Replaced 1/2hp condenser fan motor and 10 mfd cap. We started the unit for 10min and the second stage compressor open will not close. I bypass second stage,check back tomorrow. - Zhi Yu; 2016-09-15 - 18290 - Zhi Yu-The unit has bad condenser motor. We replaced the 1/2hp 1075rpm 208-230 volt. After we start up, unit cut on high pressure and compressor over heat opens. We rinse out condenser coil and charge 2 lbs R-22. - Zhi Yu | MWO: I received the following from someone in Tempe Center 195: "The Binary Space is very warm, even with the A/C on yesterday. We left it on over night as well, hoping it would cool overnight without bodies in it, but it was still close to 85 degrees when we got there today. Or is there a trick. . . 2016-09-08 - 18290 - Zhi Yu-We Replaced 1/2hp condenser fan motor and 10 mfd cap. We started the unit for 10min and the second stage compressor open will not close. I bypass second stage,check back tomorrow. - Zhi Yu; 2016-09-15 - 18290 - Zhi Yu-The unit has bad condenser motor. We replaced the 1/2hp 1075rpm 208-230 volt. After we start up, unit cut on high pressure and compressor over heat opens. We rinse out condenser coil and charge 2 lbs R-22. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-07 | 64089 | TMPE-186069 | MWO CP R1 Central Plant- Please order material for evap coolers for annual pm's. See Mike T for informatioon. 4NNI9H6 | NA | MWO CP R1 Central Plant- Please order material for evap coolers for annual pm's. See Mike T for informatioon. 4NNI9H6 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 64119 | TMPE-186039 | About a month or two ago FacMan came into our main office(WH205) to fix the air conditioning. The air conditioner is fine now, but the technicians did not put the ceiling tile properly back in place. Due to this, small bits of dust/ceiling tile have been falling on the floor. If it would be possible. . . | NA | About a month or two ago FacMan came into our main office(WH205) to fix the air conditioning. The air conditioner is fine now, but the technicians did not put the ceiling tile properly back in place. Due to this, small bits of dust/ceiling tile have been falling on the floor. If it would be possible. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 64120 | TMPE-186038 | MWO: About a month or two ago FacMan came into our main office(WH205) to fix the air conditioning. The air conditioner is fine now, but the technicians did not put the ceiling tile properly back in place. Due to this, small bits of dust/ceiling tile have been falling on the floor. If it would be . . . | 2016-09-07 - 13050 - Carlos Felix-Repositioned ceiling tiles. - Carlos Felix | MWO: About a month or two ago FacMan came into our main office(WH205) to fix the air conditioning. The air conditioner is fine now, but the technicians did not put the ceiling tile properly back in place. Due to this, small bits of dust/ceiling tile have been falling on the floor. If it would be . . . 2016-09-07 - 13050 - Carlos Felix-Repositioned ceiling tiles. - Carlos Felix | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 64121 | TMPE-186037 | MWO: Faculty Member Karen Leong's AC fan is not working and office is not cooling down. Please check AC. 4N63726 | 2016-09-08 - 18290 - Zhi Yu-Arrived the room I @ 74deg. Air blowing 53deg. No problem were found. - Zhi Yu | MWO: Faculty Member Karen Leong's AC fan is not working and office is not cooling down. Please check AC. 4N63726 2016-09-08 - 18290 - Zhi Yu-Arrived the room I @ 74deg. Air blowing 53deg. No problem were found. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 17560 | TMPE-232597 | Interstate All Battery Center Automotive battery 21 months bad cell exchange | NA | Interstate All Battery Center Automotive battery 21 months bad cell exchange NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 177403 | RFMT-130928 | !! Please order a new motor for our A'C unit. It has been making a loud banging noise when turning off/on and last time maintenance visited, they said if it continued the motor would be replaced. 4NC34LN | 2016-09-09 - 18010 - David Cates-Thor and Simon replaced blower motor and inspected the unit. Please create a TMA for them to account for their time and parts used. - David Cates; 2016-09-09 - 18010 - Simon copied on work order. - Gregory Stetka | !! Please order a new motor for our A'C unit. It has been making a loud banging noise when turning off/on and last time maintenance visited, they said if it continued the motor would be replaced. 4NC34LN 2016-09-09 - 18010 - David Cates-Thor and Simon replaced blower motor and inspected the unit. Please create a TMA for them to account for their time and parts used. - David Cates; 2016-09-09 - 18010 - Simon copied on work order. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 177410 | RFMT-130921 | !! I put in a request earlier today but nobody showed up. The a/c unit is leaking a lot of water and the carpet is soaked and starting to smell moldy. ***CALLED TO JOE SWAN*** Submitted by 4NID637 ASUHC-Agent: Kyle Green Time: 19:07 - Joe Swan contacted the Help Center to request a water . . . | 2016-09-08 - 18010 - Joe Swan-Found crack on condensate pan were the 3/4" copper pipe connects to pan. needs replaced. Temporary fix. - Joe Swan | !! I put in a request earlier today but nobody showed up. The a/c unit is leaking a lot of water and the carpet is soaked and starting to smell moldy. ***CALLED TO JOE SWAN*** Submitted by 4NID637 ASUHC-Agent: Kyle Green Time: 19:07 - Joe Swan contacted the Help Center to request a water . . . 2016-09-08 - 18010 - Joe Swan-Found crack on condensate pan were the 3/4" copper pipe connects to pan. needs replaced. Temporary fix. - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 177415 | RFMT-130916 | broken AC in study room on second floor 4NKDEMG | 2016-09-08 - 18010 - David Cates-Thor and Simon have a TMA in the system for this issue already, the reversing valve needs to be released - David Cates; 2016-09-09 - 18010 - Thor completed RVR installation. - Gregory Stetka | broken AC in study room on second floor 4NKDEMG 2016-09-08 - 18010 - David Cates-Thor and Simon have a TMA in the system for this issue already, the reversing valve needs to be released - David Cates; 2016-09-09 - 18010 - Thor completed RVR installation. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2
2016-09-07 | 177436 | RFMT-130895 | My air conditioner is leaking again but on the opposite side from where it was leaking before so now it is leaking on the right hand side. Also it would be great if someone could come shampoo the carpet after the leak is fixed, the room is really starting to smell like mildew from all of the water i. . . | 2016-09-07 - 18010 - carpet cleaning and deodorizing scheduled on 9/7/16 service request # 225339 - Gregory Stetka; 2016-09-08 - 18010 - Eric Miller-Cleared drain, installed new drain hose. - Eric Miller | My air conditioner is leaking again but on the opposite side from where it was leaking before so now it is leaking on the right hand side. Also it would be great if someone could come shampoo the carpet after the leak is fixed, the room is really starting to smell like mildew from all of the water i. . . 2016-09-07 - 18010 - carpet cleaning and deodorizing scheduled on 9/7/16 service request # 225339 - Gregory Stetka; 2016-09-08 - 18010 - Eric Miller-Cleared drain, installed new drain hose. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 177439 | RFMT-130892 | !! The air conditioning in the study loft is broken 4NH23N7 | 2016-09-07 - 18010 - David Cates-Simon and Thor already have a TMA for this issue. The unit needs to have the reversing valve replaced. - David Cates | !! The air conditioning in the study loft is broken 4NH23N7 2016-09-07 - 18010 - David Cates-Simon and Thor already have a TMA for this issue. The unit needs to have the reversing valve replaced. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2
2016-09-07 | 177452 | RFMT-130879 | !! Hello My Room as a Vent that is controlled by my suitemate. When they turn it cold, it just blows too much cold air, I cannot study and body turns blue. I need a Vent that I can close or open as we need it. The Vent in the room as no open / close lever. Or have a thermosat that we can contr. . . | 2016-09-08 - 18010 - Scott Berndt-closed vent - Scott Berndt | !! Hello My Room as a Vent that is controlled by my suitemate. When they turn it cold, it just blows too much cold air, I cannot study and body turns blue. I need a Vent that I can close or open as we need it. The Vent in the room as no open / close lever. Or have a thermosat that we can contr. . . 2016-09-08 - 18010 - Scott Berndt-closed vent - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 177460 | RFMT-130871 | Please check Adelphi I C 102 & 104 - HVAC unit not cooling. Thank you. | 2016-09-13 - 18010 - Thor Millsaps-Replaced compressor, 30 amp fuses, 35/5 mfd dual run capacitor, charged with 7.5 lbs R-22, liquid line filter/dryer. System up and running. - Thor Millsaps | Please check Adelphi I C 102 & 104 - HVAC unit not cooling. Thank you. 2016-09-13 - 18010 - Thor Millsaps-Replaced compressor, 30 amp fuses, 35/5 mfd dual run capacitor, charged with 7.5 lbs R-22, liquid line filter/dryer. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-07 | 177461 | RFMT-130870 | Please check Adelphi I C 102 & 104 - HVAC unit not cooling. Thank you. | 2016-09-07 - 18010 - David Cates-Mike had already installed portable units in rooms on 9/5/16. Checked unit but couldn't get it to turn on, even when pushing in the contacter, and also with having installed new fuses. Checked breaker panels but found no issues. Told resident that Simon would be by to check the unit. Simon is aware of the issue already, but please create a TMA for him for this if he doesn't have one already yet. - David Cates | Please check Adelphi I C 102 & 104 - HVAC unit not cooling. Thank you. 2016-09-07 - 18010 - David Cates-Mike had already installed portable units in rooms on 9/5/16. Checked unit but couldn't get it to turn on, even when pushing in the contacter, and also with having installed new fuses. Checked breaker panels but found no issues. Told resident that Simon would be by to check the unit. Simon is aware of the issue already, but please create a TMA for him for this if he doesn't have one already yet. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-07 | 177472 | RFMT-130859 | !! Air conditioner not working 4O1N5C7 | 2016-09-09 - 18010 - Russell Peterson-CAR checked temp at room and other rooms in the stack - room 75.5 degrees - 20 minutes later it was 72.5 and all the rooms in the stack were cooler - at 12;45 an EMS tech came - temp was 76 - residents told us that the air completely shuts down at night - tech investigating. - Russell Peterson | !! Air conditioner not working 4O1N5C7 2016-09-09 - 18010 - Russell Peterson-CAR checked temp at room and other rooms in the stack - room 75.5 degrees - 20 minutes later it was 72.5 and all the rooms in the stack were cooler - at 12;45 an EMS tech came - temp was 76 - residents told us that the air completely shuts down at night - tech investigating. - Russell Peterson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-07 | 216374 | RACC-112236 | Air conditioning broke for second time 4NOFGC3 | NA | Air conditioning broke for second time 4NOFGC3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-07 | 216381 | RACC-112229 | The air conditioning vent in the dining area is hanging somewhat loose from its frame. 4O0L3N6 | NA | The air conditioning vent in the dining area is hanging somewhat loose from its frame. 4O0L3N6 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 235226 | POLY-112973 | !! Repeat Request. I sent one of these out yesterday morning and the air seemed to be working when I got home at 8:30 pm. But now at 12:45 am the air is completely turned off and nothing is coming out of the vents. the AC isn't even making noise anymore. the temp is 76 in the house but it is set to . . . | NA | !! Repeat Request. I sent one of these out yesterday morning and the air seemed to be working when I got home at 8:30 pm. But now at 12:45 am the air is completely turned off and nothing is coming out of the vents. the AC isn't even making noise anymore. the temp is 76 in the house but it is set to . . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-07 | 235235 | POLY-112964 | Frank please make repairs on Vehicle 9403; it needs the back-up alarm repaired, the reverse lights are not working, and the windshield motor was cutting in and out. 4N61N43 | NA | Frank please make repairs on Vehicle 9403; it needs the back-up alarm repaired, the reverse lights are not working, and the windshield motor was cutting in and out. 4N61N43 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-08 | 58758 | TMPE-191399 | factory Motor Parts CCA650 RC130 Total: 93.78 | NA | factory Motor Parts CCA650 RC130 Total: 93.78 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 63760 | TMPE-186398 | MWO: !! 9/8/16 We have a chiller in this room that is not turning on. It is brand new and is chilled by a chiller that keeps dying that is cooled by central plant chilled water. please send out the AC shop asap. 4NBD334 | 2016-09-23 - 18080 - Zhi Yu-contact Nevin Simons The Haskris Chiller is only 6 months old. It sure be under warranties by Haskris. few day later Unit is repaired by Haskris technican. - Zhi Yu | MWO: !! 9/8/16 We have a chiller in this room that is not turning on. It is brand new and is chilled by a chiller that keeps dying that is cooled by central plant chilled water. please send out the AC shop asap. 4NBD334 2016-09-23 - 18080 - Zhi Yu-contact Nevin Simons The Haskris Chiller is only 6 months old. It sure be under warranties by Haskris. few day later Unit is repaired by Haskris technican. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 63778 | TMPE-186380 | Found the fan motor cutting out on thermal overload. Checked the capacitor and found it to be good. | NA | Found the fan motor cutting out on thermal overload. Checked the capacitor and found it to be good. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-08 | 63803 | TMPE-186355 | MWO INTDSB B288BA !! We have two swamp coolers that need to be picked up as soon as possible now that our air conditioning is fixed. Please have someone pick them up as soon as possible. Contact Name: Kimberly or Chasaty Contact Phone Number: 480-965-3521 Contact Email: kimberly.barrington@as. . . | 2016-11-23 - 18010 - Jennifer Moyer-Picked up portable A/C. - Jennifer Moyer | MWO INTDSB B288BA !! We have two swamp coolers that need to be picked up as soon as possible now that our air conditioning is fixed. Please have someone pick them up as soon as possible. Contact Name: Kimberly or Chasaty Contact Phone Number: 480-965-3521 Contact Email: kimberly.barrington@as. . . 2016-11-23 - 18010 - Jennifer Moyer-Picked up portable A/C. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-08 | 63804 | TMPE-186354 | MWO: ** AC LEAKING INTO ROOM ** - PL transfer to AC: this is a condensate leak, the unit itself need to be cleaned student reports that the AC is leaking into Discovery 123 and floor and furniture is getting wet. Thanks. | 2016-10-19 - 23040 - Derek Gittings-cleaned out condensate lines-completed - Melanie Lamm | MWO: ** AC LEAKING INTO ROOM ** - PL transfer to AC: this is a condensate leak, the unit itself need to be cleaned student reports that the AC is leaking into Discovery 123 and floor and furniture is getting wet. Thanks. 2016-10-19 - 23040 - Derek Gittings-cleaned out condensate lines-completed - Melanie Lamm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 63811 | TMPE-186347 | SWO: PVEAST add AC shop: Ejector Pumps not working ASUHC-Agent: Kyle Green Description: Lobby, women's restroom flooding, caller unsure of the source. Floor completely flooded. Near Starbucks Who was dispatched: Joe Swan/Pete Sandoval Time of dispatch: 19:51 ASUHC-Agent: Kyle Green Time: 19. . . | 2016-09-08 - 23100 - Brian Qualls-Came in at 5am with Mitch. Found sump pit pumped down. #1 pump working. ALternator relay was loose in socket. Pump# 2 pulling LRA. Impeller locked up. Derek and Mitch are taking care of now. - Brian Qualls; 2016-09-12 - 23100 - 9/8/16 Brian Qualls 1.5 hr. CTE sewage ejector failed 9/7/16 p.m., came in early to diagnose/repair - Juliana Blusiewicz; 2016-09-26 - 23100 - 9/8/2016 1.5OT 5am-6:30am Brian Qualls - PVEast Palo Verde East - Sewage ejector failed 9/7/2016 pm came in early to Diagnose/ repair. - Kerri Perkins; 2016-09-29 - 23100 - Mitchell Andrews-Sewage pump was stuck with debris. - Francesca Fernandez; 2016-10-10 - 23100 - Brian Qualls-1.50 credited as per payroll - reentered as OTS. - Jeri Zappanti; 2016-10-12 - 23100 - Mitchell Andrews-1.50 credited as per payroll - reentered as OTS. - Jeri Zappanti | SWO: PVEAST add AC shop: Ejector Pumps not working ASUHC-Agent: Kyle Green Description: Lobby, women's restroom flooding, caller unsure of the source. Floor completely flooded. Near Starbucks Who was dispatched: Joe Swan/Pete Sandoval Time of dispatch: 19:51 ASUHC-Agent: Kyle Green Time: 19. . . 2016-09-08 - 23100 - Brian Qualls-Came in at 5am with Mitch. Found sump pit pumped down. #1 pump working. ALternator relay was loose in socket. Pump# 2 pulling LRA. Impeller locked up. Derek and Mitch are taking care of now. - Brian Qualls; 2016-09-12 - 23100 - 9/8/16 Brian Qualls 1.5 hr. CTE sewage ejector failed 9/7/16 p.m., came in early to diagnose/repair - Juliana Blusiewicz; 2016-09-26 - 23100 - 9/8/2016 1.5OT 5am-6:30am Brian Qualls - PVEast Palo Verde East - Sewage ejector failed 9/7/2016 pm came in early to Diagnose/ repair. - Kerri Perkins; 2016-09-29 - 23100 - Mitchell Andrews-Sewage pump was stuck with debris. - Francesca Fernandez; 2016-10-10 - 23100 - Brian Qualls-1.50 credited as per payroll - reentered as OTS. - Jeri Zappanti; 2016-10-12 - 23100 - Mitchell Andrews-1.50 credited as per payroll - reentered as OTS. - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-08 | 63837 | TMPE-186321 | MWO: HVAC- replace shaft seal on HW pump #1 - pump #7360. | 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez | MWO: HVAC- replace shaft seal on HW pump #1 - pump #7360. 2016-09-26 - 18010 - Jose Lopez-work in progress - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 63866 | TMPE-186292 | SWO: Hello, add EL shop: We check belt,motor, bearing and looks normal condition. The motor draws 11amp and name plate @ 18.5amp The Start-up amps @ 33. notice the breaker is 15amp maybe little under size for an 15hp motor. Hvac to Electrical plz confirm the size of the breaker. I need to get. . . | 2016-10-19 - 15010 - Semeon Haile-pulled wire, replaced breaker and terminate motor - Semeon Haile; 2016-10-24 - 15010 - 10/19/16 Gary Conover 3.5 hr. OT Re-fed Exh fan, replaced breaker 10/19/16 Wilford Brown 3.5 hr. OT pull wire to dist. board to fan on roof - Juliana Blusiewicz | SWO: Hello, add EL shop: We check belt,motor, bearing and looks normal condition. The motor draws 11amp and name plate @ 18.5amp The Start-up amps @ 33. notice the breaker is 15amp maybe little under size for an 15hp motor. Hvac to Electrical plz confirm the size of the breaker. I need to get. . . 2016-10-19 - 15010 - Semeon Haile-pulled wire, replaced breaker and terminate motor - Semeon Haile; 2016-10-24 - 15010 - 10/19/16 Gary Conover 3.5 hr. OT Re-fed Exh fan, replaced breaker 10/19/16 Wilford Brown 3.5 hr. OT pull wire to dist. board to fan on roof - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2016-09-08 | 63868 | TMPE-186290 | SWO MU 104 !! The Starbucks kitchen/prep room is very warm. The fan section runs. The rooftop condensing unit Y4722 is off. Please repair. 42AI0GO | NA | SWO MU 104 !! The Starbucks kitchen/prep room is very warm. The fan section runs. The rooftop condensing unit Y4722 is off. Please repair. 42AI0GO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 63872 | TMPE-186286 | MWO CNTRPT 2nd Flr!!! HVAC WO#186288, EMS WO#186151 **Most of the 2nd Flr is affected, Please hurry !! Hello Sir/Madam, Since early morning, the air conditioning system is not working. This issue is also severe into other areas of second floor, including many research labs. Currently,. . . | 2016-09-08 - 18290 - Cheryl St. John-09.08.16 Contacted Shail Dave (left voice message on cell phone) to let him know there was an electrical shut down in the building this morning and the Heat pumps tripped off, two HVAC tech are on their way to get units restored. Shail Dave called back to say thanks for letting him know what was going on, he will wait for the cooling to be restored. I contacted the Service Center with update on Centerpoint and asked them to let customers know what was going on if more calls came in. I addressed additional email that came in, in reference to hot calls in the building. I spoke with Brian again and the HVAC shop will be working off of WO#186288 to restore the HP's. - Cheryl St. John | MWO CNTRPT 2nd Flr!!! HVAC WO#186288, EMS WO#186151 **Most of the 2nd Flr is affected, Please hurry !! Hello Sir/Madam, Since early morning, the air conditioning system is not working. This issue is also severe into other areas of second floor, including many research labs. Currently,. . . 2016-09-08 - 18290 - Cheryl St. John-09.08.16 Contacted Shail Dave (left voice message on cell phone) to let him know there was an electrical shut down in the building this morning and the Heat pumps tripped off, two HVAC tech are on their way to get units restored. Shail Dave called back to say thanks for letting him know what was going on, he will wait for the cooling to be restored. I contacted the Service Center with update on Centerpoint and asked them to let customers know what was going on if more calls came in. I addressed additional email that came in, in reference to hot calls in the building. I spoke with Brian again and the HVAC shop will be working off of WO#186288 to restore the HP's. - Cheryl St. John | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 64630 | TMPE-185528 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-08 | 177343 | RFMT-130988 | ASUHC-jbreeze Description- Room S306 Adelphi2 S cluster has a leaking AC Unit. Who was dispatched-Swan Time of dispatch-830p | 2016-09-09 - 18010 - Joe Swan-Condensate line was plugged, cleared line and put in a clean up for 9/9/16 in morning for Olympus per occupants request. Complete - Joe Swan | ASUHC-jbreeze Description- Room S306 Adelphi2 S cluster has a leaking AC Unit. Who was dispatched-Swan Time of dispatch-830p 2016-09-09 - 18010 - Joe Swan-Condensate line was plugged, cleared line and put in a clean up for 9/9/16 in morning for Olympus per occupants request. Complete - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 177359 | RFMT-130972 | !! AC is not cooling room, very little air is coming out and it is warm air only. Please fix, thank you! 4NJENM9 ASUHC-Agent: Kyle Green Time: 09-09-2016 - 00:55 - Beatriz called in to report that the issue is still occurring with the A/C. Contacted the standby res life maintenance, Eric Miller . . . | 2016-09-09 - 18010 - David Cates-Thor and Simon replaced a capacitor and recharged the freon. Please create a TMA for them to account for their time and parts. - David Cates | !! AC is not cooling room, very little air is coming out and it is warm air only. Please fix, thank you! 4NJENM9 ASUHC-Agent: Kyle Green Time: 09-09-2016 - 00:55 - Beatriz called in to report that the issue is still occurring with the A/C. Contacted the standby res life maintenance, Eric Miller . . . 2016-09-09 - 18010 - David Cates-Thor and Simon replaced a capacitor and recharged the freon. Please create a TMA for them to account for their time and parts. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-08 | 216343 | RACC-112267 | !! Something is terribly wrong with the garbage disposal and that side of the kitchen sink. When the disposal was ran it suddenly spurted food into the air and the seal was dislodged, after this incident the left side of the kitchen sink (the one with the disposal) has not been draining properly. . . . | NA | !! Something is terribly wrong with the garbage disposal and that side of the kitchen sink. When the disposal was ran it suddenly spurted food into the air and the seal was dislodged, after this incident the left side of the kitchen sink (the one with the disposal) has not been draining properly. . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 235140 | POLY-113059 | !! Air conditioner not working properly, have a child and needs to be fixed immediately. 4O1O0NB | NA | !! Air conditioner not working properly, have a child and needs to be fixed immediately. 4O1O0NB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-08 | 256662 | DTPC-111876 | Troubleshoot HVAC unit CU-7 and FC-7. No cool air from the vent. | 2016-09-08 - 18290 - James Hermann-Troubleshoot at FC-7 found a loose wire in the junction box below the disconnect. Made repairs and waited for the CU to start. It did not start, so upon inspection I found a condensing fan issue and turned it in for warranty work through Westward Ho - James Hermann; 2016-09-12 - 18290 - James Hermann-Received word from the vendor that the unit required a refrigeration recharge and it is now repaired. - James Hermann | Troubleshoot HVAC unit CU-7 and FC-7. No cool air from the vent. 2016-09-08 - 18290 - James Hermann-Troubleshoot at FC-7 found a loose wire in the junction box below the disconnect. Made repairs and waited for the CU to start. It did not start, so upon inspection I found a condensing fan issue and turned it in for warranty work through Westward Ho - James Hermann; 2016-09-12 - 18290 - James Hermann-Received word from the vendor that the unit required a refrigeration recharge and it is now repaired. - James Hermann | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-09 | 63533 | TMPE-186625 | SWO: !! The temperature is set at 70 degrees but the temperature is reading 80 in the Gymnastics Facility. PO is YG202004934. Thank you. Contact Name: Mark Gorski Contact Phone Number: 815-353-9197 Contact Email: mzgorski@asu.edu 42BDEDF | 2016-09-09 - 18290 - CALLED TO JOHN H. - Monica Moraga; 2016-09-17 - 18290 - Robert Dauscher-Called by John at 4:09pm about this call while still working another emergency call at Sun Devil Stadium Suits prior to game. Was able to arrive by 4:17pm after completing emergency as SDS and with assistance from EMS figure which of the 3 units needed looked at. Found bottom 1/3 of coil frozen 4" thick with ice. Turned off disconnect and locked and tagged unit out for the night to allow the unit to thaw. - Robert Dauscher; 2016-09-17 - 18290 - Robert Dauscher-Returned to unit after allowing sufficient time for ice to melt. Found both circuits low on refrigerant. Leak searched both circuits, unable to determine leak source, replaced Schrader cores on both circuits and adjusted refrigerant charge to allow cooling for event that day. - Robert Dauscher; 2016-09-18 - 18290 - Robert Dauscher-Added leak-stop to both circuits. Need to recheck unit on Monday 9-19-16 - Robert Dauscher; 2016-09-26 - 18290 - Robert Dauscher-Recovered small amount of refrigerant from both circuits. Unit working properly call complete - Robert Dauscher | SWO: !! The temperature is set at 70 degrees but the temperature is reading 80 in the Gymnastics Facility. PO is YG202004934. Thank you. Contact Name: Mark Gorski Contact Phone Number: 815-353-9197 Contact Email: mzgorski@asu.edu 42BDEDF 2016-09-09 - 18290 - CALLED TO JOHN H. - Monica Moraga; 2016-09-17 - 18290 - Robert Dauscher-Called by John at 4:09pm about this call while still working another emergency call at Sun Devil Stadium Suits prior to game. Was able to arrive by 4:17pm after completing emergency as SDS and with assistance from EMS figure which of the 3 units needed looked at. Found bottom 1/3 of coil frozen 4" thick with ice. Turned off disconnect and locked and tagged unit out for the night to allow the unit to thaw. - Robert Dauscher; 2016-09-17 - 18290 - Robert Dauscher-Returned to unit after allowing sufficient time for ice to melt. Found both circuits low on refrigerant. Leak searched both circuits, unable to determine leak source, replaced Schrader cores on both circuits and adjusted refrigerant charge to allow cooling for event that day. - Robert Dauscher; 2016-09-18 - 18290 - Robert Dauscher-Added leak-stop to both circuits. Need to recheck unit on Monday 9-19-16 - Robert Dauscher; 2016-09-26 - 18290 - Robert Dauscher-Recovered small amount of refrigerant from both circuits. Unit working properly call complete - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2016-09-09 | 63556 | TMPE-186602 | MWO: Leak from the ceiling - tray is full of water. Condensate leak. Room 166 | 2016-09-13 - 18010 - Carl Karr-Repair condensate pan. - Carl Karr; 2016-09-13 - 18010 - Gail Jackson-Found drain line plugged, leak at pain drain connection, installed new brass connection, reran drain line and vacuumed out. Installed clean out union in drain, replaced ceiling tile , trip to ware house for parts. - Gail Jackson | MWO: Leak from the ceiling - tray is full of water. Condensate leak. Room 166 2016-09-13 - 18010 - Carl Karr-Repair condensate pan. - Carl Karr; 2016-09-13 - 18010 - Gail Jackson-Found drain line plugged, leak at pain drain connection, installed new brass connection, reran drain line and vacuumed out. Installed clean out union in drain, replaced ceiling tile , trip to ware house for parts. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-09 | 63581 | TMPE-186577 | MWO CSB Compressor in alarm at CSB, HVAC to check out. | 2016-09-15 - 18030 - Roque Garcia-Found air compressor on and ok spoke with Nick from BMS - Roque Garcia | MWO CSB Compressor in alarm at CSB, HVAC to check out. 2016-09-15 - 18030 - Roque Garcia-Found air compressor on and ok spoke with Nick from BMS - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-09 | 63638 | TMPE-186520 | MWO PEBW 240 BT to HVAC - Both AC units are leaking condensation. Please service asap, thank you. This message was sent to me from Sharon McMaman,"I just got into PEBW 240 to prepare for my 6pm class and there is a considerable amount of water on the floor. Both AC units have accumulated signi. . . | 2016-09-09 - 18010 - Sent email out to HVAC - Amanda Thomas; 2016-10-18 - 18010 - Robert Ecabert-Taped off the top of the stand pipe because it is vented on the wrong side of the drain pipe. - Robert Ecabert | MWO PEBW 240 BT to HVAC - Both AC units are leaking condensation. Please service asap, thank you. This message was sent to me from Sharon McMaman,"I just got into PEBW 240 to prepare for my 6pm class and there is a considerable amount of water on the floor. Both AC units have accumulated signi. . . 2016-09-09 - 18010 - Sent email out to HVAC - Amanda Thomas; 2016-10-18 - 18010 - Robert Ecabert-Taped off the top of the stand pipe because it is vented on the wrong side of the drain pipe. - Robert Ecabert | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-09 | 63642 | TMPE-186516 | MWO PEBW 240 This message was sent to me from Sharon McMaman,"I just got into PEBW 240 to prepare for my 6pm class and there is a considerable amount of water on the floor. Both AC units have accumulated significant water condensation and as a result are now dripping on to both sides of the studi. . . | 2016-09-09 - 18010 - Mauricio Martinez Reyes-Transferred to HVAC. I was unable to find any water on the floor when I arrived. I looked around and I noticed droplets of condensation forming on the A/C ducts. There was an instructor in the room who explained to me that this was a recurring event. It was for this reason that I deducted that the condensation drain line for that A/C unit must be clogged so I transfer the W.O. to HVAC to further examine this issue. Materials:N/A - Mauricio Martinez Reyes | MWO PEBW 240 This message was sent to me from Sharon McMaman,"I just got into PEBW 240 to prepare for my 6pm class and there is a considerable amount of water on the floor. Both AC units have accumulated significant water condensation and as a result are now dripping on to both sides of the studi. . . 2016-09-09 - 18010 - Mauricio Martinez Reyes-Transferred to HVAC. I was unable to find any water on the floor when I arrived. I looked around and I noticed droplets of condensation forming on the A/C ducts. There was an instructor in the room who explained to me that this was a recurring event. It was for this reason that I deducted that the condensation drain line for that A/C unit must be clogged so I transfer the W.O. to HVAC to further examine this issue. Materials:N/A - Mauricio Martinez Reyes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-09-09 | 63644 | TMPE-186514 | Found the fan motor cutting out on thermal overload. Checked the capacitor and found it to be good. | 2016-09-20 - 18230 - duplicate work order - Billy Jackson | Found the fan motor cutting out on thermal overload. Checked the capacitor and found it to be good. 2016-09-20 - 18230 - duplicate work order - Billy Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-09 | 63662 | TMPE-186496 | MWO: ECE 105 Investigate dirt coming out the Supply Registers in ECE-105. Request by Rick Pretzman | 2016-09-16 - 18010 - Derek-cleaned duct work vent, filtered duct work-completed - Melanie Lamm | MWO: ECE 105 Investigate dirt coming out the Supply Registers in ECE-105. Request by Rick Pretzman 2016-09-16 - 18010 - Derek-cleaned duct work vent, filtered duct work-completed - Melanie Lamm | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-09-09 | 177301 | RFMT-131030 | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O | 2016-10-19 - 18010 - Thor Millsaps-Replaced compressor under parts warranty. Replaced liquid line filter dryer, 45/5 mfd dual capacitor. System up and running. - Thor Millsaps | !! Please inspect B 210's a/c unit. Set above 70 and not cooling properly. Thanks, Carli 4NF4L2O 2016-10-19 - 18010 - Thor Millsaps-Replaced compressor under parts warranty. Replaced liquid line filter dryer, 45/5 mfd dual capacitor. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-09 | 177317 | RFMT-131014 | !! Please order a new motor for our A'C unit. It has been making a loud banging noise when turning off/on and last time maintenance visited, they said if it continued the motor would be replaced. 4NC34LN | 2016-09-13 - 18010 - Simon Fernandez-removed and replaced indoor blower motor - Simon Fernandez | !! Please order a new motor for our A'C unit. It has been making a loud banging noise when turning off/on and last time maintenance visited, they said if it continued the motor would be replaced. 4NC34LN 2016-09-13 - 18010 - Simon Fernandez-removed and replaced indoor blower motor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-09 | 177318 | RFMT-131013 | !! AC is not cooling room, very little air is coming out and it is warm air only. Please fix, thank you! 4NJENM9 ASUHC-Agent: Kyle Green Time: 09-09-2016 - 00:55 - Beatriz called in to report that the issue is still occurring with the A/C. Contacted the standby res life maintenance, Eric Miller . . . | 2016-09-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and charged 1.5 lbs. R-22. System up and running. - Thor Millsaps; 2016-09-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and charged 1.5 lbs. R-22. System up and running. - Thor Millsaps | !! AC is not cooling room, very little air is coming out and it is warm air only. Please fix, thank you! 4NJENM9 ASUHC-Agent: Kyle Green Time: 09-09-2016 - 00:55 - Beatriz called in to report that the issue is still occurring with the A/C. Contacted the standby res life maintenance, Eric Miller . . . 2016-09-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and charged 1.5 lbs. R-22. System up and running. - Thor Millsaps; 2016-09-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and charged 1.5 lbs. R-22. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-09 | 216307 | RACC-112303 | !! Air conditioner broken, something loose in vent making loud scraping noises whenever turned on. 4NKBO61 | NA | !! Air conditioner broken, something loose in vent making loud scraping noises whenever turned on. 4NKBO61 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-09-09 | 235108 | POLY-113091 | Air conditioning is broken. 4NMJLJB | NA | Air conditioning is broken. 4NMJLJB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-09 | 235111 | POLY-113088 | R& R of (2) back up motors for the tower fans 4O216EO | NA | R& R of (2) back up motors for the tower fans 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-09 | 235124 | POLY-113075 | !! Repeat Request. Could I get a allergy filter installed please. I have been having really bad allergies since I moved in. My allergist said I need to install a allergy filter in my house. 4NCEEOE | NA | !! Repeat Request. Could I get a allergy filter installed please. I have been having really bad allergies since I moved in. My allergist said I need to install a allergy filter in my house. 4NCEEOE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-09 | 256639 | DTPC-111899 | Assist with Westward Ho AC repair to CU-7. | 2016-09-09 - 18290 - James Hermann-Provided access to Fan Coil closet. Explained the electricity repair done on the prior day. Tech stated that the unit had lost its charge and needed to be recharged with refrigerant. Repairs were made and the temperatures were corrected at the t-stat and in the room. - James Hermann [Modified: 2016-09-21 Julie Fowler] | Assist with Westward Ho AC repair to CU-7. 2016-09-09 - 18290 - James Hermann-Provided access to Fan Coil closet. Explained the electricity repair done on the prior day. Tech stated that the unit had lost its charge and needed to be recharged with refrigerant. Repairs were made and the temperatures were corrected at the t-stat and in the room. - James Hermann [Modified: 2016-09-21 Julie Fowler] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-10 | 177288 | RFMT-131043 | Please start door to door check list program for Hayden South 1st floor. Thank you. | 2016-09-30 - 10010 - Salvatore Marasco Jr-Completed all door to doors in Old Hayden South, and changed all A.C. air filters. - Salvatore Marasco Jr | Please start door to door check list program for Hayden South 1st floor. Thank you. 2016-09-30 - 10010 - Salvatore Marasco Jr-Completed all door to doors in Old Hayden South, and changed all A.C. air filters. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-10 | 177290 | RFMT-131041 | Please start door to door check list program for Hayden South 2nd floor rooms. Thank you. | 2016-09-28 - 10010 - Salvatore Marasco Jr-Completed 2nd floor door to door in Old Hayden South. Also replaced all air filters on 2nd floor. - Salvatore Marasco Jr | Please start door to door check list program for Hayden South 2nd floor rooms. Thank you. 2016-09-28 - 10010 - Salvatore Marasco Jr-Completed 2nd floor door to door in Old Hayden South. Also replaced all air filters on 2nd floor. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-10 | 235107 | POLY-113092 | Repeat Request. CALL AHEAD 928-259-3822 or 520-403-2797 The AC is not blowing cold and the fan is constantly running. Please call ahead I have a dog Brian-928-259-3822 or Sarah -520-403-2797 Thank you 4N1ANH0 | NA | Repeat Request. CALL AHEAD 928-259-3822 or 520-403-2797 The AC is not blowing cold and the fan is constantly running. Please call ahead I have a dog Brian-928-259-3822 or Sarah -520-403-2797 Thank you 4N1ANH0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-11 | 62984 | TMPE-187174 | MWO: ASUHC-Wendell Brimhall Description - Coor Building room 4520U1 would like Hvac to check out noisy fan coil. Why back dx cool unit is working Who was dispatched - Robert Dauscher Time of dispatch - 8:15 | 2016-09-12 - 18010 - Duplicate of 187206 - cancelled per Brian Qualls. (FF) - Francesca Fernandez | MWO: ASUHC-Wendell Brimhall Description - Coor Building room 4520U1 would like Hvac to check out noisy fan coil. Why back dx cool unit is working Who was dispatched - Robert Dauscher Time of dispatch - 8:15 2016-09-12 - 18010 - Duplicate of 187206 - cancelled per Brian Qualls. (FF) - Francesca Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-11 | 177190 | RFMT-131141 | ASUHC-Agent: Ahmed Khalil Description: AC unit in room is not supplying cold air. Who was dispatched: Mike Guckian Time of dispatch: 10:19AM | 2016-09-12 - 18010 - Mike Guckian-coil froze up. so i shut it down for a few hours to let it thaw. put it back together at around 5:30 or so, working fine now. 58* at vent. - Mike Guckian | ASUHC-Agent: Ahmed Khalil Description: AC unit in room is not supplying cold air. Who was dispatched: Mike Guckian Time of dispatch: 10:19AM 2016-09-12 - 18010 - Mike Guckian-coil froze up. so i shut it down for a few hours to let it thaw. put it back together at around 5:30 or so, working fine now. 58* at vent. - Mike Guckian | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-11 | 177239 | RFMT-131092 | !! I think my Air Conditioning Unit is working since the last 4 days and it has stoped cooling the room. I cant figure out the problem but maybe the filter is clogged. Please repair my unit Contact Name: Caden Scharpf Contact Phone Number: 4803364178 Contact Email: Cade.Scharpf@asu.edu 4O0F9M6 | 2016-09-12 - 18010 - Thomas Zambrano-unit was off at t-stat? turned on and checked water temp. found 58\\xb0 at living room vvvent? works fine. - Thomas Zambrano | !! I think my Air Conditioning Unit is working since the last 4 days and it has stoped cooling the room. I cant figure out the problem but maybe the filter is clogged. Please repair my unit Contact Name: Caden Scharpf Contact Phone Number: 4803364178 Contact Email: Cade.Scharpf@asu.edu 4O0F9M6 2016-09-12 - 18010 - Thomas Zambrano-unit was off at t-stat? turned on and checked water temp. found 58\\xb0 at living room vvvent? works fine. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-11 | 177243 | RFMT-131088 | !! The A/C vent is not working 124 A. The A/C filter needs to be cleaned , the A/C vent is not working in that room and hasn't worked since move in. Please fix, thank you! 4NO7859 | 2016-09-12 - 18010 - David Cates-AC is blowing cold, but with low air pressure through vent in left bedroom. Adjusted the vent in the living room and in the bedroom to force more air flow through into bedroom. - David Cates | !! The A/C vent is not working 124 A. The A/C filter needs to be cleaned , the A/C vent is not working in that room and hasn't worked since move in. Please fix, thank you! 4NO7859 2016-09-12 - 18010 - David Cates-AC is blowing cold, but with low air pressure through vent in left bedroom. Adjusted the vent in the living room and in the bedroom to force more air flow through into bedroom. - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-11 | 216224 | RACC-112386 | Air conditioning broke for third time,don't know why it keeps breaking, we basically just leave it at 75/70 all day 4NOFGC3 | NA | Air conditioning broke for third time,don't know why it keeps breaking, we basically just leave it at 75/70 all day 4NOFGC3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-11 | 235106 | POLY-113093 | !! My air conditioner seems to be leaking water very badly. The closet in the middle room of the house had a puddle of water in it yesterday. After we dried up the water, we went to check later that night and found some more water. There was also more water on the closet floor today as well. Please . . . | NA | !! My air conditioner seems to be leaking water very badly. The closet in the middle room of the house had a puddle of water in it yesterday. After we dried up the water, we went to check later that night and found some more water. There was also more water on the closet floor today as well. Please . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-12 | 4689 | WEST-106560 | Repairs needed to air handler #2. | 2016-09-14 - 18050 - James Spratta-Air Handler # 2 Failed checked fan, contacted Belair Mechanical to check status of new shaft that is on order. They are checking to see if we can get the shaft here quickly. Isolated the dampers between the two A/H's and lowered set point temps throughout the building to maintain building. - James Spratta; 2016-09-14 - 18050 - James Spratta-Belair Mechanical arrived to start disassembling damaged air handler. Removed shaft and blower wheel to send to machine shop to have shaft pressed out of fan hub. - James Spratta; 2016-09-22 - 18050 - James Spratta-Belair Mechanical on-site with new fan shaft and repaired inlet cone, installed fan wheel with new shaft. Reinstalled fan housing and test ran fan. - James Spratta; 2016-09-22 - 18050 - David Valentine-found unit running and not producing adequate air flow, shut unit down and found bearing had failed, attempted to replace bad bearing but found shaft had a large groove cut into it. - David Valentine; 2016-09-22 - 18050 - David Valentine-assist Bel Aire Mech. with access and took new belts to site. - David Valentine; 2016-09-22 - 18050 - Anthony Tucson-ISOLATED AHU 1 FROM AHU 2. CHANGED SCHEDULE TO RUN 24 HOURS. CLOSED ALL DAMPERS IN UNOCCUPIED AREAS. CHANGED ALL SET POINTS TO 73 TO COOL DOWN ALL AREAS OVERNIGHT. WALKED THROUGH ALL AREAS TO CHECK TEMPERTURE. - Anthony Tucson; 2016-09-22 - 18050 - Alfred Rohe-Attempted to replace blower drive side bearing for temporary operation while awaiting parts.Shaft was damaged and a new bearing could not be installed. - Alfred Rohe; 2016-09-23 - 18050 - Randy Randell-Brought new belts over for A/H and a hand saw to cut 4X4 to support the fan shaft. - James Spratta | Repairs needed to air handler #2. 2016-09-14 - 18050 - James Spratta-Air Handler # 2 Failed checked fan, contacted Belair Mechanical to check status of new shaft that is on order. They are checking to see if we can get the shaft here quickly. Isolated the dampers between the two A/H's and lowered set point temps throughout the building to maintain building. - James Spratta; 2016-09-14 - 18050 - James Spratta-Belair Mechanical arrived to start disassembling damaged air handler. Removed shaft and blower wheel to send to machine shop to have shaft pressed out of fan hub. - James Spratta; 2016-09-22 - 18050 - James Spratta-Belair Mechanical on-site with new fan shaft and repaired inlet cone, installed fan wheel with new shaft. Reinstalled fan housing and test ran fan. - James Spratta; 2016-09-22 - 18050 - David Valentine-found unit running and not producing adequate air flow, shut unit down and found bearing had failed, attempted to replace bad bearing but found shaft had a large groove cut into it. - David Valentine; 2016-09-22 - 18050 - David Valentine-assist Bel Aire Mech. with access and took new belts to site. - David Valentine; 2016-09-22 - 18050 - Anthony Tucson-ISOLATED AHU 1 FROM AHU 2. CHANGED SCHEDULE TO RUN 24 HOURS. CLOSED ALL DAMPERS IN UNOCCUPIED AREAS. CHANGED ALL SET POINTS TO 73 TO COOL DOWN ALL AREAS OVERNIGHT. WALKED THROUGH ALL AREAS TO CHECK TEMPERTURE. - Anthony Tucson; 2016-09-22 - 18050 - Alfred Rohe-Attempted to replace blower drive side bearing for temporary operation while awaiting parts.Shaft was damaged and a new bearing could not be installed. - Alfred Rohe; 2016-09-23 - 18050 - Randy Randell-Brought new belts over for A/H and a hand saw to cut 4X4 to support the fan shaft. - James Spratta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-12 | 62867 | TMPE-187291 | MWO: CENTERPOINT 4TH FLOOR There's a steady condensate leak in the hallway near cubicle 433BC. The tray may have a crack in it. | 2016-09-13 - 23040 - Roque Garcia-Found the condensate line plugged. Vacuumed the pan and drain line. - Roque Garcia | MWO: CENTERPOINT 4TH FLOOR There's a steady condensate leak in the hallway near cubicle 433BC. The tray may have a crack in it. 2016-09-13 - 23040 - Roque Garcia-Found the condensate line plugged. Vacuumed the pan and drain line. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-12 | 62883 | TMPE-187275 | MWO: INTDSA 121A BT transfer to AC: this is the same condensation leak that acts up when the weather gets humid There's water pouring out from above the door. | 2016-09-13 - 23000 - Thomas Gibble-cleared drain line with wet-vac and mopped up water on floor - Thomas Gibble | MWO: INTDSA 121A BT transfer to AC: this is the same condensation leak that acts up when the weather gets humid There's water pouring out from above the door. 2016-09-13 - 23000 - Thomas Gibble-cleared drain line with wet-vac and mopped up water on floor - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-12 | 62886 | TMPE-187272 | MWO: ECE 103 The a/c isn't working in the room and there are chemicals in the room. Please have this looked at asap. | 2016-09-14 - 18290 - 9/12/2016 1.25 OT 5:30pm-6:45pm Roque Garcia - ECE Room 103 not cooling I will fix next day 9/13/2016. Install portable i have two set up. - Kerri Perkins; 2016-10-10 - 18290 - John Holloway-verified ahu running checked zone temps checked air flow - John Holloway | MWO: ECE 103 The a/c isn't working in the room and there are chemicals in the room. Please have this looked at asap. 2016-09-14 - 18290 - 9/12/2016 1.25 OT 5:30pm-6:45pm Roque Garcia - ECE Room 103 not cooling I will fix next day 9/13/2016. Install portable i have two set up. - Kerri Perkins; 2016-10-10 - 18290 - John Holloway-verified ahu running checked zone temps checked air flow - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
2016-09-12 | 62936 | TMPE-187222 | MWO IRISH 215 !! Repeat Request. Please come back and finish repairing the A/C in this room. The A/C was working before, but did not have a cover. Now, I can;'t figure out how to make it work. The whole unit is having off the wall by wires. There is staff working in this room today. See re. . . | 2016-09-13 - 18010 - This is a repeat work order. All time and information are recorded on TMPE-161982. - Jennifer Moyer | MWO IRISH 215 !! Repeat Request. Please come back and finish repairing the A/C in this room. The A/C was working before, but did not have a cover. Now, I can;'t figure out how to make it work. The whole unit is having off the wall by wires. There is staff working in this room today. See re. . . 2016-09-13 - 18010 - This is a repeat work order. All time and information are recorded on TMPE-161982. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-12 | 62941 | TMPE-187217 | MWO: Got a report that the air conditioner was not working in this classroom. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 | 2016-10-18 - 18290 - Robert Ecabert-Installed 2 new contactors and a new transformer. - Robert Ecabert | MWO: Got a report that the air conditioner was not working in this classroom. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 2016-10-18 - 18290 - Robert Ecabert-Installed 2 new contactors and a new transformer. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-12 | 62943 | TMPE-187215 | MWO PSB B54F Transferred call to HVAC - PSB RM 54f is a stand alone DX Unit. EMS WO#186428, HVAC WO#187215, TS WO#195481. This room is much to hot. Currently 84 degrees, needs to be 74. Thank you! | 2016-09-15 - 18290 - Zhi Yu-The DX unit low in charge. we charge 3bls R-22. Located the leaks in the ball valve and liquid service valve. - Zhi Yu; 2016-10-24 - 18290 - Zhi Yu-We recover R-22, schedule fire tech to disable Alarm. We replaced the 2 ball valve and solenoid valve. Pressurize the system 300psi for leaks. we vacuum to 500 micron and charge 8lbs r-22.. - Zhi Yu; 2016-10-31 - 18290 - Zhi Yu-We cycle the hotgas valve, the solenoid making loud bizz noise. We replaced new solenoid mkc1 Coil. - Zhi Yu | MWO PSB B54F Transferred call to HVAC - PSB RM 54f is a stand alone DX Unit. EMS WO#186428, HVAC WO#187215, TS WO#195481. This room is much to hot. Currently 84 degrees, needs to be 74. Thank you! 2016-09-15 - 18290 - Zhi Yu-The DX unit low in charge. we charge 3bls R-22. Located the leaks in the ball valve and liquid service valve. - Zhi Yu; 2016-10-24 - 18290 - Zhi Yu-We recover R-22, schedule fire tech to disable Alarm. We replaced the 2 ball valve and solenoid valve. Pressurize the system 300psi for leaks. we vacuum to 500 micron and charge 8lbs r-22.. - Zhi Yu; 2016-10-31 - 18290 - Zhi Yu-We cycle the hotgas valve, the solenoid making loud bizz noise. We replaced new solenoid mkc1 Coil. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-12 | 62952 | TMPE-187206 | MWO: Additional Info: 15 amp/fuse #ATDR15 Noisy fan coil. Possible bad bearings. Also, backup DX cooling unit in space is not cooling when commanded. Possible tripped compressor. Send to HVAC services for checkout. For server room access and contact person call James Muscarra at 602-571-1096 . . . | 2016-09-12 - 18030 - Called out to Jack Polchow - Amanda Thomas; 2016-09-17 - 18030 - Robert Dauscher-Found both primary and secondary cooling sources offline. Tried replacing blown 15amp fuse for building fan coil. Tested unit no ground found, restarted fan coil and fuse blew after running for 45 seconds. (bad motor) Tried resetting Daikin unit and there is an error where the T-stat did not have any mode other than FAN. Unable to contact tech support. due to time of day. - Robert Dauscher; 2016-09-17 - 18030 - Mitchell Andrews-Found both primary and secondary cooling sources offline. Tried replacing blown 15amp fuse for building fan coil. Tested unit no ground found, restarted fan coil and fuse blew after running for 45 seconds. (bad motor) Tried resetting Daikin unit and there is an error where the T-stat did not have any mode other than FAN. Unable to contact tech support. due to time of day. - Robert Dauscher; 2016-09-18 - 18030 - Robert Dauscher-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-09-18 - 18030 - Thomas Gibble-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-09-18 - 18030 - Gail Jackson-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-11-04 - 18030 - Robert Dauscher-worked on the phone with tech support to get mini splits running - Mitchell Andrews | MWO: Additional Info: 15 amp/fuse #ATDR15 Noisy fan coil. Possible bad bearings. Also, backup DX cooling unit in space is not cooling when commanded. Possible tripped compressor. Send to HVAC services for checkout. For server room access and contact person call James Muscarra at 602-571-1096 . . . 2016-09-12 - 18030 - Called out to Jack Polchow - Amanda Thomas; 2016-09-17 - 18030 - Robert Dauscher-Found both primary and secondary cooling sources offline. Tried replacing blown 15amp fuse for building fan coil. Tested unit no ground found, restarted fan coil and fuse blew after running for 45 seconds. (bad motor) Tried resetting Daikin unit and there is an error where the T-stat did not have any mode other than FAN. Unable to contact tech support. due to time of day. - Robert Dauscher; 2016-09-17 - 18030 - Mitchell Andrews-Found both primary and secondary cooling sources offline. Tried replacing blown 15amp fuse for building fan coil. Tested unit no ground found, restarted fan coil and fuse blew after running for 45 seconds. (bad motor) Tried resetting Daikin unit and there is an error where the T-stat did not have any mode other than FAN. Unable to contact tech support. due to time of day. - Robert Dauscher; 2016-09-18 - 18030 - Robert Dauscher-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-09-18 - 18030 - Thomas Gibble-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-09-18 - 18030 - Gail Jackson-Worked with other techs and tech support to bring back on the Daikin unit. Unit Condensing section needs to be shut off for several minutes to allow a full reset of all boards inside unit. Also pulled motor from fan coil to match up at parts house. and picked up new motor for replacement on Monday 9-19-16 - Robert Dauscher; 2016-11-04 - 18030 - Robert Dauscher-worked on the phone with tech support to get mini splits running - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
2016-09-12 | 177121 | RFMT-131210 | The tan rectangular casing for the hallway air conditioning vent (the one closer to the breaker room) fell off. 4NJH7IB | 2016-09-13 - 18010 - Scott Berndt-replaced - Scott Berndt | The tan rectangular casing for the hallway air conditioning vent (the one closer to the breaker room) fell off. 4NJH7IB 2016-09-13 - 18010 - Scott Berndt-replaced - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-12 | 177133 | RFMT-131198 | !! Air conditioning is broken 4NJCJ9B | 2016-09-13 - 18010 - Thor Millsaps-Inspected ac unit. Adjusted freon charge. Replaced 45/5 mfd dual run capacitor. System running normally. Reset tripped circuit breaker at main panel. Referred to facman electrician to inspect multiple breaker problems. - Thor Millsaps | !! Air conditioning is broken 4NJCJ9B 2016-09-13 - 18010 - Thor Millsaps-Inspected ac unit. Adjusted freon charge. Replaced 45/5 mfd dual run capacitor. System running normally. Reset tripped circuit breaker at main panel. Referred to facman electrician to inspect multiple breaker problems. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-09-12 | 177134 | RFMT-131197 | !! Air conditioning is broken 4NJCJ9B | 2016-09-13 - 18010 - Simon Fernandez-reset breaker, repaired as required - Simon Fernandez | !! Air conditioning is broken 4NJCJ9B 2016-09-13 - 18010 - Simon Fernandez-reset breaker, repaired as required - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-09-12 | 177150 | RFMT-131181 | !! Air conditioning is broken 4NJCJ9B | 2016-09-12 - 18010 - Joe Swan-Put portable a/c IN 206 &amp; 208 until Simon can look at A/C tomorrow. Pending - Joe Swan | !! Air conditioning is broken 4NJCJ9B 2016-09-12 - 18010 - Joe Swan-Put portable a/c IN 206 &amp; 208 until Simon can look at A/C tomorrow. Pending - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-12 | 177188 | RFMT-131143 | ASUHC-Agent: Kyle Van Bergen Description: AC stopped working, Who was dispatched: Mike Guckian Time of dispatch: 1:20pm | 2016-09-12 - 18010 - Mike Guckian-replaced filter, reset unit. works good. 60* at vent. - Mike Guckian | ASUHC-Agent: Kyle Van Bergen Description: AC stopped working, Who was dispatched: Mike Guckian Time of dispatch: 1:20pm 2016-09-12 - 18010 - Mike Guckian-replaced filter, reset unit. works good. 60* at vent. - Mike Guckian | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-12 | 177214 | RFMT-131117 | Repeat Request. Sent out a request on 9/1/16 and have had zero response: Service Request # 223901 "The action requested is as follows: Can Olympus clean the air conditioning vents in our office 106 and next door in 107? They are extremely dirty. " 4MM5538 | NA | Repeat Request. Sent out a request on 9/1/16 and have had zero response: Service Request # 223901 "The action requested is as follows: Can Olympus clean the air conditioning vents in our office 106 and next door in 107? They are extremely dirty. " 4MM5538 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-12 | 177225 | RFMT-131106 | !! Repeat Request. AC is not working 4NJ820F | 2016-09-12 - 18010 - Thor Millsaps-Reset circuit breaker. Checked indoor blower motor, outdoor fan motor, compressor, amps, checked for burnt/exposed wires, replaced dual run capacitor. System up and running. If breaker continues to trip, breaker should be replaced. - Thor Millsaps | !! Repeat Request. AC is not working 4NJ820F 2016-09-12 - 18010 - Thor Millsaps-Reset circuit breaker. Checked indoor blower motor, outdoor fan motor, compressor, amps, checked for burnt/exposed wires, replaced dual run capacitor. System up and running. If breaker continues to trip, breaker should be replaced. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
2016-09-12 | 216148 | RACC-112462 | !! I am in room 516D and it has been smelling like something has gone old or rotten. I think it may be in the air filter because I have checked everything in all the areas of the room. I have tried an air freshener and that hasn't worked at all. If someone could check the air filters or vents it wou. . . | NA | !! I am in room 516D and it has been smelling like something has gone old or rotten. I think it may be in the air filter because I have checked everything in all the areas of the room. I have tried an air freshener and that hasn't worked at all. If someone could check the air filters or vents it wou. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-13 | 4758 | WEST-106491 | Air Compressor - Monthly Maintenance | 2016-09-22 - xPM-0100-M - Robert Gailey-operated compressor - Robert Gailey | Air Compressor - Monthly Maintenance 2016-09-22 - xPM-0100-M - Robert Gailey-operated compressor - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-13 | 62567 | TMPE-187591 | Pump has a bad vibration. I have created a work order for EL to look at pump 3 VFD so we can change lead/lag | 2016-11-18 - 23100 - Derek Gittings-replaced motor - Melanie Lamm; 2016-12-16 - 23100 - Michael Kelley-assisted in moving old motor an new one - Michael Kelley; 2017-02-01 - 23100 - Jennifer Moyer-Lazer align pump and motor. - Jennifer Moyer; 2017-02-01 - 23100 - Derek Gittings-Lazer align pump and motor. - Jennifer Moyer | Pump has a bad vibration. I have created a work order for EL to look at pump 3 VFD so we can change lead/lag 2016-11-18 - 23100 - Derek Gittings-replaced motor - Melanie Lamm; 2016-12-16 - 23100 - Michael Kelley-assisted in moving old motor an new one - Michael Kelley; 2017-02-01 - 23100 - Jennifer Moyer-Lazer align pump and motor. - Jennifer Moyer; 2017-02-01 - 23100 - Derek Gittings-Lazer align pump and motor. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-13 | 62614 | TMPE-187544 | MWO: Please have some one come and repair the air conditioning units in the room. Both units are blowing hot air and is it almost unbearable to work in the room. The unit have been looked at before, however, they were not repaired. Side note: other units in Irish A have been repaired, so it is u. . . | 2016-09-19 - 18010 - Thomas Gibble-flushed both fan coils - Thomas Gibble; 2016-09-19 - 18010 - Gail Jackson-flushed both fan coils - Thomas Gibble | MWO: Please have some one come and repair the air conditioning units in the room. Both units are blowing hot air and is it almost unbearable to work in the room. The unit have been looked at before, however, they were not repaired. Side note: other units in Irish A have been repaired, so it is u. . . 2016-09-19 - 18010 - Thomas Gibble-flushed both fan coils - Thomas Gibble; 2016-09-19 - 18010 - Gail Jackson-flushed both fan coils - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-13 | 62709 | TMPE-187449 | SPECIAL FUNDING - replace the shaft seal on Chiller 10. Chiller # 10 Model : YK TH TD J4-DH F Compressor Model: YDHA-90DD. JCI to transfer charge from chiller#10 into onsite storage tanks. Remove coupling and seal. Install new seal and check low speed thrust. Replace oil filter. Evacuate chiller an. . . | NA | SPECIAL FUNDING - replace the shaft seal on Chiller 10. Chiller # 10 Model : YK TH TD J4-DH F Compressor Model: YDHA-90DD. JCI to transfer charge from chiller#10 into onsite storage tanks. Remove coupling and seal. Install new seal and check low speed thrust. Replace oil filter. Evacuate chiller an. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-13 | 62727 | TMPE-187431 | SWO: !! Please open a work order for the Electric Shop to buys parts for the timer at the Football Practice Field. PO is YG202004933. Thank you. Contact Name: Brian Johnson Contact Phone Number: 602-723-9185 Contact Email: Brian.Johnson@asu.edu 42BDEDF | 2016-09-13 - 15000 - Semeon Haile-Replaced burned up 120v coil on new starter for booster pump. - Sean Chrisman; 2016-09-13 - 15000 - Semeon Haile-motor starter needs to be replaced interior contacts are damaged and no longer usable. Ordering new size 2 starter from summit electric will pick up and install on 9-14-16 - Sean Chrisman; 2016-09-13 - 15000 - Sean Chrisman-starter needs to be replaced due to bad contacts. Ordered new from summit will pick it up and install it on 9-14-16 - Sean Chrisman; 2016-09-16 - 15000 - Semeon Haile-troubleshoot irrigation pump - Semeon Haile; 2016-09-16 - 15000 - Semeon Haile-replaced starter, and control relay - Semeon Haile | SWO: !! Please open a work order for the Electric Shop to buys parts for the timer at the Football Practice Field. PO is YG202004933. Thank you. Contact Name: Brian Johnson Contact Phone Number: 602-723-9185 Contact Email: Brian.Johnson@asu.edu 42BDEDF 2016-09-13 - 15000 - Semeon Haile-Replaced burned up 120v coil on new starter for booster pump. - Sean Chrisman; 2016-09-13 - 15000 - Semeon Haile-motor starter needs to be replaced interior contacts are damaged and no longer usable. Ordering new size 2 starter from summit electric will pick up and install on 9-14-16 - Sean Chrisman; 2016-09-13 - 15000 - Sean Chrisman-starter needs to be replaced due to bad contacts. Ordered new from summit will pick it up and install it on 9-14-16 - Sean Chrisman; 2016-09-16 - 15000 - Semeon Haile-troubleshoot irrigation pump - Semeon Haile; 2016-09-16 - 15000 - Semeon Haile-replaced starter, and control relay - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-13 | 62742 | TMPE-187416 | MWO PE West 240: I am teaching a dance class, and the AC is not working. Please fix, ASAP! | 2016-09-15 - 18290 - Zhi Yu-Arrived the unit not running and T/sat blank. unit located roof. We check fuse and transformer good. I call Robert ask, the low voltage supply the t/sat sharing the same transformer located inside the unit adjacent to. - Zhi Yu | MWO PE West 240: I am teaching a dance class, and the AC is not working. Please fix, ASAP! 2016-09-15 - 18290 - Zhi Yu-Arrived the unit not running and T/sat blank. unit located roof. We check fuse and transformer good. I call Robert ask, the low voltage supply the t/sat sharing the same transformer located inside the unit adjacent to. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-13 | 216113 | RACC-112497 | !! Repeat Request. The AC unit is leaking again. Please fix. 4ND6D19 | NA | !! Repeat Request. The AC unit is leaking again. Please fix. 4ND6D19 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-13 | 216124 | RACC-112486 | Spots of black mold inside air conditioning vent (by fridge) making room smell possibly. Please clean the vent or change it. Thank you. 4NO7F1O | NA | Spots of black mold inside air conditioning vent (by fridge) making room smell possibly. Please clean the vent or change it. Thank you. 4NO7F1O NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-13 | 235042 | POLY-113157 | need to fix air compressor. air hose. Leaking air 42B22L5 | NA | need to fix air compressor. air hose. Leaking air 42B22L5 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-13 | 235178 | POLY-113021 | Coils | NA | Coils NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-13 | 256559 | DTPC-111979 | Office is warm, not cooling. 42CB5KN | 2016-09-13 - 18290 - Steve Skibbe-dianoised found bad contactor and changed out unit is cooling - Steve Skibbe | Office is warm, not cooling. 42CB5KN 2016-09-13 - 18290 - Steve Skibbe-dianoised found bad contactor and changed out unit is cooling - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 62251 | TMPE-187906 | MWO: The School of Art would like to request that Gary the FACMAN electrical trouble shooter stop by our sculpture department to help us with a electric motor issue. Please contact Bobby Zokaites cell 540 392 2541 Thanks, George Harris 480 340 4916 42AMFKL 154462 Please cancel this . . . | 2016-09-20 - 15000 - GEORGE HARRIS CALLED AND SAID HE CALLED TO HAVE THIS REQUEST CANCELLED ON 09/14/16. HE SAW THERE WAS AN ELECTRICIAN THIS AFTERNOON. GEORGE STATED IF THE REPAIRS ARE GOING TO BE BILLABLE THEN DO NOT PROCEED WITH ANYMORE WORK. HE DOES NOT HAVE THE FUNDING FOR REPAIRS. I CALLED JOHN S TO INFORM HIM OF GEORGE'S CALL. MM - Monica Moraga | MWO: The School of Art would like to request that Gary the FACMAN electrical trouble shooter stop by our sculpture department to help us with a electric motor issue. Please contact Bobby Zokaites cell 540 392 2541 Thanks, George Harris 480 340 4916 42AMFKL 154462 Please cancel this . . . 2016-09-20 - 15000 - GEORGE HARRIS CALLED AND SAID HE CALLED TO HAVE THIS REQUEST CANCELLED ON 09/14/16. HE SAW THERE WAS AN ELECTRICIAN THIS AFTERNOON. GEORGE STATED IF THE REPAIRS ARE GOING TO BE BILLABLE THEN DO NOT PROCEED WITH ANYMORE WORK. HE DOES NOT HAVE THE FUNDING FOR REPAIRS. I CALLED JOHN S TO INFORM HIM OF GEORGE'S CALL. MM - Monica Moraga | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 62295 | TMPE-187862 | MWO: USB 1420M **TRANSFER** PL to HVAC HVAC the unit is in bad shape and needs better supports. Leak was fixed but unit needs attention because it\\u2019s the cause of the leaks. BT TO PL: LEAK IS COMING FROM THE A/C UNIT DUE TO A CONDENSATE LEAK. ***ORIGINAL REQUEST***There's drops of water comi. . . | 2016-09-30 - 18010 - Roque Garcia-I called and spoke with Steve 9/29/2016 about the issue and he was going to call me back if there is still a problem. 9/30/2016 Steve has not called me so I'm closing WO. - Roque Garcia | MWO: USB 1420M **TRANSFER** PL to HVAC HVAC the unit is in bad shape and needs better supports. Leak was fixed but unit needs attention because it\\u2019s the cause of the leaks. BT TO PL: LEAK IS COMING FROM THE A/C UNIT DUE TO A CONDENSATE LEAK. ***ORIGINAL REQUEST***There's drops of water comi. . . 2016-09-30 - 18010 - Roque Garcia-I called and spoke with Steve 9/29/2016 about the issue and he was going to call me back if there is still a problem. 9/30/2016 Steve has not called me so I'm closing WO. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 62314 | TMPE-187843 | MWO: AH #3565 - the tray is overflowing and dripping! There is a leak from the ceiling that is dripping into a ceiling light. | 2016-09-14 - 18050 - John S indicated that tray is overflowing -- for HVAC - Michelle Ryan; 2016-09-21 - 18050 - Thomas Gibble-cleaned drain line - Thomas Gibble | MWO: AH #3565 - the tray is overflowing and dripping! There is a leak from the ceiling that is dripping into a ceiling light. 2016-09-14 - 18050 - John S indicated that tray is overflowing -- for HVAC - Michelle Ryan; 2016-09-21 - 18050 - Thomas Gibble-cleaned drain line - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 62363 | TMPE-187794 | MWO: NOBLE !! Noble Library EQ room on the SE corner of the building is flooding due to pump spraying out water Issue found by JCI. Please send call to HVAC Mechanical 42B21E0 | 2016-09-14 - 23100 - Called to John Howell - Jeri Zappanti; 2016-12-16 - 23100 - Jose Lopez-found motor tag other tech working on it. - Jose Lopez | MWO: NOBLE !! Noble Library EQ room on the SE corner of the building is flooding due to pump spraying out water Issue found by JCI. Please send call to HVAC Mechanical 42B21E0 2016-09-14 - 23100 - Called to John Howell - Jeri Zappanti; 2016-12-16 - 23100 - Jose Lopez-found motor tag other tech working on it. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-14 | 62405 | TMPE-187752 | MWO: !! There is a wall vent area (air conditioning Unit) in office area-B-161-B-1 (Project Research Room) that makes a loud noise when activated. 42AC6MK | 2016-09-28 - 18010 - Thomas Gibble-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Gail Jackson-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Gail Jackson-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Thomas Gibble-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Thomas Gibble-Remove and reinstall blower motor in Fujitsu mini split. Contacted Tech line for emailed instructions on procedure. Trip to Johnstone to pick up motor. COMPLETE - Gail Jackson; 2016-09-28 - 18010 - Gail Jackson-Remove and reinstall blower motor in Fujitsu mini split. Contacted Tech line for emailed instructions on procedure. Trip to Johnstone to pick up motor. COMPLETE - Gail Jackson | MWO: !! There is a wall vent area (air conditioning Unit) in office area-B-161-B-1 (Project Research Room) that makes a loud noise when activated. 42AC6MK 2016-09-28 - 18010 - Thomas Gibble-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Gail Jackson-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Gail Jackson-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Thomas Gibble-put unit back together and test ran . also we call tech line to find out how to remove and install motor. - Thomas Gibble; 2016-09-28 - 18010 - Thomas Gibble-Remove and reinstall blower motor in Fujitsu mini split. Contacted Tech line for emailed instructions on procedure. Trip to Johnstone to pick up motor. COMPLETE - Gail Jackson; 2016-09-28 - 18010 - Gail Jackson-Remove and reinstall blower motor in Fujitsu mini split. Contacted Tech line for emailed instructions on procedure. Trip to Johnstone to pick up motor. COMPLETE - Gail Jackson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-14 | 62413 | TMPE-187744 | MWO: PSE - E7 !! Please create a high priority WO request for Elect shop to check motor on MUA # 2 it trips the VFD on a current issue and this is creating a negative bldg. pressure for the labs served by this unit Thanks Jeffrey 4N00ABB | 2016-09-20 - 15100 - Arthur Gonzales-previously chked by siemon. rechked .o c fault on vfd. suspect mtr. also locked out by hvac at main sw. could not try and start vfd. - Arthur Gonzales; 2016-11-22 - 15100 - Semeon Haile-troubleshoot, found bad motor that has been replaced by HVAC guys and I commissioned VFD - Semeon Haile | MWO: PSE - E7 !! Please create a high priority WO request for Elect shop to check motor on MUA # 2 it trips the VFD on a current issue and this is creating a negative bldg. pressure for the labs served by this unit Thanks Jeffrey 4N00ABB 2016-09-20 - 15100 - Arthur Gonzales-previously chked by siemon. rechked .o c fault on vfd. suspect mtr. also locked out by hvac at main sw. could not try and start vfd. - Arthur Gonzales; 2016-11-22 - 15100 - Semeon Haile-troubleshoot, found bad motor that has been replaced by HVAC guys and I commissioned VFD - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-14 | 62433 | TMPE-187724 | Bad motor | NA | Bad motor NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 62436 | TMPE-187721 | Bad motor | NA | Bad motor NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 177007 | RFMT-131324 | ASUHC-Agent: Ahmed Khalil Description: Leak coming from AC return vent near the floor and carpet is wet from it. Who was dispatched: Joe Swan Time of dispatch: 6:24PM ASUHC-Agent: Ahmed Khalil 7:11PM Joe called back to dispatch Olympus. Dispatched to Juan. | 2016-09-15 - 18010 - Joe Swan-Found condensate pan full and drain clog so I sucked out pan with wet vac and blow drain line clear as best as i could and installed new filter. Had call center call out Olympus for water extraction. - Joe Swan | ASUHC-Agent: Ahmed Khalil Description: Leak coming from AC return vent near the floor and carpet is wet from it. Who was dispatched: Joe Swan Time of dispatch: 6:24PM ASUHC-Agent: Ahmed Khalil 7:11PM Joe called back to dispatch Olympus. Dispatched to Juan. 2016-09-15 - 18010 - Joe Swan-Found condensate pan full and drain clog so I sucked out pan with wet vac and blow drain line clear as best as i could and installed new filter. Had call center call out Olympus for water extraction. - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-14 | 177014 | RFMT-131317 | Repeat Request. There is a hole in our ac cover and it is leaking. We filled out a request service last week and I got an email saying it was fixed, but we can see that it hasn't been fixed. Attachment(s) 4NNMOIM | 2016-09-15 - 18010 - Thomas Zambrano-wrap pipes. - Thomas Zambrano; 2016-11-09 - 18010 - Thomas Zambrano-fix leak. will remove and replace hatch during summer turn. - Thomas Zambrano | Repeat Request. There is a hole in our ac cover and it is leaking. We filled out a request service last week and I got an email saying it was fixed, but we can see that it hasn't been fixed. Attachment(s) 4NNMOIM 2016-09-15 - 18010 - Thomas Zambrano-wrap pipes. - Thomas Zambrano; 2016-11-09 - 18010 - Thomas Zambrano-fix leak. will remove and replace hatch during summer turn. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-14 | 177016 | RFMT-131315 | !! Check out the vents in room HAVG2172. Residents claimed there was a lot of mold in the vents that is causing them difficulty breathing.. | 2016-09-15 - 18010 - Chester Duncan-Cleaned bath vent, resident had cleaned AC vent Changed air filter Located stack shutoffs and assisted Dan to shut off Replaced toilet handle Rebuilt shower control etc - Chester Duncan | !! Check out the vents in room HAVG2172. Residents claimed there was a lot of mold in the vents that is causing them difficulty breathing.. 2016-09-15 - 18010 - Chester Duncan-Cleaned bath vent, resident had cleaned AC vent Changed air filter Located stack shutoffs and assisted Dan to shut off Replaced toilet handle Rebuilt shower control etc - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-14 | 177017 | RFMT-131314 | !! Concerned about air quality in vent/ black dust/mold coming out.This is a major health concerns and i have already conducted a few illness' during my time at ASU and this may be one of the leading causes. Thank you. 4O286IM | 2016-09-15 - 18010 - Rene Arrieta-replace filter and vacuum out a/c unit - Rene Arrieta | !! Concerned about air quality in vent/ black dust/mold coming out.This is a major health concerns and i have already conducted a few illness' during my time at ASU and this may be one of the leading causes. Thank you. 4O286IM 2016-09-15 - 18010 - Rene Arrieta-replace filter and vacuum out a/c unit - Rene Arrieta | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-09-14 | 177018 | RFMT-131313 | !! Air Quality/Black dust/mold coming of air vent 4NOG0MH | 2016-09-15 - 18010 - Rene Arrieta-replace filter in a/c - Rene Arrieta | !! Air Quality/Black dust/mold coming of air vent 4NOG0MH 2016-09-15 - 18010 - Rene Arrieta-replace filter in a/c - Rene Arrieta | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-14 | 177019 | RFMT-131312 | !! Air is broken (once again!) It is super duper hot in here and this needs to be a priority. The portable air generator barely does anything for our room and this air vent needs to be fixed ASAP! Please buy a new part or something. Thanks! (: 4NJCJ9B | 2016-09-15 - 18010 - David Cates-Reset tripped breaker for AC. Fac-Man has already been requested to check the breaker panel. - David Cates; 2016-09-16 - 18010 - FACMAN Elec. dept out today to check panel. Res. Life HVAC shop copied this wo. today to follow up to insure all is proper and back online. - Gregory Stetka | !! Air is broken (once again!) It is super duper hot in here and this needs to be a priority. The portable air generator barely does anything for our room and this air vent needs to be fixed ASAP! Please buy a new part or something. Thanks! (: 4NJCJ9B 2016-09-15 - 18010 - David Cates-Reset tripped breaker for AC. Fac-Man has already been requested to check the breaker panel. - David Cates; 2016-09-16 - 18010 - FACMAN Elec. dept out today to check panel. Res. Life HVAC shop copied this wo. today to follow up to insure all is proper and back online. - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2016-09-14 | 216139 | RACC-112471 | !! Repeat Request. The a/c unit makes a rough noise when turing off and the noise can be heard when it is "on" through the vent in room "A". 4NFOJ38 | NA | !! Repeat Request. The a/c unit makes a rough noise when turing off and the noise can be heard when it is "on" through the vent in room "A". 4NFOJ38 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-14 | 256523 | DTPC-112015 | warranty, drinking fountain 1st floor, compressor bad, vendor and I removed fountain, warranty change out at shop | 2016-09-14 - 23080 - Keith Griffin-warranty, drinking fountain 1st floor, compressor bad, vendor and I removed fountain, warranty change out at shop - Keith Griffin [Modified: 2016-10-20 Julie Fowler]; 2016-09-30 - 23080 - Keith Griffin-Touch base with David[tech]they have received new compressor, will have new unit next week - Keith Griffin; 2016-10-20 - 23080 - Keith Griffin-Installed drinking fountain on 1st floor west side; warranty - Keith Griffin; 2016-10-20 - 23080 - Keith Griffin-Installed drinking fountain on 1st floor west side; warranty/ finished install with cover and adjustments - Keith Griffin | warranty, drinking fountain 1st floor, compressor bad, vendor and I removed fountain, warranty change out at shop 2016-09-14 - 23080 - Keith Griffin-warranty, drinking fountain 1st floor, compressor bad, vendor and I removed fountain, warranty change out at shop - Keith Griffin [Modified: 2016-10-20 Julie Fowler]; 2016-09-30 - 23080 - Keith Griffin-Touch base with David[tech]they have received new compressor, will have new unit next week - Keith Griffin; 2016-10-20 - 23080 - Keith Griffin-Installed drinking fountain on 1st floor west side; warranty - Keith Griffin; 2016-10-20 - 23080 - Keith Griffin-Installed drinking fountain on 1st floor west side; warranty/ finished install with cover and adjustments - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-15 | 4650 | WEST-106599 | trouble shoot long pond level pump control system Controller has to custom made by supplier. unit is on order. long lead time is expected. rr. 12/05/2016 12/19- rec'd controller. due to time restrictions, new controller will be installed at a later date on a new work order. rr. | 2016-09-15 - 15000 - Tim Jowers-Troubleshoot pump controls; found electrical issue and turned this over to electrician. - Catherine Riley; 2016-09-16 - 15000 - Joseph Danielek-found duplex switches are failing new ones on order - Joseph Danielek; 2016-09-16 - 15000 - Joseph Danielek-checked out control system a little with the afternoon sun there isn't enough light in the pump vault to trouble shoot safely - Joseph Danielek; 2016-09-27 - 15000 - Joseph Danielek-installed 2 15 amp single-pole double rocker switch total cost including freight 25.15 - Joseph Danielek; 2016-10-04 - 15000 - Joseph Danielek-circuit #10 tripped again / retraced #10 inside fountain control enclosures / unwired and metered each conductor (again) / hot wire from gfci/toggle switch into pump starter cabinet going to ground ramdomly / remove and replaced section of conductor/wire / jet and filter pumps running / inspected wire finding no issues with the insulation and no sign of arcing - Joseph Danielek [Modified: 2016-10-04 Joseph Danielek]; 2016-10-04 - 15000 - Joseph Danielek-circuit #10 tripped / reset late afternoon / checked out controls a bit deciding to leave it until tuesday 10-4 as dark in vault with sun overhead - Joseph Danielek; 2016-10-05 - 15000 - Joseph Danielek-checked probe/tips-clean/shaft compression nut loose-suspect moisture in control wire raceway-dissembled probe base found no evidence of leak/installed new wire nuts on connections3)/while checking the controller gcfi tripped-controller completely went bad/temporary wired in manual toggle switch to bypass level controller - Joseph Danielek; 2016-10-19 - 15000 - Joseph Danielek-ask jim (stores) to order controller - Joseph Danielek; 2016-10-20 - 15000 - Joseph Danielek-confirmed with jim-stores on purchasing controller - Joseph Danielek | trouble shoot long pond level pump control system Controller has to custom made by supplier. unit is on order. long lead time is expected. rr. 12/05/2016 12/19- rec'd controller. due to time restrictions, new controller will be installed at a later date on a new work order. rr. 2016-09-15 - 15000 - Tim Jowers-Troubleshoot pump controls; found electrical issue and turned this over to electrician. - Catherine Riley; 2016-09-16 - 15000 - Joseph Danielek-found duplex switches are failing new ones on order - Joseph Danielek; 2016-09-16 - 15000 - Joseph Danielek-checked out control system a little with the afternoon sun there isn't enough light in the pump vault to trouble shoot safely - Joseph Danielek; 2016-09-27 - 15000 - Joseph Danielek-installed 2 15 amp single-pole double rocker switch total cost including freight 25.15 - Joseph Danielek; 2016-10-04 - 15000 - Joseph Danielek-circuit #10 tripped again / retraced #10 inside fountain control enclosures / unwired and metered each conductor (again) / hot wire from gfci/toggle switch into pump starter cabinet going to ground ramdomly / remove and replaced section of conductor/wire / jet and filter pumps running / inspected wire finding no issues with the insulation and no sign of arcing - Joseph Danielek [Modified: 2016-10-04 Joseph Danielek]; 2016-10-04 - 15000 - Joseph Danielek-circuit #10 tripped / reset late afternoon / checked out controls a bit deciding to leave it until tuesday 10-4 as dark in vault with sun overhead - Joseph Danielek; 2016-10-05 - 15000 - Joseph Danielek-checked probe/tips-clean/shaft compression nut loose-suspect moisture in control wire raceway-dissembled probe base found no evidence of leak/installed new wire nuts on connections3)/while checking the controller gcfi tripped-controller completely went bad/temporary wired in manual toggle switch to bypass level controller - Joseph Danielek; 2016-10-19 - 15000 - Joseph Danielek-ask jim (stores) to order controller - Joseph Danielek; 2016-10-20 - 15000 - Joseph Danielek-confirmed with jim-stores on purchasing controller - Joseph Danielek | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7
2016-09-15 | 62095 | TMPE-188062 | MWO: LAW - 7D Elevator pump room 7D - the motor is cycling continuously may cause overheating. | 2016-09-15 - 16000 - Called to James. - Michelle Ryan | MWO: LAW - 7D Elevator pump room 7D - the motor is cycling continuously may cause overheating. 2016-09-15 - 16000 - Called to James. - Michelle Ryan | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-15 | 62134 | TMPE-188023 | Payne Hall:- Condensate dripping from float linkage on to Pump#1 motor. | NA | Payne Hall:- Condensate dripping from float linkage on to Pump#1 motor. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-15 | 62155 | TMPE-188002 | MWO: 9/15/16 Air Stop cock in the lab is failing. It is the Northwest most bench set in the room. the air is currently isolated to the bench. Can we please have a new stop cock installed. 4NBD334 | 2016-10-18 - 18010 - Jose Lopez-inspect lab for problem didn't found any problem.call customer(Nevin Simons)he explain the problem to me over the phone, found one of the valves lose. fix unit working. - Jose Lopez | MWO: 9/15/16 Air Stop cock in the lab is failing. It is the Northwest most bench set in the room. the air is currently isolated to the bench. Can we please have a new stop cock installed. 4NBD334 2016-10-18 - 18010 - Jose Lopez-inspect lab for problem didn't found any problem.call customer(Nevin Simons)he explain the problem to me over the phone, found one of the valves lose. fix unit working. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-09-15 | 62218 | TMPE-187939 | SWO: Please have the HVAC Shop check the merchandiser refrigerator in room 121 at SDSP and see if it can be repaired. Removal of refrigerant from merchandiser refrigerator PO is YG202004938. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu. . . | 2016-09-28 - 18240 - Thomas Gibble-check out refrigerator and it has a bad compressor. - Thomas Gibble | SWO: Please have the HVAC Shop check the merchandiser refrigerator in room 121 at SDSP and see if it can be repaired. Removal of refrigerant from merchandiser refrigerator PO is YG202004938. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu. . . 2016-09-28 - 18240 - Thomas Gibble-check out refrigerator and it has a bad compressor. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 62245 | TMPE-187912 | Replace oil/water separator filter on air compressor line | NA | Replace oil/water separator filter on air compressor line NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 62255 | TMPE-187902 | MWO: ERC BASEMENT AIR COMPRESSOR Y#8536 - COOLING FAN COIL IS LEAKING OIL. | 2016-12-16 - 18030 - Jose Lopez-new air compressor - Jose Lopez | MWO: ERC BASEMENT AIR COMPRESSOR Y#8536 - COOLING FAN COIL IS LEAKING OIL. 2016-12-16 - 18030 - Jose Lopez-new air compressor - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-15 | 62827 | TMPE-187331 | BREAKDOWN - BLADES FOR MOWER WILL NOT ENGAGE... | 2016-09-12 - 26000 - Robert Ferrera-EXAMINED UNIT... FOUND THAT BLADES WOULD NOT ENGAGE WHEN PTO WAS ENGAGED... TRACED PROBLEM BACK TO A FAULTY WIRING CONNECTOR ON THE PTO CLUTCH... TOOK APART CONNECTOR, REWIRED ENDS, PLUGGED THEM BACK IN... WORKS AS DESIGNED... - Robert Ferrera | BREAKDOWN - BLADES FOR MOWER WILL NOT ENGAGE... 2016-09-12 - 26000 - Robert Ferrera-EXAMINED UNIT... FOUND THAT BLADES WOULD NOT ENGAGE WHEN PTO WAS ENGAGED... TRACED PROBLEM BACK TO A FAULTY WIRING CONNECTOR ON THE PTO CLUTCH... TOOK APART CONNECTOR, REWIRED ENDS, PLUGGED THEM BACK IN... WORKS AS DESIGNED... - Robert Ferrera | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-15 | 63179 | TMPE-186979 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63180 | TMPE-186978 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63181 | TMPE-186977 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63182 | TMPE-186976 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63183 | TMPE-186975 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63184 | TMPE-186974 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 63185 | TMPE-186973 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 176939 | RFMT-131392 | !! Please send someone to flush the a/c. It's not working. CALLED TO JOE SWAN Submitted by 4NID637 | 2016-09-16 - 18010 - Joe Swan-flushed coils but it was not needed. Complete - Joe Swan | !! Please send someone to flush the a/c. It's not working. CALLED TO JOE SWAN Submitted by 4NID637 2016-09-16 - 18010 - Joe Swan-flushed coils but it was not needed. Complete - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-15 | 176957 | RFMT-131374 | !! The Air Conditioning is not working properly. It is blowing 10 Degrees hotter than usual (estimated). I noticed it this morning and it has gotten increasingly worse throughout the day. I would like to get this fixed ASAP in the event it soon stops working entirely. Thank you. 4NE19IO | NA | !! The Air Conditioning is not working properly. It is blowing 10 Degrees hotter than usual (estimated). I noticed it this morning and it has gotten increasingly worse throughout the day. I would like to get this fixed ASAP in the event it soon stops working entirely. Thank you. 4NE19IO NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-15 | 176998 | RFMT-131333 | Replace AC coil | 2016-09-16 - 18010 - Simon Fernandez-removed and replaced fan coil assembly. rechecked a/c unit no leaks. - Simon Fernandez | Replace AC coil 2016-09-16 - 18010 - Simon Fernandez-removed and replaced fan coil assembly. rechecked a/c unit no leaks. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-15 | 177000 | RFMT-131331 | Room is not getting enough air | 2016-09-15 - 18010 - Thomas Zambrano-a new motor was put on by Simon and Thor.Have simon look up specs for unit to see if a higher rpm motor can be install and have them check and or change the coil. - Thomas Zambrano | Room is not getting enough air 2016-09-15 - 18010 - Thomas Zambrano-a new motor was put on by Simon and Thor.Have simon look up specs for unit to see if a higher rpm motor can be install and have them check and or change the coil. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-15 | 216052 | RACC-112558 | !! The ceiling fan does not work in my room (A) and the A/C unit is leaking water in the hallway of the apartment when turned on. These must be fixed immediately. Thanks. 4ND8FKF | NA | !! The ceiling fan does not work in my room (A) and the A/C unit is leaking water in the hallway of the apartment when turned on. These must be fixed immediately. Thanks. 4ND8FKF NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-15 | 234941 | POLY-113258 | 9-26-16 A Purchase Order SC 23117P00121 has been issued to Efficiency Mechanical II Inc. in the amount of $17,954.00 and sent to Steve Clark and vendor. REPLACEMENT OF THE 10 TON SPLIT HEAT PUMP SYSTEM 4O216EO | NA | 9-26-16 A Purchase Order SC 23117P00121 has been issued to Efficiency Mechanical II Inc. in the amount of $17,954.00 and sent to Steve Clark and vendor. REPLACEMENT OF THE 10 TON SPLIT HEAT PUMP SYSTEM 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-16 | 4639 | WEST-106610 | Gasket on Freezer door needs to be fixed. It keeps coming off. | 2016-09-28 - 18180 - Alfred Rohe-Gasket is short across the top. It is a dart gasket and will not stay in the groove. Reinstalled gasket and advised customer should it come out again, have a vendor replace it. - Alfred Rohe | Gasket on Freezer door needs to be fixed. It keeps coming off. 2016-09-28 - 18180 - Alfred Rohe-Gasket is short across the top. It is a dart gasket and will not stay in the groove. Reinstalled gasket and advised customer should it come out again, have a vendor replace it. - Alfred Rohe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-16 | 61862 | TMPE-188295 | MWO: !! The AC in the Locker Room at Soccer is not working and we have a game today. Please send someone from HVAC ASAP. I believe this is still a warrant y issue. Thank you. Contact Name: Josh Perry Contact Phone Number: 480-544-8549 Contact Email: Joshua.Perry@asu.edu 42BDEDF | 2016-09-26 - 18010 - Robert Dauscher-***Was assigned call on a non-scheduled work day. Did not receive call till the AM of Saturday 9-24-2016*** Found chiller working properly. Found chilled water valve not opening as it should. Called in EMS on call and assisted him. Found T-stat to be faulty. Installed new EMS stat and tested system. Working properly. - Robert Dauscher | MWO: !! The AC in the Locker Room at Soccer is not working and we have a game today. Please send someone from HVAC ASAP. I believe this is still a warrant y issue. Thank you. Contact Name: Josh Perry Contact Phone Number: 480-544-8549 Contact Email: Joshua.Perry@asu.edu 42BDEDF 2016-09-26 - 18010 - Robert Dauscher-***Was assigned call on a non-scheduled work day. Did not receive call till the AM of Saturday 9-24-2016*** Found chiller working properly. Found chilled water valve not opening as it should. Called in EMS on call and assisted him. Found T-stat to be faulty. Installed new EMS stat and tested system. Working properly. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 3
2016-09-16 | 62071 | TMPE-188086 | MWO: PSB 337 The air is blowing from the vent very strong and loud. Also, There's no cover over the filter so the strong air is blowing out the filter. | NA | MWO: PSB 337 The air is blowing from the vent very strong and loud. Also, There's no cover over the filter so the strong air is blowing out the filter. NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-16 | 176899 | RFMT-131432 | Thor / Simon - FYI - David has been assigned you may need to follow up. Thank you, Greg ____________________________________________ !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it . . . | 2016-09-17 - 18010 - Res. Life HVAC has checked unit - blower motor has been ordered. Temp. HVAC units are in place. - Gregory Stetka; 2016-09-22 - 18010 - Simon Fernandez-checked a/c unit found bad blower motor . awaiting motor. Motor replaced Mon. by THOR - Simon Fernandez | Thor / Simon - FYI - David has been assigned you may need to follow up. Thank you, Greg ____________________________________________ !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it . . . 2016-09-17 - 18010 - Res. Life HVAC has checked unit - blower motor has been ordered. Temp. HVAC units are in place. - Gregory Stetka; 2016-09-22 - 18010 - Simon Fernandez-checked a/c unit found bad blower motor . awaiting motor. Motor replaced Mon. by THOR - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-16 | 176901 | RFMT-131430 | Thor / Simon - FYI - David has been assigned you may need to follow up. Thank you, Greg ___________________________________________ !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it o. . . | 2016-09-17 - 18010 - Res. Life HVAC has checked unit an blower motor has been ordered. Temp. portable HVAC units are in place for now. - Gregory Stetka; 2016-09-19 - 18010 - Thor Millsaps-Replaced Indoor blower motor with X-13 Rescue motor - Thor Millsaps | Thor / Simon - FYI - David has been assigned you may need to follow up. Thank you, Greg ___________________________________________ !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it o. . . 2016-09-17 - 18010 - Res. Life HVAC has checked unit an blower motor has been ordered. Temp. portable HVAC units are in place for now. - Gregory Stetka; 2016-09-19 - 18010 - Thor Millsaps-Replaced Indoor blower motor with X-13 Rescue motor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-16 | 176908 | RFMT-131423 | Simon / Thor; Please follow up after ASU electrical dept has completed their w.o.for electrical panel circuit check and to insure all is proper with the HVAC system and it is back on line. Thank you, Greg ____________________________________________ !! Air is broken (once again!) It is super du. . . | 2016-09-22 - 18010 - Simon Fernandez-checked a/c unit found breaker tripped .requested electrician to check buss bar and circuit breaker. Electrician replaced circuit breaker. a/c unit okay - Simon Fernandez | Simon / Thor; Please follow up after ASU electrical dept has completed their w.o.for electrical panel circuit check and to insure all is proper with the HVAC system and it is back on line. Thank you, Greg ____________________________________________ !! Air is broken (once again!) It is super du. . . 2016-09-22 - 18010 - Simon Fernandez-checked a/c unit found breaker tripped .requested electrician to check buss bar and circuit breaker. Electrician replaced circuit breaker. a/c unit okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-09-16 | 176909 | RFMT-131422 | Simon / Thor; Please follow up after ASU electrical dept has completed their w.o. for panel circuit check and insure all is proper with the HAVC system and it is back on line. Thank you, Greg ____________________________________________ !! Air is broken (once again!) It is super duper hot in her. . . | 2016-09-19 - 18010 - Thor Millsaps-Facman electrician replaced breaker for a/c unit at main panel. Said breaker switch was burnt. A/C unit running properly. Checked all components. Removed portable ac units from room. - Thor Millsaps | Simon / Thor; Please follow up after ASU electrical dept has completed their w.o. for panel circuit check and insure all is proper with the HAVC system and it is back on line. Thank you, Greg ____________________________________________ !! Air is broken (once again!) It is super duper hot in her. . . 2016-09-19 - 18010 - Thor Millsaps-Facman electrician replaced breaker for a/c unit at main panel. Said breaker switch was burnt. A/C unit running properly. Checked all components. Removed portable ac units from room. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2016-09-16 | 176914 | RFMT-131417 | !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it off. is blowing cold air but the sound isnt right Room 106 and and 108 F 4NJ36A3 | 2016-09-17 - 18010 - Spoke with David on the phone - he has looked at the unit and had contacted Simon for further repairs. - Gregory Stetka; 2016-09-21 - 18010 - David Cates-Checked AC closet but mounts were secure. Simon and Thor replaced AC blower motor, please create a TMA for them to account for their time on this issue. - David Cates; 2016-09-21 - 18010 - Thor and Simon completed work - Gregory Stetka | !! Air conditioning is extremly loud. Had it off all day yesterday, turned it on it sounded like a dead cat in the room and it whistles in the other room. kept it off. is blowing cold air but the sound isnt right Room 106 and and 108 F 4NJ36A3 2016-09-17 - 18010 - Spoke with David on the phone - he has looked at the unit and had contacted Simon for further repairs. - Gregory Stetka; 2016-09-21 - 18010 - David Cates-Checked AC closet but mounts were secure. Simon and Thor replaced AC blower motor, please create a TMA for them to account for their time on this issue. - David Cates; 2016-09-21 - 18010 - Thor and Simon completed work - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-16 | 176929 | RFMT-131402 | !! Help HD - Jonathan Breeze 09/15/16 - 5:56 PM Building: _University Towers__________ Room/Area:___611__ Requested By: _kyle inthavong_________ Phone: ___209.918.5526__________ Description of Problem or Complaint: AC unit is leaking. Caller said someone already came out but the problem is stil. . . | 2016-09-16 - 18010 - Thomas Zambrano-top chiller ball valve leaking at handle, somebody put a deverter pan under neath pipe to catch water.The valve needs to be replaced asap. - Thomas Zambrano | !! Help HD - Jonathan Breeze 09/15/16 - 5:56 PM Building: _University Towers__________ Room/Area:___611__ Requested By: _kyle inthavong_________ Phone: ___209.918.5526__________ Description of Problem or Complaint: AC unit is leaking. Caller said someone already came out but the problem is stil. . . 2016-09-16 - 18010 - Thomas Zambrano-top chiller ball valve leaking at handle, somebody put a deverter pan under neath pipe to catch water.The valve needs to be replaced asap. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-16 | 215979 | RACC-112631 | !! The air conditioning is broken 4NOL3O8 | NA | !! The air conditioning is broken 4NOL3O8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-16 | 216011 | RACC-112599 | !! Repeat Request. A/C filter area dripping clear liquid whenever the fan was on. 4NFAKC2 | NA | !! Repeat Request. A/C filter area dripping clear liquid whenever the fan was on. 4NFAKC2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-17 | 176789 | RFMT-131542 | Cindy Luna 09/17/2016 17:32 - Too hot in elevator equipment room. 5:35pm - Dispatched Mike Guckien @ 480-316-8109. | 2016-09-19 - 18010 - Mike Guckian-deployed portable ac units to keep control panels cool. - Mike Guckian | Cindy Luna 09/17/2016 17:32 - Too hot in elevator equipment room. 5:35pm - Dispatched Mike Guckien @ 480-316-8109. 2016-09-19 - 18010 - Mike Guckian-deployed portable ac units to keep control panels cool. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-17 | 176820 | RFMT-131511 | !! AC broken -- it's 80 degrees in the room and this is our fourth request, it gets worse every time somebody comes to attempt to fix it. 4NOF205 | 2016-09-19 - 18010 - Thomas Zambrano-the unit needs to be sent to hvac tech. theres nothing i can do . the return line is clogged - Thomas Zambrano | !! AC broken -- it's 80 degrees in the room and this is our fourth request, it gets worse every time somebody comes to attempt to fix it. 4NOF205 2016-09-19 - 18010 - Thomas Zambrano-the unit needs to be sent to hvac tech. theres nothing i can do . the return line is clogged - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-17 | 176854 | RFMT-131477 | PM - Please check all stairwells; railings , treads ,landings, lighting to insure all is in proper working , undamaged and safe conditions. Repair , correct , report as needed. Thank you. | 2016-09-29 - 13130 - Salvatore Marasco Jr-*Southeast stairs have cracks in cement on landing and on stairs. *Northwest stairs have small cracks in cement. *Corner of the Northwest 2nd floor hallway has broken cement at base of support pole. - Salvatore Marasco Jr | PM - Please check all stairwells; railings , treads ,landings, lighting to insure all is in proper working , undamaged and safe conditions. Repair , correct , report as needed. Thank you. 2016-09-29 - 13130 - Salvatore Marasco Jr-*Southeast stairs have cracks in cement on landing and on stairs. *Northwest stairs have small cracks in cement. *Corner of the Northwest 2nd floor hallway has broken cement at base of support pole. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-17 | 176864 | RFMT-131467 | PM - Please check all buildings electrical, equipment , storage and mech. rooms for proper conditions. Repair , correct , report as needed. | 2016-10-03 - 10010 - Salvatore Marasco Jr--!st floor custodial/I.T. closet has custodians cleaning supplies. -2nd floor custodial closet has cleaning supplies. -Basement is the storage for glass plates for all center campus buildings. Needs to be swept out and exterminated of spiders and such. -!st floor storage/former kitchen has air filters stored for the buildings Irish B&amp;C. -Electric panels look to be in good working order and are locked away from public. - Salvatore Marasco Jr | PM - Please check all buildings electrical, equipment , storage and mech. rooms for proper conditions. Repair , correct , report as needed. 2016-10-03 - 10010 - Salvatore Marasco Jr--!st floor custodial/I.T. closet has custodians cleaning supplies. -2nd floor custodial closet has cleaning supplies. -Basement is the storage for glass plates for all center campus buildings. Needs to be swept out and exterminated of spiders and such. -!st floor storage/former kitchen has air filters stored for the buildings Irish B&amp;C. -Electric panels look to be in good working order and are locked away from public. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-17 | 176865 | RFMT-131466 | PM - Please check all buildings electrical, equipment , storage and mech. rooms for proper conditions. Repair , correct , report as needed. | 2016-10-03 - 10010 - Salvatore Marasco Jr--Electric panels look to be in good working order and are locked away from the public. -1st floor closet has air filters stored along with custodial supplies. -2nd floor closet has custodial supplies stored. -Basement needs to be swept out and rid of some debris. - Salvatore Marasco Jr | PM - Please check all buildings electrical, equipment , storage and mech. rooms for proper conditions. Repair , correct , report as needed. 2016-10-03 - 10010 - Salvatore Marasco Jr--Electric panels look to be in good working order and are locked away from the public. -1st floor closet has air filters stored along with custodial supplies. -2nd floor closet has custodial supplies stored. -Basement needs to be swept out and rid of some debris. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-17 | 234911 | POLY-113288 | !! Our air Conditioning unit outsides fan is not rotating and we have the air condition on 4N7B313 | NA | !! Our air Conditioning unit outsides fan is not rotating and we have the air condition on 4N7B313 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-18 | 61279 | TMPE-188878 | SWO University Towers 103/105: !! September 13, 2016 The Department of Environmental Health and Safety (EH&S) received a request for an Indoor Air Quality (IAQ) check from Arizona Division of Occupational Safety & Health regarding concerns of a complaint regarding the occupants of the Tempe Campu. . . | 2016-09-19 - 18010 - Emailed HVAC of the request and provide a status when completed (FF) - Francesca Fernandez; 2016-09-19 - 18010 - Carl Karr-Checked outside aid dampers on 103,103c,and 105. Found all dampers open. Plumbing shop repaired broken vent lines,perhaps this was the problem. - Carl Karr; 2016-09-19 - 18010 - Mitchell Andrews-Checked outside aid dampers on 103,103c,and 105. Found all dampers open. Plumbing shop repaired broken vent lines,perhaps this was the problem. - Carl Karr | SWO University Towers 103/105: !! September 13, 2016 The Department of Environmental Health and Safety (EH&S) received a request for an Indoor Air Quality (IAQ) check from Arizona Division of Occupational Safety & Health regarding concerns of a complaint regarding the occupants of the Tempe Campu. . . 2016-09-19 - 18010 - Emailed HVAC of the request and provide a status when completed (FF) - Francesca Fernandez; 2016-09-19 - 18010 - Carl Karr-Checked outside aid dampers on 103,103c,and 105. Found all dampers open. Plumbing shop repaired broken vent lines,perhaps this was the problem. - Carl Karr; 2016-09-19 - 18010 - Mitchell Andrews-Checked outside aid dampers on 103,103c,and 105. Found all dampers open. Plumbing shop repaired broken vent lines,perhaps this was the problem. - Carl Karr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-18 | 176819 | RFMT-131512 | Please inspect the A/C unit in Cluster J's chapter room and study room. Thanks, Carli 4NF4L2O | 2016-09-19 - 18010 - Thor Millsaps-Downstairs ac unit not cooling. Defrost control board not putting out 24v to contactor. Bypassed defrost board. System up and running. Will need to replace defrost board for proper heating operation in winter. Upstairs unit running properly in cooling. - Thor Millsaps | Please inspect the A/C unit in Cluster J's chapter room and study room. Thanks, Carli 4NF4L2O 2016-09-19 - 18010 - Thor Millsaps-Downstairs ac unit not cooling. Defrost control board not putting out 24v to contactor. Bypassed defrost board. System up and running. Will need to replace defrost board for proper heating operation in winter. Upstairs unit running properly in cooling. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-19 | 61072 | TMPE-189085 | MWO CNTRPT 310-10 Repeat Request. The AC unit in conference room 310-10 makes a loud buzzing noise when it is running. It makes it difficult for people to hear when someone is presenting. Can someone take a look at the unit and see if this noise is normal? Thank you! 4MO5454 | 2016-09-26 - 18010 - Michael Cozens-Found noisy compressor with oil spray. Turned over to HVAC for checkout and repair - Mike Cozens | MWO CNTRPT 310-10 Repeat Request. The AC unit in conference room 310-10 makes a loud buzzing noise when it is running. It makes it difficult for people to hear when someone is presenting. Can someone take a look at the unit and see if this noise is normal? Thank you! 4MO5454 2016-09-26 - 18010 - Michael Cozens-Found noisy compressor with oil spray. Turned over to HVAC for checkout and repair - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-19 | 61169 | TMPE-188988 | MWO ECG 346 Suite!!! EMS to HVAC- the Air Compressor for the building is down. All rooms in this suite are without AC. Very hot, please address asap, thank you! | 2016-09-26 - 18290 - Roque Garcia-The air compressor was manually shut off by the contracting company Scotts Electric Motor repair replacing the chilled water pump motor located next to the air compressor, because it was noisy. I called and spoke with John and advised him of my findings. - Roque Garcia | MWO ECG 346 Suite!!! EMS to HVAC- the Air Compressor for the building is down. All rooms in this suite are without AC. Very hot, please address asap, thank you! 2016-09-26 - 18290 - Roque Garcia-The air compressor was manually shut off by the contracting company Scotts Electric Motor repair replacing the chilled water pump motor located next to the air compressor, because it was noisy. I called and spoke with John and advised him of my findings. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-19 | 61198 | TMPE-188959 | MWO COOR 1st Flr Both of the drinking fountains across room 150 (and in that area) are running with very warm water. Please look into as soon as you can, thank you. | 2016-09-20 - 23080 - Donald Crowe-transfer to HVAC I plugged in drinking fountain that is farthest South in breezeway but the motor did not come on. the other drinking fountain was already plugged in but the cooling motor was not running either. materials: none - Donald Crowe | MWO COOR 1st Flr Both of the drinking fountains across room 150 (and in that area) are running with very warm water. Please look into as soon as you can, thank you. 2016-09-20 - 23080 - Donald Crowe-transfer to HVAC I plugged in drinking fountain that is farthest South in breezeway but the motor did not come on. the other drinking fountain was already plugged in but the cooling motor was not running either. materials: none - Donald Crowe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-19 | 61199 | TMPE-188958 | MWO: It is reported, "LSC sub-basement room L2-45 (ultilty room) Details: R175 water chiller has stopped cooling. This chiller services a microscope in L2-34. This originally occurred last week, system crashed. Re-started system, cooled down OK but on Sat morning had crashed again. Request HVAC t. . . | 2016-09-26 - 18080 - Roque Garcia-Upon arrival I met with Professor Dave he is located on the same level and he found and resolved by cleaning the HX. He was going to call Judy and let her know the chiller is ok and have her contact FACMAN with update. - Roque Garcia | MWO: It is reported, "LSC sub-basement room L2-45 (ultilty room) Details: R175 water chiller has stopped cooling. This chiller services a microscope in L2-34. This originally occurred last week, system crashed. Re-started system, cooled down OK but on Sat morning had crashed again. Request HVAC t. . . 2016-09-26 - 18080 - Roque Garcia-Upon arrival I met with Professor Dave he is located on the same level and he found and resolved by cleaning the HX. He was going to call Judy and let her know the chiller is ok and have her contact FACMAN with update. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-19 | 61205 | TMPE-188952 | MWO IRISH 128 !! Toward the north end of the building (first floor) between the offices 128 and 131, the A/C or cooler unit needs to be cleaned and flushed out. There is stagnant/corrosive water in the pipes that need to be drained. It is affecting the health of staff members. 42C5AE4 | 2016-12-30 - 18010 - PM crew to flush in April. - Jennifer Moyer | MWO IRISH 128 !! Toward the north end of the building (first floor) between the offices 128 and 131, the A/C or cooler unit needs to be cleaned and flushed out. There is stagnant/corrosive water in the pipes that need to be drained. It is affecting the health of staff members. 42C5AE4 2016-12-30 - 18010 - PM crew to flush in April. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-19 | 61277 | TMPE-188880 | MWO Central Plant: work order for Robert Dauscher to assist. ASUHC-jbreeze new WO for Luis to make repairs - LL EQ room chilled water Description- Greg called in at 907(actually 913) saying that there was a chilled water leak somewhere on campus and to call the plumber to have him investigate . . . | 2016-09-26 - 23100 - Robert Dauscher-replaced 10Hp motor in basement of Wilson hall and assisted with chilled water line repair. also called in Weekend electrician to bypass motor starter so new pump motor could run A/C-Mech portion of this call is complete. Electricians waiting on parts for motor starter. - Robert Dauscher | MWO Central Plant: work order for Robert Dauscher to assist. ASUHC-jbreeze new WO for Luis to make repairs - LL EQ room chilled water Description- Greg called in at 907(actually 913) saying that there was a chilled water leak somewhere on campus and to call the plumber to have him investigate . . . 2016-09-26 - 23100 - Robert Dauscher-replaced 10Hp motor in basement of Wilson hall and assisted with chilled water line repair. also called in Weekend electrician to bypass motor starter so new pump motor could run A/C-Mech portion of this call is complete. Electricians waiting on parts for motor starter. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-19 | 176722 | RFMT-131609 | !! The a/c is causing a foul smell. Submitted by 4NID637 | 2016-09-21 - 18010 - David Cates-AC condensation was clogged up, got it draining back into the pipes in L206. Also replaced filters in both rooms and pulled items away from air returns. Greg called Olympus to extract the standing water under the AC coils. - David Cates; 2016-09-21 - 18010 - Olympus reqstd serv.rqst.# 228901 - Gregory Stetka | !! The a/c is causing a foul smell. Submitted by 4NID637 2016-09-21 - 18010 - David Cates-AC condensation was clogged up, got it draining back into the pipes in L206. Also replaced filters in both rooms and pulled items away from air returns. Greg called Olympus to extract the standing water under the AC coils. - David Cates; 2016-09-21 - 18010 - Olympus reqstd serv.rqst.# 228901 - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-19 | 176724 | RFMT-131607 | !! A/C is broken 4NOLEOA | 2016-09-20 - 18010 - Thomas Zambrano-the ball valve needs to be replace asap. flushing it will not work anymore. please sent to plumber to repair. - Thomas Zambrano | !! A/C is broken 4NOLEOA 2016-09-20 - 18010 - Thomas Zambrano-the ball valve needs to be replace asap. flushing it will not work anymore. please sent to plumber to repair. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2
2016-09-19 | 176737 | RFMT-131594 | !! The AC motor is broken | 2016-09-20 - 18010 - Thomas Zambrano-replaced moter. - Thomas Zambrano | !! The AC motor is broken 2016-09-20 - 18010 - Thomas Zambrano-replaced moter. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-09-19 | 176742 | RFMT-131589 | Please change the air filter Submitted by 4NID637 | 2016-09-20 - 18010 - Scott Berndt-replaced a/c filter - Scott Berndt | Please change the air filter Submitted by 4NID637 2016-09-20 - 18010 - Scott Berndt-replaced a/c filter - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-19 | 176752 | RFMT-131579 | Please replace the ball valve and the flush valve at University Towers room 311. (Dan) | 2016-09-21 - 23000 - Dan Guerra-This unit already has ball valves and flush valves on it that work, so we flush out a.c. coil real good and now the Temp. reading is 50 to 51. - Dan Guerra | Please replace the ball valve and the flush valve at University Towers room 311. (Dan) 2016-09-21 - 23000 - Dan Guerra-This unit already has ball valves and flush valves on it that work, so we flush out a.c. coil real good and now the Temp. reading is 50 to 51. - Dan Guerra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-09-19 | 176753 | RFMT-131578 | Please replace ball valve and flush valves in University Towers room 611. (Dan) | 2016-09-21 - 23000 - Dan Guerra-This unit already has ball valves and flush valves, so we flushed a.c. coil out real good and now the Temp. reading is 54 to 55. Note- The upper ball valve will need to be replaced because it leaks when in the off position. - Dan Guerra | Please replace ball valve and flush valves in University Towers room 611. (Dan) 2016-09-21 - 23000 - Dan Guerra-This unit already has ball valves and flush valves, so we flushed a.c. coil out real good and now the Temp. reading is 54 to 55. Note- The upper ball valve will need to be replaced because it leaks when in the off position. - Dan Guerra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-09-19 | 176754 | RFMT-131577 | !! Water leaking from air conditioning unit Attachment(s) 4NO2D07 | 2016-09-20 - 18010 - Thomas Zambrano-cleaned out pan - Thomas Zambrano | !! Water leaking from air conditioning unit Attachment(s) 4NO2D07 2016-09-20 - 18010 - Thomas Zambrano-cleaned out pan - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-19 | 176760 | RFMT-131571 | res life / Thor: Please check operation of elevator penthouse a/c | 2016-09-19 - 18010 - Thor Millsaps-Disconnect for air handler in penthouse was off. Switched disconnect back on and a/c came on in cooling. Checked all components on condenser and air handler. System running normally. Removed portable ac units from penthouse. - Thor Millsaps | res life / Thor: Please check operation of elevator penthouse a/c 2016-09-19 - 18010 - Thor Millsaps-Disconnect for air handler in penthouse was off. Switched disconnect back on and a/c came on in cooling. Checked all components on condenser and air handler. System running normally. Removed portable ac units from penthouse. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-19 | 234829 | POLY-113370 | !! AC not working!!! Filter has been changed and temoerature has been set in required range, but unit is not cooling house and is blowing hot air. 4NK4LFJ | NA | !! AC not working!!! Filter has been changed and temoerature has been set in required range, but unit is not cooling house and is blowing hot air. 4NK4LFJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-19 | 234860 | POLY-113339 | 9/23 - STEVE - Jesse said you were going to take care of this work order from 9/19/16, so I am forwarding it to you, so you have it to post your time on. Thanks, Gayle There is a water leak located in room 142A at Chandler Innovation Center. Please investigate and make repairs. Image of the leak . . . | 2016-09-23 - 23000 - Jesse Deanda-9/19 - Jesse called Steve Clark with the HVAC shop, and Steve said he would take care of it. - Gayle Swenson | 9/23 - STEVE - Jesse said you were going to take care of this work order from 9/19/16, so I am forwarding it to you, so you have it to post your time on. Thanks, Gayle There is a water leak located in room 142A at Chandler Innovation Center. Please investigate and make repairs. Image of the leak . . . 2016-09-23 - 23000 - Jesse Deanda-9/19 - Jesse called Steve Clark with the HVAC shop, and Steve said he would take care of it. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-20 | 60879 | TMPE-189278 | MWO: BT TO HVAC - LOOKS LIKE THE LEAK IS COMING FROM THE AC SUPPLY LINE. ***ORIGINAL REQUEST***!! Repeat Request. We have a leak dripping through a light fixture in the hallway on the second floor of Interdisciplinary Awing just outside the A210 door. It is big enough that it has left a larg. . . | 2016-09-20 - 18010 - CALLED TO JOHN H. - Monica Moraga; 2016-09-21 - 18010 - Thomas Gibble-cleared drain line - Thomas Gibble; 2016-09-21 - 18010 - Gail Jackson-cleared drain line - Thomas Gibble | MWO: BT TO HVAC - LOOKS LIKE THE LEAK IS COMING FROM THE AC SUPPLY LINE. ***ORIGINAL REQUEST***!! Repeat Request. We have a leak dripping through a light fixture in the hallway on the second floor of Interdisciplinary Awing just outside the A210 door. It is big enough that it has left a larg. . . 2016-09-20 - 18010 - CALLED TO JOHN H. - Monica Moraga; 2016-09-21 - 18010 - Thomas Gibble-cleared drain line - Thomas Gibble; 2016-09-21 - 18010 - Gail Jackson-cleared drain line - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-20 | 60909 | TMPE-189248 | SWO: MU - 87 Please check the motor for Hot Water Pump #2, Y6150. The starter is energized, but the motor doesn't run. 42AI0GO | 2016-10-12 - 23100 - Derek Gittings-replace motor, aligned, and completed - Melanie Lamm | SWO: MU - 87 Please check the motor for Hot Water Pump #2, Y6150. The starter is energized, but the motor doesn't run. 42AI0GO 2016-10-12 - 23100 - Derek Gittings-replace motor, aligned, and completed - Melanie Lamm | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-20 | 60925 | TMPE-189232 | MWO CNTRPT 310-10 Repeat Request. The AC unit in conference room 310-10 makes a loud buzzing noise when it is running. It makes it difficult for people to hear when someone is presenting. Can someone take a look at the unit and see if this noise is normal? Thank you! 4MO5454 | 2016-09-30 - 18010 - Roque Garcia-Found noise coming from Shattering contactor on 9/28/2016 2 hours for this date and returned on 9/30/2016 4 hours for this date replaced shattering contactor and its working like new. - Roque Garcia | MWO CNTRPT 310-10 Repeat Request. The AC unit in conference room 310-10 makes a loud buzzing noise when it is running. It makes it difficult for people to hear when someone is presenting. Can someone take a look at the unit and see if this noise is normal? Thank you! 4MO5454 2016-09-30 - 18010 - Roque Garcia-Found noise coming from Shattering contactor on 9/28/2016 2 hours for this date and returned on 9/30/2016 4 hours for this date replaced shattering contactor and its working like new. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-20 | 60934 | TMPE-189223 | MWO: SOCCER Repeat Request. The AC is out again in the Locker Room at the Soccer Facility. I've spoken with John Howell and he wanted another work order opened. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF | 2016-09-20 - 18290 - Called to John Howell - Jemina Kilma; 2016-09-26 - 18290 - Roque Garcia-Replaced the delta actuator and made sure it was working properly. Insulated the chilled water pipe.I called and spoke with Bonnie and Eric to update them about the problem and the parts needed to repair. Also advise them it wasn't the chiller causing the problem. - Roque Garcia | MWO: SOCCER Repeat Request. The AC is out again in the Locker Room at the Soccer Facility. I've spoken with John Howell and he wanted another work order opened. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF 2016-09-20 - 18290 - Called to John Howell - Jemina Kilma; 2016-09-26 - 18290 - Roque Garcia-Replaced the delta actuator and made sure it was working properly. Insulated the chilled water pipe.I called and spoke with Bonnie and Eric to update them about the problem and the parts needed to repair. Also advise them it wasn't the chiller causing the problem. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-09-20 | 60963 | TMPE-189194 | have Ingersoll Rand check out unit and find out why we are getting a motor fault | NA | have Ingersoll Rand check out unit and find out why we are getting a motor fault NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-20 | 176664 | RFMT-131667 | !! Air conditioning is either freezing or off. The temperature dial will not turn warm. 4NNKO9B | 2016-09-26 - 18010 - Casey Faultner-Replaced bad thermostat with a new one. - Casey Faultner | !! Air conditioning is either freezing or off. The temperature dial will not turn warm. 4NNKO9B 2016-09-26 - 18010 - Casey Faultner-Replaced bad thermostat with a new one. - Casey Faultner | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-20 | 176668 | RFMT-131663 | !! The air conditioning has stopped working for my room. It runs but it does not blow cold air or maintain the temperature the thermostat is set on. The temperature continues to rise and is currently at 78 degrees. 4NJ4JHO | 2016-09-21 - 18010 - Thor Millsaps-Replaced 1/4 HP 825 RPM condenser fan motor, 7.5 mfd capacitor. System up and running. - Thor Millsaps | !! The air conditioning has stopped working for my room. It runs but it does not blow cold air or maintain the temperature the thermostat is set on. The temperature continues to rise and is currently at 78 degrees. 4NJ4JHO 2016-09-21 - 18010 - Thor Millsaps-Replaced 1/4 HP 825 RPM condenser fan motor, 7.5 mfd capacitor. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-20 | 176694 | RFMT-131637 | Air conditioner does not work 4NN8N7B | 2016-09-21 - 18010 - John Romero-Checked out unit. Remote has new battery and is working but the unit isn't responding will need to send to Simon to look at. - John Romero | Air conditioner does not work 4NN8N7B 2016-09-21 - 18010 - John Romero-Checked out unit. Remote has new battery and is working but the unit isn't responding will need to send to Simon to look at. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-20 | 176702 | RFMT-131629 | Hayden South - 139: The air handler is not working in Room 139 of Hayden South. | 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr; 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr; 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr | Hayden South - 139: The air handler is not working in Room 139 of Hayden South. 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr; 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr; 2016-09-20 - 18010 - Salvatore Marasco Jr-Replaced burned out motor (HC/10)D-1144,and cleaned blower and housing. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-20 | 213823 | RACC-114787 | !! The Air Conditioner does not work on rooms A & B; however, it does work for room C & D 4NEI18D | NA | !! The Air Conditioner does not work on rooms A & B; however, it does work for room C & D 4NEI18D NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 60683 | TMPE-189474 | MWO Interdisciplinary A 210 area: !! Problem with air flow in A210 area, specifically in A210A, A210B1 and A210C2, which are all connected to the same air handler. Some work was done to this air handler in relation to a water leak this morning (please refer to WO#189277 and 189278). Now the air f. . . | 2016-09-22 - 18010 - Emailed to HVAC, dispatched to Brian Qualls (FF) - Francesca Fernandez; 2016-09-23 - 18010 - Thomas Gibble-we found return air dampers closed. we open them up and too much air was coming out. we an closed the dampers half way. they are happy with here. - Thomas Gibble; 2016-09-23 - 18010 - Gail Jackson-we found return air dampers closed. we open them up and too much air was coming out. we an closed the dampers half way. they are happy with here. - Thomas Gibble | MWO Interdisciplinary A 210 area: !! Problem with air flow in A210 area, specifically in A210A, A210B1 and A210C2, which are all connected to the same air handler. Some work was done to this air handler in relation to a water leak this morning (please refer to WO#189277 and 189278). Now the air f. . . 2016-09-22 - 18010 - Emailed to HVAC, dispatched to Brian Qualls (FF) - Francesca Fernandez; 2016-09-23 - 18010 - Thomas Gibble-we found return air dampers closed. we open them up and too much air was coming out. we an closed the dampers half way. they are happy with here. - Thomas Gibble; 2016-09-23 - 18010 - Gail Jackson-we found return air dampers closed. we open them up and too much air was coming out. we an closed the dampers half way. they are happy with here. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-21 | 60689 | TMPE-189468 | MWO: UCENT B - 105: EMS TO HVAC - UNIT NEEDS FREON. ***ORIGINAL REQUEST*** FYI, please see about the temperature in our suite. It was really warm in our back area a week or so ago and they said the Freon was low. Can someone please check this? | 2016-09-21 - 18290 - CALLED TO JOHN H. - Monica Moraga; 2016-09-22 - 18290 - Reported to job site approximately 525pm. The office staff needed to close the doors by 645. Due to lack of repair time, I installed a portable a/c unit to cool the servers for the night. I briefly looked at the two units in the ceiling and determined that they were both putting out warm air. Unit closest to the server room was short cycling. Currently, I have two motors out of two units in Wilson Hall and I am scheduled off on Friday. I have to put those back together and then address the server room and I will communicate that to the customer. Also, the units in that room were "starving for air" due to the pleated filters being dirty. One of the filters was dated June 2016. I recommend a loose fiber filter for these units. Pleated filters on these units will reduce the life of the unit. I was informed that the office suites had their locks changed because ASU staff were in office suites without prior permission. Also, cameras were installed for that reason. I also did not have badge access to University Center B main building. I had to rely on the kindness of employees entering/leaving the building to let me in for repair. Every effort is being made to complete all jobs in a timely manner. Thank you for your cooperation. - Jennifer Moyer; 2016-09-22 - 18290 - There is no customer contact information on this work order. I will research the original requestor on TMA and contact them. - Jennifer Moyer; 2016-09-22 - 18290 - 9/21/2016 2 OT 5:15pm-7:15pm Jennifer Moyer - UCENT B University Center Bldg B/ Set up portable to cool servers. - Kerri Perkins; 2016-09-22 - 18290 - 9/21/2016 .25 CE 5pm-5:15pm Brian Qualls - UCENT B Univ Center B - Stayed to give Jennifer Moyer info. on job. - Kerri Perkins; 2016-09-22 - 18290 - Jennifer Moyer-The coil was plugged. Drained and flushed coil. - Jennifer Moyer; 2016-09-22 - 18290 - Zhi Yu-The coil was plugged. Drained and flushed coil. - Jennifer Moyer; 2016-10-12 - 18290 - Brian Qualls-.38 credited as per payroll - reentered as .25 CES - Jeri Zappanti | MWO: UCENT B - 105: EMS TO HVAC - UNIT NEEDS FREON. ***ORIGINAL REQUEST*** FYI, please see about the temperature in our suite. It was really warm in our back area a week or so ago and they said the Freon was low. Can someone please check this? 2016-09-21 - 18290 - CALLED TO JOHN H. - Monica Moraga; 2016-09-22 - 18290 - Reported to job site approximately 525pm. The office staff needed to close the doors by 645. Due to lack of repair time, I installed a portable a/c unit to cool the servers for the night. I briefly looked at the two units in the ceiling and determined that they were both putting out warm air. Unit closest to the server room was short cycling. Currently, I have two motors out of two units in Wilson Hall and I am scheduled off on Friday. I have to put those back together and then address the server room and I will communicate that to the customer. Also, the units in that room were "starving for air" due to the pleated filters being dirty. One of the filters was dated June 2016. I recommend a loose fiber filter for these units. Pleated filters on these units will reduce the life of the unit. I was informed that the office suites had their locks changed because ASU staff were in office suites without prior permission. Also, cameras were installed for that reason. I also did not have badge access to University Center B main building. I had to rely on the kindness of employees entering/leaving the building to let me in for repair. Every effort is being made to complete all jobs in a timely manner. Thank you for your cooperation. - Jennifer Moyer; 2016-09-22 - 18290 - There is no customer contact information on this work order. I will research the original requestor on TMA and contact them. - Jennifer Moyer; 2016-09-22 - 18290 - 9/21/2016 2 OT 5:15pm-7:15pm Jennifer Moyer - UCENT B University Center Bldg B/ Set up portable to cool servers. - Kerri Perkins; 2016-09-22 - 18290 - 9/21/2016 .25 CE 5pm-5:15pm Brian Qualls - UCENT B Univ Center B - Stayed to give Jennifer Moyer info. on job. - Kerri Perkins; 2016-09-22 - 18290 - Jennifer Moyer-The coil was plugged. Drained and flushed coil. - Jennifer Moyer; 2016-09-22 - 18290 - Zhi Yu-The coil was plugged. Drained and flushed coil. - Jennifer Moyer; 2016-10-12 - 18290 - Brian Qualls-.38 credited as per payroll - reentered as .25 CES - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2016-09-21 | 60713 | TMPE-189444 | SWO: Karsten CALLED TO BOB. DEREK CRAWFORD CALLED AND SAID THE ROOFER WAS THERE TO MAKE REPAIRS BUT THAT IT'S STILL LEAKING AND THEY HAVE AN EVENT TODAY 09/27/16 AT 3:00PM. MM There is a leak in the roof at the Karsten Golf Club House | 2016-09-26 - 13120 - Christopher Dovales-repairing cracks on roof membrane - Christopher Dovales; 2016-09-27 - 13120 - Christopher Dovales-repaired all cracks on roof membrane in this area completed - Christopher Dovales; 2016-09-27 - 13120 - CALLED TO BOB. DERRICK CRAWFORD CALLED AND SAID THE ROOFER WAS THERE TO MAKE REPAIRS BUT THAT IT'S STILL LEAKING AND THEY HAVE AN EVENT TODAY 09/27/16 AT 3:00PM. MM - Monica Moraga; 2016-09-28 - 13120 - Christopher Dovales-checking on ceiling leak AC was leak condensate line was plugged cleared - Christopher Dovales | SWO: Karsten CALLED TO BOB. DEREK CRAWFORD CALLED AND SAID THE ROOFER WAS THERE TO MAKE REPAIRS BUT THAT IT'S STILL LEAKING AND THEY HAVE AN EVENT TODAY 09/27/16 AT 3:00PM. MM There is a leak in the roof at the Karsten Golf Club House 2016-09-26 - 13120 - Christopher Dovales-repairing cracks on roof membrane - Christopher Dovales; 2016-09-27 - 13120 - Christopher Dovales-repaired all cracks on roof membrane in this area completed - Christopher Dovales; 2016-09-27 - 13120 - CALLED TO BOB. DERRICK CRAWFORD CALLED AND SAID THE ROOFER WAS THERE TO MAKE REPAIRS BUT THAT IT'S STILL LEAKING AND THEY HAVE AN EVENT TODAY 09/27/16 AT 3:00PM. MM - Monica Moraga; 2016-09-28 - 13120 - Christopher Dovales-checking on ceiling leak AC was leak condensate line was plugged cleared - Christopher Dovales | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-21 | 60719 | TMPE-189438 | MWO: West Hall - 225 A/C unit is leaking and dripping water | 2016-09-21 - 18010 - Carlos Felix-Transferred to HVAC minor A/C drip. - Carlos Felix | MWO: West Hall - 225 A/C unit is leaking and dripping water 2016-09-21 - 18010 - Carlos Felix-Transferred to HVAC minor A/C drip. - Carlos Felix | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 60756 | TMPE-189401 | MWO: UCENT B STE 301 Please close the vent in the area that's closest to the restroom. | 2016-09-23 - 18010 - Jeffery Armstrong-completed talked to lady also tried to divert the air flow from her desk. - Jeffery Armstrong | MWO: UCENT B STE 301 Please close the vent in the area that's closest to the restroom. 2016-09-23 - 18010 - Jeffery Armstrong-completed talked to lady also tried to divert the air flow from her desk. - Jeffery Armstrong | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 60765 | TMPE-189392 | MWO:ZHI, This fan coil has the chilled water valved off because it has a severe water leak. See if you can determine if it is repairable. If not, please get me pictures, model numbers, voltage and measurements so we can get a replacement unit. Thanks! HVAC added to check out individual space, EMS. . . | 2016-09-26 - 18290 - Remove unit for repair. Motor on order. - Jennifer Moyer | MWO:ZHI, This fan coil has the chilled water valved off because it has a severe water leak. See if you can determine if it is repairable. If not, please get me pictures, model numbers, voltage and measurements so we can get a replacement unit. Thanks! HVAC added to check out individual space, EMS. . . 2016-09-26 - 18290 - Remove unit for repair. Motor on order. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2016-09-21 | 60836 | TMPE-189321 | MWO: ASU Art Museum Conservation Studio has two AC units. They are both split system units that are not connected to the building's air handlers (#5 and #6). The units are not keeping the room cool enough for its conservation purposes. Temperatures have been hovering around 75 degrees. They shoul. . . | 2016-09-23 - 18010 - Thomas Gibble-Clean filters, check unit operation with remote, informed customer doors to conservation room will need to be closed , Mitsubishi mini split with 2 evaps. Condensing unit on balcony 30 ft plus high, no access through bldg. A bucket truck will be needed, secure area must contact security before work. - Gail Jackson; 2016-09-23 - 18010 - Gail Jackson-Clean filters, check unit operation with remote, informed customer doors to conservation room will need to be closed , Mitsubishi mini split with 2 evaps. Condensing unit on balcony 30 ft plus high, no access through bldg. A bucket truck will be needed, secure area must contact security before work. Searched entire building for access to unit none found. - Gail Jackson; 2016-10-20 - 18010 - Thomas Gibble-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson; 2016-10-20 - 18010 - Gail Jackson-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson; 2016-10-20 - 18010 - Gail Jackson-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson | MWO: ASU Art Museum Conservation Studio has two AC units. They are both split system units that are not connected to the building's air handlers (#5 and #6). The units are not keeping the room cool enough for its conservation purposes. Temperatures have been hovering around 75 degrees. They shoul. . . 2016-09-23 - 18010 - Thomas Gibble-Clean filters, check unit operation with remote, informed customer doors to conservation room will need to be closed , Mitsubishi mini split with 2 evaps. Condensing unit on balcony 30 ft plus high, no access through bldg. A bucket truck will be needed, secure area must contact security before work. - Gail Jackson; 2016-09-23 - 18010 - Gail Jackson-Clean filters, check unit operation with remote, informed customer doors to conservation room will need to be closed , Mitsubishi mini split with 2 evaps. Condensing unit on balcony 30 ft plus high, no access through bldg. A bucket truck will be needed, secure area must contact security before work. Searched entire building for access to unit none found. - Gail Jackson; 2016-10-20 - 18010 - Thomas Gibble-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson; 2016-10-20 - 18010 - Gail Jackson-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson; 2016-10-20 - 18010 - Gail Jackson-Had Shawn the Locksmith re bolt lock for window access to balcony where exhaust fan and Mini split condenser is located. Units have were installed 2 years ago. Replaced belt and cleaned coil. Notified Steve (bldg techs), Mike(Nelson Security) and Billy (PMS) about changes. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2016-09-21 | 60868 | TMPE-189289 | MWO COOR 1st Flr **TRANSFER** BT to HVAC I plugged in the drinking fountain on the right side but the compressor still did not turn on. The drinking fountain on the left was already plugged in but the compressor did not turn on either. The water on both drinking fountains were luke warm. The. . . | 2016-09-26 - 23080 - Robert Dauscher-Checked both drinking fountains. found T-stats bad(not calling when they should be). Need to replace both units t-stats. Brian Q to order parts. Gave Part #'s and prices on 9-26-2016 at about 9:45am. parts not in stock had to have shipped in from other areas of the state. Need to have Plumbing added to call. both P-traps in poor condition. May fail on removal. Please have plumbing pick up 2 new traps and set time for next Sunday to pull units and repair. - Robert Dauscher | MWO COOR 1st Flr **TRANSFER** BT to HVAC I plugged in the drinking fountain on the right side but the compressor still did not turn on. The drinking fountain on the left was already plugged in but the compressor did not turn on either. The water on both drinking fountains were luke warm. The. . . 2016-09-26 - 23080 - Robert Dauscher-Checked both drinking fountains. found T-stats bad(not calling when they should be). Need to replace both units t-stats. Brian Q to order parts. Gave Part #'s and prices on 9-26-2016 at about 9:45am. parts not in stock had to have shipped in from other areas of the state. Need to have Plumbing added to call. both P-traps in poor condition. May fail on removal. Please have plumbing pick up 2 new traps and set time for next Sunday to pull units and repair. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-21 | 60876 | TMPE-189281 | The sheave is worn and causing belt failure. The sheave size is 3/4"x BK-40 (single belt). | 2016-10-31 - 18010 - Thomas Gibble-find ex-fan and took size of it. ordered a sheave for the motor from grainger. - Thomas Gibble; 2016-11-02 - 18010 - Thomas Gibble-put on the new sheave on the ex-fan - Thomas Gibble | The sheave is worn and causing belt failure. The sheave size is 3/4"x BK-40 (single belt). 2016-10-31 - 18010 - Thomas Gibble-find ex-fan and took size of it. ordered a sheave for the motor from grainger. - Thomas Gibble; 2016-11-02 - 18010 - Thomas Gibble-put on the new sheave on the ex-fan - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-21 | 176584 | RFMT-131747 | !! Our air conditioner is not putting out cold air. Since it is so hot outside, the sooner this gets looked at the better. Thank you. 4NKM6NL | 2016-09-22 - 18010 - David Cates-AC was frozen up, turned off unit and spoke with Thor about issue. He had to recharge the unit. Please create a TMA for him to account for his time and materials used. - David Cates | !! Our air conditioner is not putting out cold air. Since it is so hot outside, the sooner this gets looked at the better. Thank you. 4NKM6NL 2016-09-22 - 18010 - David Cates-AC was frozen up, turned off unit and spoke with Thor about issue. He had to recharge the unit. Please create a TMA for him to account for his time and materials used. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 176594 | RFMT-131737 | RL HVAC - Please check out the A/C unit in this lounge. McClintock 203 4NEI9DN | 2016-09-22 - 18010 - Simon Fernandez-a/c unit not running,reset unit,unit on but not cooling.rechecked unit found system flat,found leak,repaired,recharged unit unit okay - Simon Fernandez | RL HVAC - Please check out the A/C unit in this lounge. McClintock 203 4NEI9DN 2016-09-22 - 18010 - Simon Fernandez-a/c unit not running,reset unit,unit on but not cooling.rechecked unit found system flat,found leak,repaired,recharged unit unit okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 176619 | RFMT-131712 | !! The AC Unit panel in the sink area between rooms 314 and 316 is leaking water. There was a large puddle of water on the counter this morning and water is dripping constantly from it. 4NFM5E5 | 2016-09-21 - 18010 - David Cates-Shop vacced out AC condensation drain, and requested for Olympus to come and clean the area. - David Cates; 2016-09-21 - 18010 - Olympus rqst. # 229034 - Gregory Stetka; 2016-09-21 - 18010 - Also copied Res. Life HVAC techs to follow up to insure no further repairs needed. - Gregory Stetka | !! The AC Unit panel in the sink area between rooms 314 and 316 is leaking water. There was a large puddle of water on the counter this morning and water is dripping constantly from it. 4NFM5E5 2016-09-21 - 18010 - David Cates-Shop vacced out AC condensation drain, and requested for Olympus to come and clean the area. - David Cates; 2016-09-21 - 18010 - Olympus rqst. # 229034 - Gregory Stetka; 2016-09-21 - 18010 - Also copied Res. Life HVAC techs to follow up to insure no further repairs needed. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-21 | 234739 | POLY-113460 | !! A/C unit is leaking water. 4NFAFM4 | NA | !! A/C unit is leaking water. 4NFAFM4 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 234769 | POLY-113430 | START UP A/C EQUIPMENT THAT WAS SHUT DOWN DUE TO POWER SUPPLY ISSUES 4O216EO | 2016-10-06 - 18010 - Suresh Nair-9/21 - Suresh replaced 5 30-amp fuses, and restarted all units. - Gayle Swenson | START UP A/C EQUIPMENT THAT WAS SHUT DOWN DUE TO POWER SUPPLY ISSUES 4O216EO 2016-10-06 - 18010 - Suresh Nair-9/21 - Suresh replaced 5 30-amp fuses, and restarted all units. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 234782 | POLY-113417 | Repeat Request. CALL AHEAD I have a dog 520-403-2797 or 928-259-3822 The ac unit is not blowing cold and the fan is always running. Please call Sarah 520-403-2797 or Brian 928-259-3822 Thank you 4N1ANH0 | NA | Repeat Request. CALL AHEAD I have a dog 520-403-2797 or 928-259-3822 The ac unit is not blowing cold and the fan is always running. Please call Sarah 520-403-2797 or Brian 928-259-3822 Thank you 4N1ANH0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-21 | 256335 | DTPC-112203 | Troubleshoot Unit 1-5 as only one condenser fan motor is running. | 2016-09-21 - 18010 - James Hermann-troubleshoot unit. - James Hermann; 2017-01-23 - 18010 - Reassigned from James Herman to Ralph Lemons. pb - Patricia Best; 2017-01-23 - 18010 - Ralph Lemons-Work has been completed and unit is running at this time. - Ralph Lemons | Troubleshoot Unit 1-5 as only one condenser fan motor is running. 2016-09-21 - 18010 - James Hermann-troubleshoot unit. - James Hermann; 2017-01-23 - 18010 - Reassigned from James Herman to Ralph Lemons. pb - Patricia Best; 2017-01-23 - 18010 - Ralph Lemons-Work has been completed and unit is running at this time. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-22 | 60427 | TMPE-189730 | MWO: Centerpoint - 104-03: !! All , The 2 units not working in OKED space are labeled on the bottom of the units, they are , HP17 and HP12. I have attached the omega report with more info as needed. We need these repaired for occupants. Attachment(s) 42BIGC1 | 2016-09-23 - 18290 - Called to Bob in EMS - Jeri Zappanti; 2017-02-17 - 18290 - Mitchell Andrews-replaced all three motors that were grounded out test and balance can now be preformed - Mitchell Andrews | MWO: Centerpoint - 104-03: !! All , The 2 units not working in OKED space are labeled on the bottom of the units, they are , HP17 and HP12. I have attached the omega report with more info as needed. We need these repaired for occupants. Attachment(s) 42BIGC1 2016-09-23 - 18290 - Called to Bob in EMS - Jeri Zappanti; 2017-02-17 - 18290 - Mitchell Andrews-replaced all three motors that were grounded out test and balance can now be preformed - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 60511 | TMPE-189646 | MWO: ASU PD 107U1 The a/c unit is leaking pretty good. Please send to HVAC. | 2016-09-22 - 18010 - CALLED TO JOHN H. - Monica Moraga; 2016-09-27 - 18010 - Oner Munoz-Checked system out, found faulty condensation pump, ordered a new pump. - Oner Munoz; 2016-09-27 - 18010 - Oner Munoz-Installed new condensation pump. - Oner Munoz | MWO: ASU PD 107U1 The a/c unit is leaking pretty good. Please send to HVAC. 2016-09-22 - 18010 - CALLED TO JOHN H. - Monica Moraga; 2016-09-27 - 18010 - Oner Munoz-Checked system out, found faulty condensation pump, ordered a new pump. - Oner Munoz; 2016-09-27 - 18010 - Oner Munoz-Installed new condensation pump. - Oner Munoz | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-22 | 60539 | TMPE-189618 | SWO: MU - Pitchforks: Please setup a work order to have a Painter come to Pitchforks located in the MU on the first floor There is a AC vent that needs wiped down and painted. The vent is on the ceiling in front of the Middle Eastern station. It is black in color See Jim Emmons for detail | NA | SWO: MU - Pitchforks: Please setup a work order to have a Painter come to Pitchforks located in the MU on the first floor There is a AC vent that needs wiped down and painted. The vent is on the ceiling in front of the Middle Eastern station. It is black in color See Jim Emmons for detail NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 60592 | TMPE-189565 | MWO PSG 123 The air handler is "raining" onto boxes and such. About a gallon of water currently on the floor. | 2016-09-22 - 18050 - Called out to John Howell - Amanda Thomas; 2016-09-23 - 18050 - Zhi Yu-condensation line plug-up. We vacuum and blow out both A/H located in the storage ware house. couple ceiling tile damage and water on floor. Advise client to call Olympus for clean-up - Zhi Yu; 2016-09-23 - 18050 - Jennifer Moyer-condensation line plug-up. We vacuum and blow out both A/H located in the storage ware house. couple ceiling tile damage and water on floor. Advise client to call Olympus for clean-up - Zhi Yu | MWO PSG 123 The air handler is "raining" onto boxes and such. About a gallon of water currently on the floor. 2016-09-22 - 18050 - Called out to John Howell - Amanda Thomas; 2016-09-23 - 18050 - Zhi Yu-condensation line plug-up. We vacuum and blow out both A/H located in the storage ware house. couple ceiling tile damage and water on floor. Advise client to call Olympus for clean-up - Zhi Yu; 2016-09-23 - 18050 - Jennifer Moyer-condensation line plug-up. We vacuum and blow out both A/H located in the storage ware house. couple ceiling tile damage and water on floor. Advise client to call Olympus for clean-up - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 61299 | TMPE-188858 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-22 | 61753 | TMPE-188404 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-22 | 61761 | TMPE-188396 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-22 | 61762 | TMPE-188395 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-22 | 61765 | TMPE-188392 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-22 | 176536 | RFMT-131795 | Simon / Thor - this has been a re-occurring call back for units tripped reset switch. Greg !! AC broke a few days ago, was fixed, and broke again 4NOL3A7 | 2016-09-23 - 18010 - Simon Fernandez-checked a/c unit ,found bad motor. replaced motor and run cap. - Simon Fernandez | Simon / Thor - this has been a re-occurring call back for units tripped reset switch. Greg !! AC broke a few days ago, was fixed, and broke again 4NOL3A7 2016-09-23 - 18010 - Simon Fernandez-checked a/c unit ,found bad motor. replaced motor and run cap. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-09-22 | 176578 | RFMT-131753 | RES LIFE / Thor: Corridor ceiling a/c unit by elevator lobby. Please inspect and repair Belimo valve | 2016-09-27 - 18010 - Thor Millsaps-Repaired chilled water valve. Reattached valve body to base and tightened wing nut. System up and running. - Thor Millsaps | RES LIFE / Thor: Corridor ceiling a/c unit by elevator lobby. Please inspect and repair Belimo valve 2016-09-27 - 18010 - Thor Millsaps-Repaired chilled water valve. Reattached valve body to base and tightened wing nut. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-09-22 | 176587 | RFMT-131744 | !! Leakage. in the bathroom. Leakage is really bad. Need urgent action 4NKMBEK | 2016-09-22 - 23000 - David Cates-Cleared AC condensation drain and drained water from panel. - David Cates | !! Leakage. in the bathroom. Leakage is really bad. Need urgent action 4NKMBEK 2016-09-22 - 23000 - David Cates-Cleared AC condensation drain and drained water from panel. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 176596 | RFMT-131735 | !! Repeat Request. AC low and medium do not work. When we turn it on in high, it starts leaking. Thanks you! Contact Name: Contact Phone Number: 9186888341 Contact Email: 4NDK207 | 2016-09-23 - 18010 - Simon Fernandez-checked a/c unit found bad pan. removed and replaced pan. checked motor 2speed motor has hi--med--,unit checks okay - Simon Fernandez | !! Repeat Request. AC low and medium do not work. When we turn it on in high, it starts leaking. Thanks you! Contact Name: Contact Phone Number: 9186888341 Contact Email: 4NDK207 2016-09-23 - 18010 - Simon Fernandez-checked a/c unit found bad pan. removed and replaced pan. checked motor 2speed motor has hi--med--,unit checks okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-22 | 215849 | RACC-112761 | !! Water leak from AC intake. Water pooling on floor and baseboard. Attachment(s) 4NC764L | NA | !! Water leak from AC intake. Water pooling on floor and baseboard. Attachment(s) 4NC764L NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 234712 | POLY-113487 | !! Air conditioner has not worked for 2 days. 4NMLBEI | NA | !! Air conditioner has not worked for 2 days. 4NMLBEI NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-22 | 234729 | POLY-113470 | !! AC is making really loud high pitched noise, sounds like it is broken, can't leave on because noise is so loud 4NIL357 | NA | !! AC is making really loud high pitched noise, sounds like it is broken, can't leave on because noise is so loud 4NIL357 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-23 | 56062 | TMPE-194095 | Naumann Hobbs located unit, inspected and found rear tire flat, valve stem broken. Removed tire and replaced valve stem. Reinstalled tire. Total: 35.44 | NA | Naumann Hobbs located unit, inspected and found rear tire flat, valve stem broken. Removed tire and replaced valve stem. Reinstalled tire. Total: 35.44 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2
2016-09-23 | 60375 | TMPE-189782 | MWO LSA 279 !! This room has a dedicated AC unit supply and it is apparently not working. Please open a WO to have this addressed accordingly. There is an active experiment planned to start late next week. Thank you. 4NLGBH4 | 2016-09-27 - 18290 - Roque Garcia-Freon level was low but not flat. Searched for freon leak and no leak was found. Added R22 10 lbs unit is a high temp and it started working to specs. - Roque Garcia | MWO LSA 279 !! This room has a dedicated AC unit supply and it is apparently not working. Please open a WO to have this addressed accordingly. There is an active experiment planned to start late next week. Thank you. 4NLGBH4 2016-09-27 - 18290 - Roque Garcia-Freon level was low but not flat. Searched for freon leak and no leak was found. Added R22 10 lbs unit is a high temp and it started working to specs. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-23 | 176475 | RFMT-131856 | ASUHC-Agent: Linda Herdan Description: A/C is not working, reported two days ago, unit not coming on at all Who was dispatched: Joe Swan Time of dispatch: 18:56 | 2016-09-26 - 18010 - Joe Swan-No familiar with thermostat work fine. complete - Joe Swan | ASUHC-Agent: Linda Herdan Description: A/C is not working, reported two days ago, unit not coming on at all Who was dispatched: Joe Swan Time of dispatch: 18:56 2016-09-26 - 18010 - Joe Swan-No familiar with thermostat work fine. complete - Joe Swan | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-23 | 176481 | RFMT-131850 | Please enter order information / data in the results page of this work order for; HVAC unit evaporator fan motors for shelf stock for Adelphi I complex. Thank you. | 2016-09-27 - 18010 - Thor Millsaps-Work order is for ordering shelf stock at Adelphi I. - Thor Millsaps | Please enter order information / data in the results page of this work order for; HVAC unit evaporator fan motors for shelf stock for Adelphi I complex. Thank you. 2016-09-27 - 18010 - Thor Millsaps-Work order is for ordering shelf stock at Adelphi I. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176484 | RFMT-131847 | Please order all needed HVAC filters for the door to door program. Fill out HVAC filter order form and leave on Adelphi shop desk. Also record filter sizes and amounts in results page of this work order. Thank you. | 2016-09-26 - 18010 - David Cates-All Adelphi 2 filter sizes will be listed in other TMA results instead of splitting them in half. - David Cates; 2016-09-26 - 18010 - David listed filter sizes and amount for the entire complex in the other Adelphi II work order. - Gregory Stetka | Please order all needed HVAC filters for the door to door program. Fill out HVAC filter order form and leave on Adelphi shop desk. Also record filter sizes and amounts in results page of this work order. Thank you. 2016-09-26 - 18010 - David Cates-All Adelphi 2 filter sizes will be listed in other TMA results instead of splitting them in half. - David Cates; 2016-09-26 - 18010 - David listed filter sizes and amount for the entire complex in the other Adelphi II work order. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-23 | 176486 | RFMT-131845 | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 | 2016-09-23 - 18010 - Simon checked unit - I requested Olympus to extract and deodorize carpet. - Gregory Stetka; 2016-09-26 - 18010 - Simon Fernandez-checked a/c unit found condensate pan clogged.cleared clogged drain line for condensate pan. unit checked okay. - Simon Fernandez | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 2016-09-23 - 18010 - Simon checked unit - I requested Olympus to extract and deodorize carpet. - Gregory Stetka; 2016-09-26 - 18010 - Simon Fernandez-checked a/c unit found condensate pan clogged.cleared clogged drain line for condensate pan. unit checked okay. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176487 | RFMT-131844 | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 | 2016-09-27 - 18010 - Thor Millsaps-Cleared condensate drain line and cleaned condensate pan. Unit is now draining properly. - Thor Millsaps | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 2016-09-27 - 18010 - Thor Millsaps-Cleared condensate drain line and cleaned condensate pan. Unit is now draining properly. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176488 | RFMT-131843 | Joe this is for the work you did on 09/22/16 for Sonora 227 and 314 HVAC systems not working. Thank you. | 2016-09-23 - 18010 - Joe Swan-No A/C rooms 314 &amp; 227. tripped breaker in both rooms. - Joe Swan | Joe this is for the work you did on 09/22/16 for Sonora 227 and 314 HVAC systems not working. Thank you. 2016-09-23 - 18010 - Joe Swan-No A/C rooms 314 &amp; 227. tripped breaker in both rooms. - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176503 | RFMT-131828 | Simon / Thor - this has been a re-occurring call back for units tripped reset switch. Greg !! AC broke a few days ago, was fixed, and broke again 4NOL3A7 | 2016-09-23 - 18010 - Thor and Simon replace fan coil fan motor. - Gregory Stetka | Simon / Thor - this has been a re-occurring call back for units tripped reset switch. Greg !! AC broke a few days ago, was fixed, and broke again 4NOL3A7 2016-09-23 - 18010 - Thor and Simon replace fan coil fan motor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2016-09-23 | 176512 | RFMT-131819 | Please enter order information / data in the results page of this work order for; HVAC unit condensing fans motors for shelf stock for Adelphi I complex. Thank you. | 2016-09-27 - 18010 - Thor Millsaps-Work order is for ordering shelf stock. - Thor Millsaps | Please enter order information / data in the results page of this work order for; HVAC unit condensing fans motors for shelf stock for Adelphi I complex. Thank you. 2016-09-27 - 18010 - Thor Millsaps-Work order is for ordering shelf stock. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176520 | RFMT-131811 | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 | 2016-09-23 - 18010 - Salvatore Marasco Jr-Vacuumed out condensate drain line, requested A.C. techs. to look at unit to inspect it. - Salvatore Marasco Jr | the air conditioner is leaking & causing a huge puddle on our floor in our room. Contact Name: Contact Phone Number: 2098344505 Contact Email: drew_r23@yahoo.com 4O0CO38 2016-09-23 - 18010 - Salvatore Marasco Jr-Vacuumed out condensate drain line, requested A.C. techs. to look at unit to inspect it. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176522 | RFMT-131809 | !! Hello. My air conditioner/heater unit stopped working and I turned it off for a few days and it still won't turn on, so I need someone to please come look at it and hopefully fix it. There is only a buzzing sound when it's turned on, but the actual unit does not let out any type of air. 4NL46B4 | 2016-09-23 - 18010 - Salvatore Marasco Jr-Replaced blower motor with salvaged motor from Cholla. - Salvatore Marasco Jr | !! Hello. My air conditioner/heater unit stopped working and I turned it off for a few days and it still won't turn on, so I need someone to please come look at it and hopefully fix it. There is only a buzzing sound when it's turned on, but the actual unit does not let out any type of air. 4NL46B4 2016-09-23 - 18010 - Salvatore Marasco Jr-Replaced blower motor with salvaged motor from Cholla. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-23 | 176546 | RFMT-131785 | !! Our air conditioner is not putting out cold air. Since it is so hot outside, the sooner this gets looked at the better. Thank you. 4NKM6NL | 2016-09-23 - 18010 - Thor repaired unit to normal operation and will follow up on Monday to recheck vitals. - Gregory Stetka; 2016-09-27 - 18010 - Thor Millsaps-Finished defrosting unit and added 2 lbs. R-22. System up and running. - Thor Millsaps | !! Our air conditioner is not putting out cold air. Since it is so hot outside, the sooner this gets looked at the better. Thank you. 4NKM6NL 2016-09-23 - 18010 - Thor repaired unit to normal operation and will follow up on Monday to recheck vitals. - Gregory Stetka; 2016-09-27 - 18010 - Thor Millsaps-Finished defrosting unit and added 2 lbs. R-22. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-23 | 234672 | POLY-113527 | The stove in this unit is not hooked up. The oven works, but the burners do not. The closet door in bedroom number 2 (the second largest bedroom, it is the bedroom on its own side of the house) does not open or close smoothly The hallway bathroom lock does not lock (it is the bathroom next to . . . | NA | The stove in this unit is not hooked up. The oven works, but the burners do not. The closet door in bedroom number 2 (the second largest bedroom, it is the bedroom on its own side of the house) does not open or close smoothly The hallway bathroom lock does not lock (it is the bathroom next to . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-09-23 | 256240 | DTPC-112298 | Hot in IDF room 261C1 | 2016-09-26 - 18290 - Thomas Klein-Found unit was in alarm someone reset before I could see the code, ask them not to do that again. Checked unit. It was working properly when I left. - Thomas Klein | Hot in IDF room 261C1 2016-09-26 - 18290 - Thomas Klein-Found unit was in alarm someone reset before I could see the code, ask them not to do that again. Checked unit. It was working properly when I left. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-25 | 176433 | RFMT-131898 | !! My AC unit blows a bunch of dust and dead bugs all over my room every time I turn it on. I would like someone to come out and take a look at it to either clean it or replace the filter so it doesnt make a mess every time I turn the fan and AC on. Thank you so much 4O09EJ5 | 2016-09-26 - 18010 - Rene Arrieta-replace filter - Rene Arrieta | !! My AC unit blows a bunch of dust and dead bugs all over my room every time I turn it on. I would like someone to come out and take a look at it to either clean it or replace the filter so it doesnt make a mess every time I turn the fan and AC on. Thank you so much 4O09EJ5 2016-09-26 - 18010 - Rene Arrieta-replace filter - Rene Arrieta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-26 | 58755 | TMPE-191402 | Factory Motor Parts 88863829 C560 R80 Total: 72.41 | NA | Factory Motor Parts 88863829 C560 R80 Total: 72.41 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 58929 | TMPE-191228 | MWO: BAC-18 !! Life safety issue: The "Black Box" fiber optic switch unit in the Fire fiber optic switching cabinet is emitting a loud buzzing noise and the internal cooling fan or another component may be failing. Please evaluate ASAP. Also, the fire communications fiber optic switch cabinet fa. . . | 2016-09-26 - 18010 - Contacted Fire &amp; Safety - was advised Customer would need to contact UTO. Called/emailed customer to contact UTO. - Jemina Kilma | MWO: BAC-18 !! Life safety issue: The "Black Box" fiber optic switch unit in the Fire fiber optic switching cabinet is emitting a loud buzzing noise and the internal cooling fan or another component may be failing. Please evaluate ASAP. Also, the fire communications fiber optic switch cabinet fa. . . 2016-09-26 - 18010 - Contacted Fire &amp; Safety - was advised Customer would need to contact UTO. Called/emailed customer to contact UTO. - Jemina Kilma | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 58930 | TMPE-191227 | MWO: SUN ANGEL STADIUM I'm with ASU ROTC and we have a physical fitness test this Wednesday 09/28/16 on the track and we would like if the landscapers can wait until 7:00am to do their work because they kick up dust. | 2016-09-27 - 19000 - Emailed FACMAN to let them know that this would go to Athletics LO - Laura Oglesby; 2016-09-27 - 19000 - Contacted Mr. Haug and told him this needed to go to Athletics. he told me that FACMAN had contacted him to let him know that he needed to contact Athletics. Mr. Haug told me he had been in touch with Athletics and it has been taken care of for the 28th. - Ruben Lopez | MWO: SUN ANGEL STADIUM I'm with ASU ROTC and we have a physical fitness test this Wednesday 09/28/16 on the track and we would like if the landscapers can wait until 7:00am to do their work because they kick up dust. 2016-09-27 - 19000 - Emailed FACMAN to let them know that this would go to Athletics LO - Laura Oglesby; 2016-09-27 - 19000 - Contacted Mr. Haug and told him this needed to go to Athletics. he told me that FACMAN had contacted him to let him know that he needed to contact Athletics. Mr. Haug told me he had been in touch with Athletics and it has been taken care of for the 28th. - Ruben Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 58961 | TMPE-191196 | MWO: 084 W180 Transfer call to HVAC to change filters in AH#4. Need changed ASAP due to event this evening. EMS WO#191119, HVAC WO#191196. !! There is an excessive amount of air handler noise in Katzin Concert Hall. We have a concert tonight at 7:30. 42B21NB | 2016-09-26 - 18170 - Jose Mazon-filters change at HA. #4 EQ. room W245UI .music west bldg. job complete - Jose Mazon | MWO: 084 W180 Transfer call to HVAC to change filters in AH#4. Need changed ASAP due to event this evening. EMS WO#191119, HVAC WO#191196. !! There is an excessive amount of air handler noise in Katzin Concert Hall. We have a concert tonight at 7:30. 42B21NB 2016-09-26 - 18170 - Jose Mazon-filters change at HA. #4 EQ. room W245UI .music west bldg. job complete - Jose Mazon | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-26 | 58981 | TMPE-191176 | MWO: Heat is blowing into office area. No AC in office. 42AK1HG | 2016-09-29 - 18290 - Zhi Yu-Arrived the unit condenser fan motor seize up. We replaced 1/2 hp 208/230v motor and 12.5 mfd cap. We start the unit blower motor run very slow and high amp draw. we also replaced indoor blower motor 3/4hp and 15mfd cap. Work order 191510 and 191176 are duplicate. - Zhi Yu; 2016-09-29 - 18290 - Gail Jackson-Arrived the unit condenser fan motor seize up. We replaced 1/2 hp 208/230v motor and 12.5 mfd cap. We start the unit blower motor run very slow and high amp draw. we also replaced indoor blower motor 3/4hp and 15mfd cap. Work order 191510 and 191176 are duplicate. - Zhi Yu | MWO: Heat is blowing into office area. No AC in office. 42AK1HG 2016-09-29 - 18290 - Zhi Yu-Arrived the unit condenser fan motor seize up. We replaced 1/2 hp 208/230v motor and 12.5 mfd cap. We start the unit blower motor run very slow and high amp draw. we also replaced indoor blower motor 3/4hp and 15mfd cap. Work order 191510 and 191176 are duplicate. - Zhi Yu; 2016-09-29 - 18290 - Gail Jackson-Arrived the unit condenser fan motor seize up. We replaced 1/2 hp 208/230v motor and 12.5 mfd cap. We start the unit blower motor run very slow and high amp draw. we also replaced indoor blower motor 3/4hp and 15mfd cap. Work order 191510 and 191176 are duplicate. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 58987 | TMPE-191170 | MWO: COOR 3RD FL EQ RM A/H #8; condensation plugged; need to vacuum out 4 different compartments that are full of water. | 2016-09-30 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2016-09-30 - 18050 - Jose Lopez-air handler was full of water in all 5 rooms cause by plug condensate line,unplug line and vacuum water from compartments inform central plant unit was back on line working normal - Jose Lopez | MWO: COOR 3RD FL EQ RM A/H #8; condensation plugged; need to vacuum out 4 different compartments that are full of water. 2016-09-30 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2016-09-30 - 18050 - Jose Lopez-air handler was full of water in all 5 rooms cause by plug condensate line,unplug line and vacuum water from compartments inform central plant unit was back on line working normal - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 59084 | TMPE-191073 | MWO:ZHI, This fan coil has the chilled water valved off because it has a severe water leak. See if you can determine if it is repairable. If not, please get me pictures, model numbers, voltage and measurements so we can get a replacement unit. Thanks! HVAC added to check out individual space, EMS. . . | 2016-09-28 - 18290 - Jennifer Moyer-Install new assembly into unit. - Jennifer Moyer; 2016-09-28 - 18290 - Zhi Yu-Install new assembly into unit. - Jennifer Moyer | MWO:ZHI, This fan coil has the chilled water valved off because it has a severe water leak. See if you can determine if it is repairable. If not, please get me pictures, model numbers, voltage and measurements so we can get a replacement unit. Thanks! HVAC added to check out individual space, EMS. . . 2016-09-28 - 18290 - Jennifer Moyer-Install new assembly into unit. - Jennifer Moyer; 2016-09-28 - 18290 - Zhi Yu-Install new assembly into unit. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-26 | 176354 | RFMT-131977 | !! AC has been broken for more than 24 hours Contact Name: Contact Phone Number: 9095410455 Contact Email: 4NJME90 | 2016-09-27 - 18010 - David Cates-Resident said that the tstat was set very low yesterday, and stopped working last night so they turned it all of the way up. Turned it down to 70 degrees when I arrived today and the unit came on working perfectly. Unit most likely froze up when they had it set too low. - David Cates | !! AC has been broken for more than 24 hours Contact Name: Contact Phone Number: 9095410455 Contact Email: 4NJME90 2016-09-27 - 18010 - David Cates-Resident said that the tstat was set very low yesterday, and stopped working last night so they turned it all of the way up. Turned it down to 70 degrees when I arrived today and the unit came on working perfectly. Unit most likely froze up when they had it set too low. - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-26 | 176356 | RFMT-131975 | !! Garbage disposal is not working. 4NOGN4F | 2016-09-27 - 23000 - Thomas Zambrano-repair dosposal and found dishwasher leaking ar motor. i will replace on9/28/16 - Thomas Zambrano; 2016-09-28 - 23000 - Thomas Zambrano-wrong room, dishwasher works fine. the replacement went to room 520. - Thomas Zambrano | !! Garbage disposal is not working. 4NOGN4F 2016-09-27 - 23000 - Thomas Zambrano-repair dosposal and found dishwasher leaking ar motor. i will replace on9/28/16 - Thomas Zambrano; 2016-09-28 - 23000 - Thomas Zambrano-wrong room, dishwasher works fine. the replacement went to room 520. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 208693 | RAMA-100571 | Bedroom D (in A-221) has been having trouble with their Dishwasher, her ceiling fan that will not run the fan and light at the same time, and also her window will not open. She has requested that she be present during repairs in her room. Tuesday at 3pm is the best time to make the repairs if possib. . . | NA | Bedroom D (in A-221) has been having trouble with their Dishwasher, her ceiling fan that will not run the fan and light at the same time, and also her window will not open. She has requested that she be present during repairs in her room. Tuesday at 3pm is the best time to make the repairs if possib. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 215694 | RACC-112916 | The air vent towards the back of the room does not ventilate. It may be closed but there is no way for us to open it. Thank you! 4O29BE1 | NA | The air vent towards the back of the room does not ventilate. It may be closed but there is no way for us to open it. Thank you! 4O29BE1 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 215709 | RACC-112901 | The air conditioner display is not working, we think it is out of batteries. 4NNNMKE | NA | The air conditioner display is not working, we think it is out of batteries. 4NNNMKE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 215710 | RACC-112900 | !! The garbage disposal will not work. After switching the on/off switch there is no noise and nothing happens. Also our fan in the living room shakes rapidly when we turn it on and there is a fan blade missing. Lastly the light cover for the living room fan/light is missing as well. Thank you, Beau. . . | NA | !! The garbage disposal will not work. After switching the on/off switch there is no noise and nothing happens. Also our fan in the living room shakes rapidly when we turn it on and there is a fan blade missing. Lastly the light cover for the living room fan/light is missing as well. Thank you, Beau. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 234691 | POLY-113508 | 10/13 - STEVE - Jesse said that he gave this work order over to you on 8/26/16 to fix, since apparently the compressor on the fountain is not working. Repeat Request. I had requested that the outside drinking fountains be repaired. They have not been repaired so far and I was wondering if you cou. . . | NA | 10/13 - STEVE - Jesse said that he gave this work order over to you on 8/26/16 to fix, since apparently the compressor on the fountain is not working. Repeat Request. I had requested that the outside drinking fountains be repaired. They have not been repaired so far and I was wondering if you cou. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-26 | 256234 | DTPC-112304 | Dropped drivers license down AC Vent (4th Row). Her class is over at 12:40. Please call her after that.If you get her license. Thx | 2016-09-27 - 13080 - Thomas Klein-Found license had to remove grill which had been secured in place.Removed license, returned to owner and reattached the grill. - Thomas Klein | Dropped drivers license down AC Vent (4th Row). Her class is over at 12:40. Please call her after that.If you get her license. Thx 2016-09-27 - 13080 - Thomas Klein-Found license had to remove grill which had been secured in place.Removed license, returned to owner and reattached the grill. - Thomas Klein | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-26 | 256243 | DTPC-112295 | The 4th floor and common areas are very warm. | 2016-09-26 - 18290 - James Hermann-Looked at the air handling units for the floor and the cooling valves were disabled. Emailed Steve to find cause. Temp was 77 in the hallways. - James Hermann; 2016-09-27 - 18290 - James Hermann-Found a problem with the cooling valves that was linked to the OAT. After troubleshooting and and bypassing the OAT and then talking to Brian O'Hagen we are going to looking at the programming aspect and all of the equipment functions properly on a stand alone basis. - James Hermann; 2016-09-27 - 18290 - Steve Skibbe-Found a problem with the cooling valves that was linked to the OAT. After troubleshooting and and bypassing the OAT and then talking to Brian O'Hagen we are going to looking at the programming aspect and all of the equipment functions properly on a stand alone basis. - James Hermann; 2016-11-15 - 18290 - James Hermann-problem related to the Allerton Envision programming issues and has been resolved. - James Hermann | The 4th floor and common areas are very warm. 2016-09-26 - 18290 - James Hermann-Looked at the air handling units for the floor and the cooling valves were disabled. Emailed Steve to find cause. Temp was 77 in the hallways. - James Hermann; 2016-09-27 - 18290 - James Hermann-Found a problem with the cooling valves that was linked to the OAT. After troubleshooting and and bypassing the OAT and then talking to Brian O'Hagen we are going to looking at the programming aspect and all of the equipment functions properly on a stand alone basis. - James Hermann; 2016-09-27 - 18290 - Steve Skibbe-Found a problem with the cooling valves that was linked to the OAT. After troubleshooting and and bypassing the OAT and then talking to Brian O'Hagen we are going to looking at the programming aspect and all of the equipment functions properly on a stand alone basis. - James Hermann; 2016-11-15 - 18290 - James Hermann-problem related to the Allerton Envision programming issues and has been resolved. - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-09-27 | 58740 | TMPE-191417 | MWO MUSIC W260 *TRANSFER* BT to HVAC The condenser fan was running constantly and the compressor was short cycling. It is now tuned off ORIG REQUEST In the hallway near W260, a plume of smoke came out of the vent below the water fountain. Not smoking anymore but the hallway is filled with haze a. . . | 2016-11-29 - 23080 - Jennifer Moyer-Locate water fountain, tried to locate breaker to isolate power, troubleshoot unit. Compressor winding burnt. Work order created for electric shop to isolate power. Work order created for plumbing shop to replace unit, R-12 refrigerant: obsolete. - Jennifer Moyer | MWO MUSIC W260 *TRANSFER* BT to HVAC The condenser fan was running constantly and the compressor was short cycling. It is now tuned off ORIG REQUEST In the hallway near W260, a plume of smoke came out of the vent below the water fountain. Not smoking anymore but the hallway is filled with haze a. . . 2016-11-29 - 23080 - Jennifer Moyer-Locate water fountain, tried to locate breaker to isolate power, troubleshoot unit. Compressor winding burnt. Work order created for electric shop to isolate power. Work order created for plumbing shop to replace unit, R-12 refrigerant: obsolete. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
2016-09-27 | 58816 | TMPE-191341 | MWO: PSF RM F74 *TRANSFER* EL To HVAC Fan coil is making an unusually loud noise. Transferred call to EL Shop, this room has a fan coil above the drop ceiling for cooling. There is no power to the fan coil. Please add electrical services so that cooling can be restored to this lab. EMS WO#18. . . | 2016-09-30 - 18010 - Roque Garcia-Purchased motor yesterday 9/29/2016 from ARS and returned motor 9/30/2016 to ARS. Motor was defective noisy and exchanged it and reinstalled today 9/30/2016. - Roque Garcia; 2016-10-20 - 18010 - Roque Garcia-Replaced motor and pulley. The new motor was defective and was making noise. Removed and returned and replaced it again with replacement. - Roque Garcia | MWO: PSF RM F74 *TRANSFER* EL To HVAC Fan coil is making an unusually loud noise. Transferred call to EL Shop, this room has a fan coil above the drop ceiling for cooling. There is no power to the fan coil. Please add electrical services so that cooling can be restored to this lab. EMS WO#18. . . 2016-09-30 - 18010 - Roque Garcia-Purchased motor yesterday 9/29/2016 from ARS and returned motor 9/30/2016 to ARS. Motor was defective noisy and exchanged it and reinstalled today 9/30/2016. - Roque Garcia; 2016-10-20 - 18010 - Roque Garcia-Replaced motor and pulley. The new motor was defective and was making noise. Removed and returned and replaced it again with replacement. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-27 | 58866 | TMPE-191291 | SWO MU Eco Fresh Cafe !! Exhaust fan # 1610 is not working. Motor is making a noise when you try and start it up. 42A7I1A | 2016-10-03 - 18160 - Thomas Gibble-Removed and replaced motor, found on/off switch on unit was also burned out, trip to independent electric for new switch. Installed new belts, run test. COMPLETE - Gail Jackson; 2016-10-03 - 18160 - Gail Jackson-Removed and replaced motor, found on/off switch on unit was also burned out, trip to independent electric for new switch. Installed new belts, run test. COMPLETE - Gail Jackson | SWO MU Eco Fresh Cafe !! Exhaust fan # 1610 is not working. Motor is making a noise when you try and start it up. 42A7I1A 2016-10-03 - 18160 - Thomas Gibble-Removed and replaced motor, found on/off switch on unit was also burned out, trip to independent electric for new switch. Installed new belts, run test. COMPLETE - Gail Jackson; 2016-10-03 - 18160 - Gail Jackson-Removed and replaced motor, found on/off switch on unit was also burned out, trip to independent electric for new switch. Installed new belts, run test. COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-27 | 176294 | RFMT-132037 | Please meet Johnson Controls HVAC tech during the service call for the Harmonic Control repair for Chiller # 1. Please obtain a copy of the service call field invoice. Thank you. | 2016-09-28 - 18010 - Thor Millsaps-Met Johnson Controls chiller mechanic- Edward. Reset chiller #1. Disabled and disconnected harmonic filter board. Serial Comm fault caused chiller to shut down at 3am this morning. Edward made sure all connections were tight. Chiller #1 started back up and is running. Shut down chiller #2. Edward will send electronic field report to manager. - Thor Millsaps | Please meet Johnson Controls HVAC tech during the service call for the Harmonic Control repair for Chiller # 1. Please obtain a copy of the service call field invoice. Thank you. 2016-09-28 - 18010 - Thor Millsaps-Met Johnson Controls chiller mechanic- Edward. Reset chiller #1. Disabled and disconnected harmonic filter board. Serial Comm fault caused chiller to shut down at 3am this morning. Edward made sure all connections were tight. Chiller #1 started back up and is running. Shut down chiller #2. Edward will send electronic field report to manager. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-27 | 176305 | RFMT-132026 | Please order fan coil motors for shelf stock. Fasco # 131809 Mod. D 347 Thank you. | 2016-09-28 - 18010 - MOTORS ORDERED 09/27/16 - Gregory Stetka | Please order fan coil motors for shelf stock. Fasco # 131809 Mod. D 347 Thank you. 2016-09-28 - 18010 - MOTORS ORDERED 09/27/16 - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-27 | 234646 | POLY-113553 | * Light on the front porch needs to be replaced * Shared bathroom sink is clogged * Filter in AC needs to be replaced since the slot cannot be located in this particular unit. 4N45332 | NA | * Light on the front porch needs to be replaced * Shared bathroom sink is clogged * Filter in AC needs to be replaced since the slot cannot be located in this particular unit. 4N45332 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-28 | 4339 | WEST-106910 | courtyard fountain 'low water cut out' malfunctioning. Controller has to be custom made by supplier. unit is on order. long lead time expected. rr. 12/19- rec'd controller. due to time restrictions, controller will be installed at a later date on a new work order. rr. | 2016-09-29 - 15000 - Joseph Danielek-trouble shoot pond water level / low water pump cut out controller - pump relay on control board malfunctioning - need new control board - connected pump motor starter to nc spade on water level relay to run pump when water level is satisfied meaning when filling the pump cycles off, when full pump cycles on when fill valve closed - Joseph Danielek; 2016-10-19 - 15000 - Joseph Danielek-cleaned probe and realized fill side of board failed - board in complete failure - fountain in manual fill and run mode - ask jim (stores) to order controller and probe fountain people recommended as replacement - Joseph Danielek [Modified: 2016-10-19 Joseph Danielek]; 2016-10-20 - 15000 - Joseph Danielek-confirmed with jim-stores on purchasing controller - Joseph Danielek | courtyard fountain 'low water cut out' malfunctioning. Controller has to be custom made by supplier. unit is on order. long lead time expected. rr. 12/19- rec'd controller. due to time restrictions, controller will be installed at a later date on a new work order. rr. 2016-09-29 - 15000 - Joseph Danielek-trouble shoot pond water level / low water pump cut out controller - pump relay on control board malfunctioning - need new control board - connected pump motor starter to nc spade on water level relay to run pump when water level is satisfied meaning when filling the pump cycles off, when full pump cycles on when fill valve closed - Joseph Danielek; 2016-10-19 - 15000 - Joseph Danielek-cleaned probe and realized fill side of board failed - board in complete failure - fountain in manual fill and run mode - ask jim (stores) to order controller and probe fountain people recommended as replacement - Joseph Danielek [Modified: 2016-10-19 Joseph Danielek]; 2016-10-20 - 15000 - Joseph Danielek-confirmed with jim-stores on purchasing controller - Joseph Danielek | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-28 | 58514 | TMPE-191643 | SWO Weatherup: !! Notify HVAC shop. AHU2, Women's Gym is commanded on, the fans are running but the compressors are not on. Please troubleshoot. Call me if you need help. Thanks. 42C3NC4 Left Voicemail with Roque no answer on the standby line 5:15pm Roque called back 5:35pm will reach o. . . | 2016-09-28 - 18030 - Roque Garcia-Spoke with Robert Zeller and he was notified from Brian Qualls that the unit is working and running. Brian took care of the problem. - Roque Garcia; 2016-09-30 - 18030 - 9/28/2016 0.25OT 5pm-5:15pm Brian Qualls - Weatherup Weatherup - A/H #2 Compressors not coming on. - Kerri Perkins | SWO Weatherup: !! Notify HVAC shop. AHU2, Women's Gym is commanded on, the fans are running but the compressors are not on. Please troubleshoot. Call me if you need help. Thanks. 42C3NC4 Left Voicemail with Roque no answer on the standby line 5:15pm Roque called back 5:35pm will reach o. . . 2016-09-28 - 18030 - Roque Garcia-Spoke with Robert Zeller and he was notified from Brian Qualls that the unit is working and running. Brian took care of the problem. - Roque Garcia; 2016-09-30 - 18030 - 9/28/2016 0.25OT 5pm-5:15pm Brian Qualls - Weatherup Weatherup - A/H #2 Compressors not coming on. - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-28 | 58524 | TMPE-191633 | MWO: INTDSA-A207B The independent AC system (Mitsubishi Electric Mr. Slim) that is in A207B is not cooling properly. It's very important that we have this room cooled as many computers are located in there that give off a great amount of heat. Thermostat is set at 67 degrees, but it is only 72 de. . . | 2016-10-04 - 18290 - 10/4/2016 at 2:30 pm, JH called and left a message with Elisabeth Luquez at 480-965-3954 to get more details. - John Howell; 2016-10-05 - 18290 - Jennifer Moyer-Unit was set at 67 and not cooling to temperature. The thermostat displayed a dirty filter alarm. Customer stated that the filter had not been cleaned in their recent memory. I removed the filters, washed, dried, and reinstalled them. Filters were extremely dirty and may have restricted air flow to the unit. To reset the unit/thermostat, I turned the unit off for 3 or 4 minutes, then turned it back on. The air exiting the unit was significantly cooler and was dropping the air temperature in the room. I could not stay to monitor the unit, as I had to pick up my co-worker from another job. - Jennifer Moyer; 2016-10-05 - 18290 - Jennifer Moyer-checked operation of unit. Unit is operational. - Jennifer Moyer; 2016-10-05 - 18290 - Midhat Mukanovic-checked operation of unit. Unit is operational. - Jennifer Moyer; 2016-11-29 - 18290 - Jennifer Moyer-Installed new motor. - Jennifer Moyer | MWO: INTDSA-A207B The independent AC system (Mitsubishi Electric Mr. Slim) that is in A207B is not cooling properly. It's very important that we have this room cooled as many computers are located in there that give off a great amount of heat. Thermostat is set at 67 degrees, but it is only 72 de. . . 2016-10-04 - 18290 - 10/4/2016 at 2:30 pm, JH called and left a message with Elisabeth Luquez at 480-965-3954 to get more details. - John Howell; 2016-10-05 - 18290 - Jennifer Moyer-Unit was set at 67 and not cooling to temperature. The thermostat displayed a dirty filter alarm. Customer stated that the filter had not been cleaned in their recent memory. I removed the filters, washed, dried, and reinstalled them. Filters were extremely dirty and may have restricted air flow to the unit. To reset the unit/thermostat, I turned the unit off for 3 or 4 minutes, then turned it back on. The air exiting the unit was significantly cooler and was dropping the air temperature in the room. I could not stay to monitor the unit, as I had to pick up my co-worker from another job. - Jennifer Moyer; 2016-10-05 - 18290 - Jennifer Moyer-checked operation of unit. Unit is operational. - Jennifer Moyer; 2016-10-05 - 18290 - Midhat Mukanovic-checked operation of unit. Unit is operational. - Jennifer Moyer; 2016-11-29 - 18290 - Jennifer Moyer-Installed new motor. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-09-28 | 58617 | TMPE-191540 | SWO: !! Please repair ice machine at Starbucks at Palo Verde East. Closed until Wednesday 8/10/16 so please contact Stephanie at 520-991-6754. Submitted by 4O2FB2L | 2016-09-28 - 18210 - Zhi Yu-Found ice machine short cycling. Trouble shoot, low charge. - Francesca Fernandez; 2016-09-28 - 18210 - Zhi Yu-Found leaking dump valve that leaked R/O water on frig dryer eating holes in it. All frig leaked out. Trip to TRUE TEMP for valve and filter: install parts, vacuum, charge and run test. No parking in area due to construction. - Francesca Fernandez; 2016-09-28 - 18210 - Gail Jackson-Found leaking dump valve that leaked R/O water on frig dryer eating holes in it. All frig leaked out. Trip to TRUE TEMP for valve and filter: install parts, vacuum, charge and run test. No parking in area due to construction. - Francesca Fernandez | SWO: !! Please repair ice machine at Starbucks at Palo Verde East. Closed until Wednesday 8/10/16 so please contact Stephanie at 520-991-6754. Submitted by 4O2FB2L 2016-09-28 - 18210 - Zhi Yu-Found ice machine short cycling. Trouble shoot, low charge. - Francesca Fernandez; 2016-09-28 - 18210 - Zhi Yu-Found leaking dump valve that leaked R/O water on frig dryer eating holes in it. All frig leaked out. Trip to TRUE TEMP for valve and filter: install parts, vacuum, charge and run test. No parking in area due to construction. - Francesca Fernandez; 2016-09-28 - 18210 - Gail Jackson-Found leaking dump valve that leaked R/O water on frig dryer eating holes in it. All frig leaked out. Trip to TRUE TEMP for valve and filter: install parts, vacuum, charge and run test. No parking in area due to construction. - Francesca Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-09-28 | 58619 | TMPE-191538 | SWO: Can I get someone to go to Manzy dining hall. They have a cooler not working. It\\u2019s in the front at the pizza station. Thanks The reach-in refrigerator is down and will not turn on to cool the product. | 2016-09-28 - 18100 - Zhi Yu-Arrived Cooler switch turn off. We turn cooler observe temperature and clean coil. Inside box temp @36deg and top cold well @20deg - Francesca Fernandez; 2016-09-28 - 18100 - Gail Jackson-Arrived Cooler switch turn off. We turn cooler observe temperature and clean coil. Inside box temp @36deg and top cold well @20deg - Francesca Fernandez | SWO: Can I get someone to go to Manzy dining hall. They have a cooler not working. It\\u2019s in the front at the pizza station. Thanks The reach-in refrigerator is down and will not turn on to cool the product. 2016-09-28 - 18100 - Zhi Yu-Arrived Cooler switch turn off. We turn cooler observe temperature and clean coil. Inside box temp @36deg and top cold well @20deg - Francesca Fernandez; 2016-09-28 - 18100 - Gail Jackson-Arrived Cooler switch turn off. We turn cooler observe temperature and clean coil. Inside box temp @36deg and top cold well @20deg - Francesca Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-09-28 | 58647 | TMPE-191510 | MWO ARWH 130B This office is extremely hot, please adjust asap, thank you! | 2016-09-28 - 18290 - Zhi Yu-Bad Condenser fan Motor. 1/2hp 1075 rpm 208-230. In Working progress. Work order 191510 and 191176 are duplicate. - Zhi Yu [Modified: 2016-09-29 Zhi Yu] | MWO ARWH 130B This office is extremely hot, please adjust asap, thank you! 2016-09-28 - 18290 - Zhi Yu-Bad Condenser fan Motor. 1/2hp 1075 rpm 208-230. In Working progress. Work order 191510 and 191176 are duplicate. - Zhi Yu [Modified: 2016-09-29 Zhi Yu] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-28 | 58649 | TMPE-191508 | MWO: !! Hello, The water chiller for the wind tunnel, in USE 174 started making a loud grinding noise this morning. There is a clear liquid leaking out of it, which I think is Freon. Can someone please take a look at it very soon? Thank you. 42A89JG | 2016-09-28 - 18080 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-11 - 18080 - Thomas Gibble-replaced pump,value and temp control. cleaned tank. - Thomas Gibble; 2016-10-11 - 18080 - Gail Jackson-replaced pump,value and temp control. cleaned tank. - Thomas Gibble; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Gail Jackson-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson | MWO: !! Hello, The water chiller for the wind tunnel, in USE 174 started making a loud grinding noise this morning. There is a clear liquid leaking out of it, which I think is Freon. Can someone please take a look at it very soon? Thank you. 42A89JG 2016-09-28 - 18080 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-11 - 18080 - Thomas Gibble-replaced pump,value and temp control. cleaned tank. - Thomas Gibble; 2016-10-11 - 18080 - Gail Jackson-replaced pump,value and temp control. cleaned tank. - Thomas Gibble; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Thomas Gibble-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson; 2016-10-17 - 18080 - Gail Jackson-Found pump, control valve and Ranco T-Stat burned out, trip to united Frig, ARS, and Grainger for parts. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-28 | 58699 | TMPE-191458 | SWO: Request for Estimate. Please provide me with an estimate to service the ice machine in ECF 130D. It is making a ticking noise when the compressor turns on. 42C4H6G Please talk to Roque for specifics. | 2016-11-08 - 18180 - Gail Jackson-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-08 - 18180 - Thomas Gibble-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-08 - 18180 - Thomas Gibble-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-15 - 18180 - Gail Jackson-Disassemble machine, clean all parts, and begin reassembly. - Gail Jackson; 2016-11-15 - 18180 - Thomas Gibble-Disassemble machine, clean all parts, and begin reassembly. - Gail Jackson; 2016-11-15 - 18180 - Gail Jackson-reassemble machine, repair leg, run cleaner and run test - Gail Jackson; 2016-11-15 - 18180 - Thomas Gibble-reassemble machine, repair leg, run cleaner and run test - Gail Jackson; 2016-11-16 - 18180 - Gail Jackson-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson; 2016-11-16 - 18180 - Carl Karr-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson; 2016-11-16 - 18180 - Derek Gittings-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson | SWO: Request for Estimate. Please provide me with an estimate to service the ice machine in ECF 130D. It is making a ticking noise when the compressor turns on. 42C4H6G Please talk to Roque for specifics. 2016-11-08 - 18180 - Gail Jackson-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-08 - 18180 - Thomas Gibble-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-08 - 18180 - Thomas Gibble-Customer reports metal shavings in ice. Machine had this same problem before when it was still under warranty. Found angle stop would not shut H2O off, trip to ACE for new part and installation, searched for main shut off; found in ceiling; replaced valve. Transport ice maker to shop for repairs. - Gail Jackson; 2016-11-15 - 18180 - Gail Jackson-Disassemble machine, clean all parts, and begin reassembly. - Gail Jackson; 2016-11-15 - 18180 - Thomas Gibble-Disassemble machine, clean all parts, and begin reassembly. - Gail Jackson; 2016-11-15 - 18180 - Gail Jackson-reassemble machine, repair leg, run cleaner and run test - Gail Jackson; 2016-11-15 - 18180 - Thomas Gibble-reassemble machine, repair leg, run cleaner and run test - Gail Jackson; 2016-11-16 - 18180 - Gail Jackson-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson; 2016-11-16 - 18180 - Carl Karr-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson; 2016-11-16 - 18180 - Derek Gittings-Transport machine to Eng. F and installed. Trip to shop for lift. Trip to ACE to replace drain tubing. Found power strip burned out, trip to Eng. G for replacement. Installed new H20 filter and drain tubing. Run test. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-09-28 | 176185 | RFMT-132146 | I need the air filter changed in my vent--it keeps spitting out chunks of dust, I would like it replaced, not just wiped out. 4NK3GNI | 2016-09-29 - 18010 - Scott Berndt-cleaned out and replaced a/c filter - Scott Berndt | I need the air filter changed in my vent--it keeps spitting out chunks of dust, I would like it replaced, not just wiped out. 4NK3GNI 2016-09-29 - 18010 - Scott Berndt-cleaned out and replaced a/c filter - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-28 | 176210 | RFMT-132121 | !! We are in the J cluster in the Chapter Room and the a/c is at 90 degrees. Could you please send someone asap to check the a/c? Submitted by 4NID637 | 2016-09-28 - 18010 - Thor Millsaps-Replaced 35/5 mfd dual capacitor. System up and running. - Thor Millsaps | !! We are in the J cluster in the Chapter Room and the a/c is at 90 degrees. Could you please send someone asap to check the a/c? Submitted by 4NID637 2016-09-28 - 18010 - Thor Millsaps-Replaced 35/5 mfd dual capacitor. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 176214 | RFMT-132117 | !! The main door that they share with the the market will not shut. Submitted by 4NBIEFN | 2016-09-28 - 13070 - Gabriel Figueroa-motor fell off, turned into lock shop. - Gabriel Figueroa | !! The main door that they share with the the market will not shut. Submitted by 4NBIEFN 2016-09-28 - 13070 - Gabriel Figueroa-motor fell off, turned into lock shop. - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-28 | 176218 | RFMT-132113 | !! Shortly after our air conditioning filter was changed, mold started to form all over the bathroom, despite leaving the door open after showers to let out steamy air. Me and another roommate both have asthma and it's starting to affect how we breathe. It is NOT mildew. It's mold. We need these iss. . . | NA | !! Shortly after our air conditioning filter was changed, mold started to form all over the bathroom, despite leaving the door open after showers to let out steamy air. Me and another roommate both have asthma and it's starting to affect how we breathe. It is NOT mildew. It's mold. We need these iss. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 176219 | RFMT-132112 | !! Shortly after our air conditioning filter was changed, mold started to form all over the bathroom, despite leaving the door open after showers to let out steamy air. Me and another roommate both have asthma and it's starting to affect how we breathe. It is NOT mildew. It's mold. Along with that o. . . | 2016-09-29 - 18010 - Mike Guckian-looks good to me. she said someone was in yesterday to clean it. - Mike Guckian | !! Shortly after our air conditioning filter was changed, mold started to form all over the bathroom, despite leaving the door open after showers to let out steamy air. Me and another roommate both have asthma and it's starting to affect how we breathe. It is NOT mildew. It's mold. Along with that o. . . 2016-09-29 - 18010 - Mike Guckian-looks good to me. she said someone was in yesterday to clean it. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 176228 | RFMT-132103 | Please inspect all vent filters in cluster j. Some residents reported it needing to be replaced. Thanks, Carli 4NF4L2O | 2016-09-28 - 18010 - David Cates-All filters in Adelphi I are scheduled to be replaced during the Door To Door preventative maintenance inspections starting in October. - David Cates | Please inspect all vent filters in cluster j. Some residents reported it needing to be replaced. Thanks, Carli 4NF4L2O 2016-09-28 - 18010 - David Cates-All filters in Adelphi I are scheduled to be replaced during the Door To Door preventative maintenance inspections starting in October. - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-28 | 176232 | RFMT-132099 | !! We are in the J cluster in the Chapter Room and the a/c is at 90 degrees. Could you please send someone asap to check the a/c? Submitted by 4NID637 | 2016-09-28 - 18010 - David Cates-Simon and Thor replaced a capacitor on the unit - David Cates | !! We are in the J cluster in the Chapter Room and the a/c is at 90 degrees. Could you please send someone asap to check the a/c? Submitted by 4NID637 2016-09-28 - 18010 - David Cates-Simon and Thor replaced a capacitor on the unit - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 176234 | RFMT-132097 | Please check HVAC systems condensation lines and pans for proper operation, installation and conditions in room L 108. Adjust , repair or report as appropriate. Thank you. | 2016-09-28 - 18010 - Thor Millsaps-Cleared primary condensate drain line and tested for proper drainage. Checked refrigerant and added 1 lb r22. - Thor Millsaps | Please check HVAC systems condensation lines and pans for proper operation, installation and conditions in room L 108. Adjust , repair or report as appropriate. Thank you. 2016-09-28 - 18010 - Thor Millsaps-Cleared primary condensate drain line and tested for proper drainage. Checked refrigerant and added 1 lb r22. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 176235 | RFMT-132096 | !! Requesting service from Olympus for Hayden South rm. 105: The occupant is concerned there may be mold in the carpet. The occupant mentioned the carpet was previously wet due to the air conditioning units condensation leak. Please clean and treat carpet. Thank you. Submitted by 42DINIB | NA | !! Requesting service from Olympus for Hayden South rm. 105: The occupant is concerned there may be mold in the carpet. The occupant mentioned the carpet was previously wet due to the air conditioning units condensation leak. Please clean and treat carpet. Thank you. Submitted by 42DINIB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 234539 | POLY-113660 | !! The AC has been setting itself back to 81 degrees even when we try to set it at 77. And the AC has not been cooling the rooms sufficiently. Also it never turns off even though it is not set on auto or on fan mode. The ac is on but the air is not cooling the entire house. 4NC87B2 | NA | !! The AC has been setting itself back to 81 degrees even when we try to set it at 77. And the AC has not been cooling the rooms sufficiently. Also it never turns off even though it is not set on auto or on fan mode. The ac is on but the air is not cooling the entire house. 4NC87B2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 234564 | POLY-113635 | Air compressor/handler is icing over and dripping water. Please restore to normal operating condition 42B55N2 | NA | Air compressor/handler is icing over and dripping water. Please restore to normal operating condition 42B55N2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-09-28 | 234572 | POLY-113627 | !! A/C not working properly. Filter was already changed but house is still hot. Dial for A/C might not be working either. 4NFHC4M | NA | !! A/C not working properly. Filter was already changed but house is still hot. Dial for A/C might not be working either. 4NFHC4M NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 234577 | POLY-113622 | CALLED ESLI !! Air conditioner not working. Service required. Contact Name: Sai Tatapudi Contact Phone Number: 4807271220 Contact Email: sai.tatapudi@asu.edu 4NLJOFI | NA | CALLED ESLI !! Air conditioner not working. Service required. Contact Name: Sai Tatapudi Contact Phone Number: 4807271220 Contact Email: sai.tatapudi@asu.edu 4NLJOFI NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 234582 | POLY-113617 | BILLED BILLED JC5-7011 $60.96 FOR LABOR ON #JC288008289 ON 4/19/17 Century Hall - middle and end study rooms on 2nd floor south: The AC is broken in the rooms and are not cooling the rooms. *WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL* | NA | BILLED BILLED JC5-7011 $60.96 FOR LABOR ON #JC288008289 ON 4/19/17 Century Hall - middle and end study rooms on 2nd floor south: The AC is broken in the rooms and are not cooling the rooms. *WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL* NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-09-28 | 234587 | POLY-113612 | BILLED BILLED JC5-7011 $60.96 FOR LABOR ON #JC2II008382 ON 4/25/17 Both vent fans in the bathroom are out and not working *WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL* | NA | BILLED BILLED JC5-7011 $60.96 FOR LABOR ON #JC2II008382 ON 4/25/17 Both vent fans in the bathroom are out and not working *WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL* NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-09-28 | 234595 | POLY-113604 | BILLED BILLED JC5-7011 $46.72 FOR LABOR ON #JC2II008350 ON 4/24/17 AC is out. Can the temp become cooler WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL | 2016-10-21 - 18010 - Allan Blair-10/3 - Allan reset the controls at the unit. - Gayle Swenson | BILLED BILLED JC5-7011 $46.72 FOR LABOR ON #JC2II008350 ON 4/24/17 AC is out. Can the temp become cooler WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL 2016-10-21 - 18010 - Allan Blair-10/3 - Allan reset the controls at the unit. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-28 | 234606 | POLY-113593 | BILLED BILLED JC5-7011 $186.88 FOR LABOR ON #JC2II008311 ON 4/21/17 AC is not cooling can filter be changed and temp lowered WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL | NA | BILLED BILLED JC5-7011 $186.88 FOR LABOR ON #JC2II008311 ON 4/21/17 AC is not cooling can filter be changed and temp lowered WILL BE CHARGED BACK/REIMBURSED BY CENTURY HALL NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-29 | 58391 | TMPE-191766 | MWO: !! The air conditioning is not working again in this office. 4NF62MD | 2017-02-17 - 18010 - Mitchell Andrews-found leaks on the 4 way valve unit need to be replaced - Mitchell Andrews | MWO: !! The air conditioning is not working again in this office. 4NF62MD 2017-02-17 - 18010 - Mitchell Andrews-found leaks on the 4 way valve unit need to be replaced - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-09-29 | 58408 | TMPE-191749 | MWO: USB 2650 Help Center - Diana Building: USB Room: 2650 USB 2650 ceiling tile got soaked and fell to the ground the one tile but there is a lot of wetness on the floor. A/c might be leaking it had been worked on earlier this month. The a/c is working properly, it is not physically lea. . . | 2016-09-29 - 23000 - CALLED TO BT SEAN. - Monica Moraga; 2016-09-29 - 23000 - Sean Humphrey-Transferred to HVAC - Sean Humphrey | MWO: USB 2650 Help Center - Diana Building: USB Room: 2650 USB 2650 ceiling tile got soaked and fell to the ground the one tile but there is a lot of wetness on the floor. A/c might be leaking it had been worked on earlier this month. The a/c is working properly, it is not physically lea. . . 2016-09-29 - 23000 - CALLED TO BT SEAN. - Monica Moraga; 2016-09-29 - 23000 - Sean Humphrey-Transferred to HVAC - Sean Humphrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-29 | 176164 | RFMT-132167 | Please replace the cold water belimo valve at San Pablo room 237. Simon | 2016-09-30 - 18010 - Simon Fernandez-checked a/c unit found bad Belimo valve,removed and replaced Belimo. - Simon Fernandez | Please replace the cold water belimo valve at San Pablo room 237. Simon 2016-09-30 - 18010 - Simon Fernandez-checked a/c unit found bad Belimo valve,removed and replaced Belimo. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-09-29 | 215606 | RACC-113004 | !! Air conditioning and kitchen outlets/lights not working 4NNH8D2 | NA | !! Air conditioning and kitchen outlets/lights not working 4NNH8D2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-29 | 234525 | POLY-113674 | Please supply 2 more keys for the padlock for refrigerant at the A/C house. | NA | Please supply 2 more keys for the padlock for refrigerant at the A/C house. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-30 | 58148 | TMPE-192009 | MWO: GWC 675 The walk in cooler is alarming. It's at 12 degrees and should be at 4 degrees. | 2016-09-30 - 18100 - CALLED TO JOHN H. - Monica Moraga; 2016-11-04 - 18100 - Robert Dauscher-Found bad blower motor... Blowing fuses.. need to order specialty OEM motor. - Robert Dauscher; 2016-11-04 - 18100 - Robert Dauscher-replaced OEM Motor that was ordered and shipped to vendor. Monitor box operation - Robert Dauscher | MWO: GWC 675 The walk in cooler is alarming. It's at 12 degrees and should be at 4 degrees. 2016-09-30 - 18100 - CALLED TO JOHN H. - Monica Moraga; 2016-11-04 - 18100 - Robert Dauscher-Found bad blower motor... Blowing fuses.. need to order specialty OEM motor. - Robert Dauscher; 2016-11-04 - 18100 - Robert Dauscher-replaced OEM Motor that was ordered and shipped to vendor. Monitor box operation - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-09-30 | 58189 | TMPE-191968 | Installation of new evap cooler by Johnson Controls | NA | Installation of new evap cooler by Johnson Controls NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-30 | 58191 | TMPE-191966 | Installation of new evap cooler Johnson Controls | NA | Installation of new evap cooler Johnson Controls NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-30 | 58236 | TMPE-191921 | MWO: Noble - 2 thermostats Hi, The covers are missing from 2 thermostats on the 3rd floor. They are located on the wall between room 350 and room 364. Thanks! Daphne Gill 480.727.6270 4MNA207 | 2016-10-10 - 18010 - Jennifer Moyer-Picked up thermostat covers from central plant and installed. - Jennifer Moyer | MWO: Noble - 2 thermostats Hi, The covers are missing from 2 thermostats on the 3rd floor. They are located on the wall between room 350 and room 364. Thanks! Daphne Gill 480.727.6270 4MNA207 2016-10-10 - 18010 - Jennifer Moyer-Picked up thermostat covers from central plant and installed. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-30 | 176081 | RFMT-132250 | Please inspect K 214/216 for continued problems cooling the room. Thanks, Carli 4NF4L2O | 2016-10-01 - 18010 - Joe Swan-intake air vent was blocked. - Joe Swan | Please inspect K 214/216 for continued problems cooling the room. Thanks, Carli 4NF4L2O 2016-10-01 - 18010 - Joe Swan-intake air vent was blocked. - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-09-30 | 176118 | RFMT-132213 | !! No AC, please address asap Submitted by 4O077C3 | 2016-10-01 - 18010 - repair completed tech need to add notes in results and finish. - Gregory Stetka; 2016-10-03 - 18010 - Thor Millsaps-Replaced thermostat with digital non-programmable thermostat. Set temp set point limits to 70 cooling and 80 heating. - Thor Millsaps | !! No AC, please address asap Submitted by 4O077C3 2016-10-01 - 18010 - repair completed tech need to add notes in results and finish. - Gregory Stetka; 2016-10-03 - 18010 - Thor Millsaps-Replaced thermostat with digital non-programmable thermostat. Set temp set point limits to 70 cooling and 80 heating. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-09-30 | 215598 | RACC-113012 | !! Maintenance came by to replace our A/C Filters but left top hatch open and also did not replace filters - just left hatch down. They told us they would be back but never came. This is a safety hazard for our heads. Contact Name: Contact Phone Number: 5202561431 Contact Email: Attachment(s) 4O187HL | NA | !! Maintenance came by to replace our A/C Filters but left top hatch open and also did not replace filters - just left hatch down. They told us they would be back but never came. This is a safety hazard for our heads. Contact Name: Contact Phone Number: 5202561431 Contact Email: Attachment(s) 4O187HL NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-01 | 4449 | WEST-106800 | HVAC-GENERAL-MU Air Filters South | 2016-09-30 - 18010 - Chad T Ball-Remove lid and inspect filter condition. Filter change not necessary at this time. - Chad T Ball | HVAC-GENERAL-MU Air Filters South 2016-09-30 - 18010 - Chad T Ball-Remove lid and inspect filter condition. Filter change not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-01 | 4450 | WEST-106799 | HVAC-GENERAL-MU Air Filters North | 2016-09-30 - 18010 - Chad T Ball-Remove lid and inspect filter condition. Filter change not necessary at this time. - Chad T Ball | HVAC-GENERAL-MU Air Filters North 2016-09-30 - 18010 - Chad T Ball-Remove lid and inspect filter condition. Filter change not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-01 | 4525 | WEST-106724 | HVAC-GENERAL-EVAP-02W | 2016-10-06 - 18010 - Alfred Rohe-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball; 2016-10-06 - 18010 - Chad T Ball-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball | HVAC-GENERAL-EVAP-02W 2016-10-06 - 18010 - Alfred Rohe-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball; 2016-10-06 - 18010 - Chad T Ball-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-01 | 4526 | WEST-106723 | HVAC-GENERAL-EVAP-01E | 2016-10-06 - 18010 - Alfred Rohe-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball; 2016-10-06 - 18010 - Chad T Ball-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball | HVAC-GENERAL-EVAP-01E 2016-10-06 - 18010 - Alfred Rohe-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball; 2016-10-06 - 18010 - Chad T Ball-Seasonal shut down of evap coolers. Shut off and temporarily disconnected water supply. Disconnected pump motor and drained basin. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-01 | 59238 | TMPE-190919 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-01 | 59239 | TMPE-190918 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-01 | 176057 | RFMT-132274 | !! Water leaking from AC unit in ceiling over bathroom sink area. Contact Name: Peter Skidmore Contact Phone Number: Contact Email: ptskidmo@asu.edu 4ND2BL1 | 2016-10-03 - 13050 - Thomas Zambrano-cleaned out pan. when you turn the unit on the water leaks around outside of pan. need Hvac tech to troubleshoot. - Thomas Zambrano | !! Water leaking from AC unit in ceiling over bathroom sink area. Contact Name: Peter Skidmore Contact Phone Number: Contact Email: ptskidmo@asu.edu 4ND2BL1 2016-10-03 - 13050 - Thomas Zambrano-cleaned out pan. when you turn the unit on the water leaks around outside of pan. need Hvac tech to troubleshoot. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-01 | 176075 | RFMT-132256 | UNOCCUPIED ROOM CHECK - SONORA 103: Please check Sonora 103 to see if carpet is dry and if there is still an odor in the room. Please close windows and change a/c filters. Thank you. | 2016-10-03 - 10010 - Mike Guckian-Checked on 103. Still stinky. Reported findings to Greg S. - Mike Guckian | UNOCCUPIED ROOM CHECK - SONORA 103: Please check Sonora 103 to see if carpet is dry and if there is still an odor in the room. Please close windows and change a/c filters. Thank you. 2016-10-03 - 10010 - Mike Guckian-Checked on 103. Still stinky. Reported findings to Greg S. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-01 | 234464 | POLY-113735 | CALL AHEAD I have a dog Brian 928-259-3822 AC pump is leaking into the master bedroom Please call Brian to schedule time 928-259-3822 Thank you Contact Name: Sarah Contact Phone Number: 5204032797 Contact Email: 4N1ANH0 | NA | CALL AHEAD I have a dog Brian 928-259-3822 AC pump is leaking into the master bedroom Please call Brian to schedule time 928-259-3822 Thank you Contact Name: Sarah Contact Phone Number: 5204032797 Contact Email: 4N1ANH0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-02 | 176026 | RFMT-132305 | !! In the bathroom, on the ceiling where the air conditioning is located, there is a small leak. Water is dripping from the ceiling slowly, can you please take a look? Thank you! Contact Name: Eddie Cervantes Rodriguez Contact Phone Number: Contact Email: Eddie.Cervantesrodriguez@asu.edu 4NJN743 | 2016-10-03 - 18010 - David Cates-Cleared AC condensation drain - David Cates | !! In the bathroom, on the ceiling where the air conditioning is located, there is a small leak. Water is dripping from the ceiling slowly, can you please take a look? Thank you! Contact Name: Eddie Cervantes Rodriguez Contact Phone Number: Contact Email: Eddie.Cervantesrodriguez@asu.edu 4NJN743 2016-10-03 - 18010 - David Cates-Cleared AC condensation drain - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-02 | 176039 | RFMT-132292 | The air conditioning in this room recently (past day) became very weak. Even set at 60/fan on/cool, a fan is necessary to keep the room cool. Any help would be greatly appreciated, thank you. 4O0C9J0 | 2016-10-03 - 18010 - John Romero-Checked out A/C unit with Thor.Everything is working like it should. Vent temp 58 degrees - John Romero | The air conditioning in this room recently (past day) became very weak. Even set at 60/fan on/cool, a fan is necessary to keep the room cool. Any help would be greatly appreciated, thank you. 4O0C9J0 2016-10-03 - 18010 - John Romero-Checked out A/C unit with Thor.Everything is working like it should. Vent temp 58 degrees - John Romero | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-02 | 215548 | RACC-113062 | !! Repeat Request. The AC unit in my room needs to be replaced. My roommates and I were told that a new unit had been ordered, but that was over 3 weeks ago. There is a temporary AC in our shared/common area. It is keeping things cool, but is extremely loud. My private room has only a fan and no AC . . . | NA | !! Repeat Request. The AC unit in my room needs to be replaced. My roommates and I were told that a new unit had been ordered, but that was over 3 weeks ago. There is a temporary AC in our shared/common area. It is keeping things cool, but is extremely loud. My private room has only a fan and no AC . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-02 | 234460 | POLY-113739 | !! Water coming up from tile in living room near AC vent. 4NN19I3 | NA | !! Water coming up from tile in living room near AC vent. 4NN19I3 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-02 | 234471 | POLY-113728 | *This was a call out on 10/2/16* A/C not working Replaced blower motor | NA | *This was a call out on 10/2/16* A/C not working Replaced blower motor NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-03 | 57492 | TMPE-192665 | MWO: !! There is a big white metal thing outside behind the CSB building and has "REYMSA" written on it. There was a big pop and a big piece of plastic flew out of it. At the same time part of the air conditioning went off in the building. 4N0J6L5 | 2016-10-03 - 18110 - CALLED TO JOHN H. - Monica Moraga; 2016-10-04 - 18110 - Carl Karr-Install temporary fans on cooling tower. - Carl Karr; 2016-10-04 - 18110 - Michael Kelley-Responded to Emergency call. Cooling tower fan shattered. - Michael Kelley; 2016-10-04 - 18110 - Michael Kelley-Repaired and upgraded temp fix on fans. - Michael Kelley; 2016-10-05 - 18110 - 10/4/2016 1.5CE 5am-6:30am Michael Kelley - CSB Emergency repair to cooling tower. Tempe Crane help remove a motor form tower. - Kerri Perkins; 2016-10-05 - 18110 - 10/3/2016 3.5 CE 3pm-6:30pm Micheal Kelley - CSB Emergency repair of cooling tower. - Kerri Perkins; 2016-10-06 - 18110 - Robert Dauscher-Layout for frame pick up material start cutting .material - William Zimmer; 2016-10-06 - 18110 - Robert Dauscher- Weld up frame install sheet metal and install on tower. - William Zimmer | MWO: !! There is a big white metal thing outside behind the CSB building and has "REYMSA" written on it. There was a big pop and a big piece of plastic flew out of it. At the same time part of the air conditioning went off in the building. 4N0J6L5 2016-10-03 - 18110 - CALLED TO JOHN H. - Monica Moraga; 2016-10-04 - 18110 - Carl Karr-Install temporary fans on cooling tower. - Carl Karr; 2016-10-04 - 18110 - Michael Kelley-Responded to Emergency call. Cooling tower fan shattered. - Michael Kelley; 2016-10-04 - 18110 - Michael Kelley-Repaired and upgraded temp fix on fans. - Michael Kelley; 2016-10-05 - 18110 - 10/4/2016 1.5CE 5am-6:30am Michael Kelley - CSB Emergency repair to cooling tower. Tempe Crane help remove a motor form tower. - Kerri Perkins; 2016-10-05 - 18110 - 10/3/2016 3.5 CE 3pm-6:30pm Micheal Kelley - CSB Emergency repair of cooling tower. - Kerri Perkins; 2016-10-06 - 18110 - Robert Dauscher-Layout for frame pick up material start cutting .material - William Zimmer; 2016-10-06 - 18110 - Robert Dauscher- Weld up frame install sheet metal and install on tower. - William Zimmer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-03 | 57494 | TMPE-192663 | MWO: Please create a WO for HVAC shop to investigate why the Trane package unit needs to be reset to cool space. I noticed one condenser fan is frozen but the other 2 operate and cool fine. Customer complaint for 2nd time need to eliminate safety trip if possible. I have removed schedule for n. . . | 2016-10-05 - 18010 - Thomas Gibble-Found condenser fan motor burned out. Trip to Trane Tempe for motor and ARS Phx. for fan blade. Trip to Warehouse for belts. Installed all parts; run test; COMPLETE. - Gail Jackson; 2016-10-05 - 18010 - Gail Jackson-Found condenser fan motor burned out. Trip to Trane Tempe for motor and ARS Phx. for fan blade. Trip to Warehouse for belts. Installed all parts; run test; COMPLETE. - Gail Jackson | MWO: Please create a WO for HVAC shop to investigate why the Trane package unit needs to be reset to cool space. I noticed one condenser fan is frozen but the other 2 operate and cool fine. Customer complaint for 2nd time need to eliminate safety trip if possible. I have removed schedule for n. . . 2016-10-05 - 18010 - Thomas Gibble-Found condenser fan motor burned out. Trip to Trane Tempe for motor and ARS Phx. for fan blade. Trip to Warehouse for belts. Installed all parts; run test; COMPLETE. - Gail Jackson; 2016-10-05 - 18010 - Gail Jackson-Found condenser fan motor burned out. Trip to Trane Tempe for motor and ARS Phx. for fan blade. Trip to Warehouse for belts. Installed all parts; run test; COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-03 | 57562 | TMPE-192595 | MWO: BA 390 Every Monday morning the a/c doesn't seem to work and the room is always very hot. We had to move to a different room this morning because it was just unbearable. Please adjust the temperature for the next class and please make sure we don't continue to have this issue again next Mond. . . | 2016-10-03 - 18290 - Jeffrey Green-went to BA roof and reset Trane package unit it had tripped again one condenser fan is seized it cools OK with 2 of 3 just need it to not trip safeties called customer and created WO for HVAC shop - Jeffrey Green | MWO: BA 390 Every Monday morning the a/c doesn't seem to work and the room is always very hot. We had to move to a different room this morning because it was just unbearable. Please adjust the temperature for the next class and please make sure we don't continue to have this issue again next Mond. . . 2016-10-03 - 18290 - Jeffrey Green-went to BA roof and reset Trane package unit it had tripped again one condenser fan is seized it cools OK with 2 of 3 just need it to not trip safeties called customer and created WO for HVAC shop - Jeffrey Green | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-03 | 175956 | RFMT-132375 | P.M. - Please check Central Plant South HVAC & Mechanical Equipment after Chiller relocation is completed. Relocation project is scheduled to start Tuesday 10/03/16. Note and report findings as appropriate. Thank you. | 2016-10-05 - 18010 - Thor Millsaps-Checked mechanical room. Trane chiller from Cholla has been set on far east concrete pad. No connections have been made to chiller. Chiller is in place and secure. Blocks have been removed from exterior wall left of double door presumably to enlarge opening so chiller could be brought into building. Blocks are lying on the ground and have not been put back into place. Reset refrigerant alarm. Chiller #1 warning- motor bearing lube suggested. - Thor Millsaps | P.M. - Please check Central Plant South HVAC & Mechanical Equipment after Chiller relocation is completed. Relocation project is scheduled to start Tuesday 10/03/16. Note and report findings as appropriate. Thank you. 2016-10-05 - 18010 - Thor Millsaps-Checked mechanical room. Trane chiller from Cholla has been set on far east concrete pad. No connections have been made to chiller. Chiller is in place and secure. Blocks have been removed from exterior wall left of double door presumably to enlarge opening so chiller could be brought into building. Blocks are lying on the ground and have not been put back into place. Reset refrigerant alarm. Chiller #1 warning- motor bearing lube suggested. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 6
2016-10-03 | 175965 | RFMT-132366 | Please check fan coil unit in Sonora 103. We have notice an odor in the room and have not been able to resolve. Please check fan coil unit to insure proper operation and clean. Thank you. | 2016-10-04 - 18010 - Thor Millsaps-Checked fan coil, checked duct work, checked drain traps. Could not locate odor. Did not notice strong odor in room. - Thor Millsaps | Please check fan coil unit in Sonora 103. We have notice an odor in the room and have not been able to resolve. Please check fan coil unit to insure proper operation and clean. Thank you. 2016-10-04 - 18010 - Thor Millsaps-Checked fan coil, checked duct work, checked drain traps. Could not locate odor. Did not notice strong odor in room. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-10-03 | 175972 | RFMT-132359 | !! There was someone working on my ac unit and he said if I continued to have issues with it then it's going to need a new motor. Could you please have the ac repaired? Submitted by 4NID637 | NA | !! There was someone working on my ac unit and he said if I continued to have issues with it then it's going to need a new motor. Could you please have the ac repaired? Submitted by 4NID637 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-03 | 176008 | RFMT-132323 | !! need a air filter change, 4O021N2 | 2016-10-03 - 18010 - Casey Faultner-Replaced A/C Filter 16X25X1 - Casey Faultner | !! need a air filter change, 4O021N2 2016-10-03 - 18010 - Casey Faultner-Replaced A/C Filter 16X25X1 - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-03 | 255789 | DTPC-112749 | Air Compressor | 2016-10-11 - 18030 - Bruce Pickford-PMs amp and volt reads,checked belts, and oil level, blew tank - Keith Griffin | Air Compressor 2016-10-11 - 18030 - Bruce Pickford-PMs amp and volt reads,checked belts, and oil level, blew tank - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-04 | 57231 | TMPE-192926 | MWO: ASUHC-Agent Jesse Tannous Description Originally Jennifer Moyer called this in stating she was working on a job but could no longer stay and requested HVAC out. She provided the request number 191633, which upon looking it up did not seem to relate to the issue she reported. She explained t. . . | 2016-10-06 - 18010 - Duane Rider-Troubleshoot unit,, found leak tighted line, charge with R-410A. Condensing fan motor needs replaced. - Duane Rider; 2016-10-06 - 18010 - Duane Rider-Rechecked unit for refrigerant leaks. no leaks found. ultra sonic leak detector used. - Duane Rider; 2016-10-10 - 18010 - 10/4/2016 3.5OT 6:30pm-10pm Duane Rider - INTDS A - Kerri Perkins; 2017-01-09 - 18010 - Duane Rider-Closed work order - Duane Rider | MWO: ASUHC-Agent Jesse Tannous Description Originally Jennifer Moyer called this in stating she was working on a job but could no longer stay and requested HVAC out. She provided the request number 191633, which upon looking it up did not seem to relate to the issue she reported. She explained t. . . 2016-10-06 - 18010 - Duane Rider-Troubleshoot unit,, found leak tighted line, charge with R-410A. Condensing fan motor needs replaced. - Duane Rider; 2016-10-06 - 18010 - Duane Rider-Rechecked unit for refrigerant leaks. no leaks found. ultra sonic leak detector used. - Duane Rider; 2016-10-10 - 18010 - 10/4/2016 3.5OT 6:30pm-10pm Duane Rider - INTDS A - Kerri Perkins; 2017-01-09 - 18010 - Duane Rider-Closed work order - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-04 | 57253 | TMPE-192904 | MWO CNTRPT 421BA There is an Air handler unit making a loud buzzing sound in the area of 421 BA. HAVC department. 4NM9B6B | 2017-02-17 - 18050 - Mitchell Andrews-replaced the blower motor in the unit used the last motor we had in stock for the building - Mitchell Andrews | MWO CNTRPT 421BA There is an Air handler unit making a loud buzzing sound in the area of 421 BA. HAVC department. 4NM9B6B 2017-02-17 - 18050 - Mitchell Andrews-replaced the blower motor in the unit used the last motor we had in stock for the building - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-04 | 57266 | TMPE-192891 | MWO: Create WO for HVAC shop to look at heat pump for this space setpt was turned down to 74 it is 81 deg F the unit is serves Jack Hsu's office (356) It is much too hot His office is located in the area 351on the third floor. 4N00ABB | 2016-10-17 - 18290 - Roque Garcia-The Novar tstat was removed and it reset the unit. It started working and notified occupant of status. - Roque Garcia | MWO: Create WO for HVAC shop to look at heat pump for this space setpt was turned down to 74 it is 81 deg F the unit is serves Jack Hsu's office (356) It is much too hot His office is located in the area 351on the third floor. 4N00ABB 2016-10-17 - 18290 - Roque Garcia-The Novar tstat was removed and it reset the unit. It started working and notified occupant of status. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-04 | 57270 | TMPE-192887 | MWO: Solvent exhaust fan 2 Y#2730, located under grading on upper roof has cracked and broken belts that need to be replaced. Send to HVAC services. For more info contact Mike Cozens 480-330-3235. 42B213C | 2016-10-05 - 18060 - Derek Gittings-replaced 3 belts and realigned. - Jennifer Moyer | MWO: Solvent exhaust fan 2 Y#2730, located under grading on upper roof has cracked and broken belts that need to be replaced. Send to HVAC services. For more info contact Mike Cozens 480-330-3235. 42B213C 2016-10-05 - 18060 - Derek Gittings-replaced 3 belts and realigned. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-10-04 | 57287 | TMPE-192870 | MWO: The a/c fan in the drawing studio Room 401 is making a very loud noise when it runs. (This is the fan that blows the air from the ceiling vents.) This is not typical and it is disruptive to the class. Can you please have someone take a look at it. Thank you. Contact Name: Contact Pho. . . | 2016-11-03 - 18010 - Gail Jackson-No excessive noise found at this time. - Gail Jackson | MWO: The a/c fan in the drawing studio Room 401 is making a very loud noise when it runs. (This is the fan that blows the air from the ceiling vents.) This is not typical and it is disruptive to the class. Can you please have someone take a look at it. Thank you. Contact Name: Contact Pho. . . 2016-11-03 - 18010 - Gail Jackson-No excessive noise found at this time. - Gail Jackson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-04 | 57289 | TMPE-192868 | MWO MUSIC EB3-85 *TRANSFER* PL to HVAC check all the Pump Lids in this area. May help with getting rid of the smell. ORIG REQUEST !! Repeat Request. From my boss Brian DeMaris, What can we do about the horrid sewer smell on EB3? It's gotten worse the past couple weeks, and now it's so wretched. . . | 2016-10-07 - 18020 - Michael Kelley-Discovered that the inspection plates on the ejector were not sealed. Cleaned room. Removed old silicone. Scraped, sanded &amp; cleaned Put 7 tubes of silicone on plate. Put a rubber gasket under inspection plate. - Michael Kelley; 2016-10-07 - 18020 - Michael Kelley-Inspected job. Found no smell. Contacted Linda Bennett at Music- 480-965-2856. Explained the fix and to please follow up if there was any more problems. - Michael Kelley | MWO MUSIC EB3-85 *TRANSFER* PL to HVAC check all the Pump Lids in this area. May help with getting rid of the smell. ORIG REQUEST !! Repeat Request. From my boss Brian DeMaris, What can we do about the horrid sewer smell on EB3? It's gotten worse the past couple weeks, and now it's so wretched. . . 2016-10-07 - 18020 - Michael Kelley-Discovered that the inspection plates on the ejector were not sealed. Cleaned room. Removed old silicone. Scraped, sanded &amp; cleaned Put 7 tubes of silicone on plate. Put a rubber gasket under inspection plate. - Michael Kelley; 2016-10-07 - 18020 - Michael Kelley-Inspected job. Found no smell. Contacted Linda Bennett at Music- 480-965-2856. Explained the fix and to please follow up if there was any more problems. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-04 | 57293 | TMPE-192864 | The motor is seized on the exhaust fan. Motor data: HP 1/4; 120v; 1725 rpm; FR48 | 2017-02-27 - 18230 - Wire needs replaced on switch connecting to motor. Management created work order for electrician to replace. Raining today, and I have training Feb. 28, Mar.1, and Mar. 2. Job is Routine maintenance to occur thereafter. - Jennifer Moyer; 2017-02-27 - 18230 - Jennifer Moyer-repair arrangements made. - Jennifer Moyer; 2017-05-01 - 18230 - Electrician replaced crusty wire and I removed the old motor and purchased a new motor for installation. - Jennifer Moyer; 2017-05-08 - 18230 - Jennifer Moyer-Installed two new sheaves and a new motor. - Jennifer Moyer; 2017-05-08 - 18230 - Austen Jackson-Installed two new sheaves and a new motor. - Jennifer Moyer | The motor is seized on the exhaust fan. Motor data: HP 1/4; 120v; 1725 rpm; FR48 2017-02-27 - 18230 - Wire needs replaced on switch connecting to motor. Management created work order for electrician to replace. Raining today, and I have training Feb. 28, Mar.1, and Mar. 2. Job is Routine maintenance to occur thereafter. - Jennifer Moyer; 2017-02-27 - 18230 - Jennifer Moyer-repair arrangements made. - Jennifer Moyer; 2017-05-01 - 18230 - Electrician replaced crusty wire and I removed the old motor and purchased a new motor for installation. - Jennifer Moyer; 2017-05-08 - 18230 - Jennifer Moyer-Installed two new sheaves and a new motor. - Jennifer Moyer; 2017-05-08 - 18230 - Austen Jackson-Installed two new sheaves and a new motor. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-04 | 57320 | TMPE-192837 | MWO: GWC - 627: Hello, I was just told that our cold room in GWC is not working again. As always, this is affects our ability to do research significantly. Can you please send someone to take a look and fix the problem? Thanks much, Kaushal 07.28.16 Cold Room (Growth Chamber) . . . | 2016-10-04 - 18300 - Called out to John - Amanda Thomas; 2016-10-18 - 18300 - Robert Ecabert-Started to troubleshoot growth chamber. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert- found unit out of refrigerant while troubleshooting due to a cracked vibration elimanator on the discharge line. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz- found unit out of refrigerant while troubleshooting due to a cracked vibration elimanator on the discharge line. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Installed a new discharge line vibration and a new suction line vibration elimanator. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Installed a new discharge line vibration and a new suction line vibration elimanator. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Installed new liquid line drier. Leak checked unit with nitrogen and I found no leaks. I then put the unit in a vacuum down to 400 microns. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Installed new liquid line drier. Leak checked unit with nitrogen and I found no leaks. I then put the unit in a vacuum down to 400 microns. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Charged unit with 7.0 lbs of R-409a refrigerant from refrigerant drum RSD111016-01.Also installed a new actuator drive motor and a solid state drive. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Charged unit with 7.0 lbs of R-409a refrigerant from refrigerant drum RSD111016-01.Also installed a new actuator drive motor and a solid state drive. - Robert Ecabert | MWO: GWC - 627: Hello, I was just told that our cold room in GWC is not working again. As always, this is affects our ability to do research significantly. Can you please send someone to take a look and fix the problem? Thanks much, Kaushal 07.28.16 Cold Room (Growth Chamber) . . . 2016-10-04 - 18300 - Called out to John - Amanda Thomas; 2016-10-18 - 18300 - Robert Ecabert-Started to troubleshoot growth chamber. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert- found unit out of refrigerant while troubleshooting due to a cracked vibration elimanator on the discharge line. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz- found unit out of refrigerant while troubleshooting due to a cracked vibration elimanator on the discharge line. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Installed a new discharge line vibration and a new suction line vibration elimanator. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Installed a new discharge line vibration and a new suction line vibration elimanator. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Installed new liquid line drier. Leak checked unit with nitrogen and I found no leaks. I then put the unit in a vacuum down to 400 microns. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Installed new liquid line drier. Leak checked unit with nitrogen and I found no leaks. I then put the unit in a vacuum down to 400 microns. - Robert Ecabert; 2016-10-18 - 18300 - Oner Munoz-Charged unit with 7.0 lbs of R-409a refrigerant from refrigerant drum RSD111016-01.Also installed a new actuator drive motor and a solid state drive. - Robert Ecabert; 2016-10-18 - 18300 - Robert Ecabert-Charged unit with 7.0 lbs of R-409a refrigerant from refrigerant drum RSD111016-01.Also installed a new actuator drive motor and a solid state drive. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-04 | 57401 | TMPE-192756 | SWO: MANZY CAFE The freezer is malfunctioning. Please send someone right away to check it out. | 2016-10-04 - 18180 - CALLED TO JOHN H. - Monica Moraga; 2016-10-04 - 18180 - Thomas Gibble-Found 1 evap fan motor with wires shorted out. Trip to Johnstone for replacement. Removed and replaced fan motor, run test, check condensing unit on roof. - Gail Jackson; 2016-10-04 - 18180 - Gail Jackson-Found 1 evap fan motor with wires shorted out. Trip to Johnstone for replacement. Removed and replaced fan motor, run test, check condensing unit on roof. - Gail Jackson; 2016-10-06 - 18180 - REOPENED WORK ORDER. CUSTOMER CALLED AND SAID THE FREEZER IS RUNNING WARMER THAN IT SHOULD BE. CALLED TO JOHN H. MM - Monica Moraga; 2016-10-11 - 18180 - Thomas Gibble-replaced evap fan and LL value. - Thomas Gibble; 2016-10-11 - 18180 - Gail Jackson-replaced evap fan and LL value. - Thomas Gibble | SWO: MANZY CAFE The freezer is malfunctioning. Please send someone right away to check it out. 2016-10-04 - 18180 - CALLED TO JOHN H. - Monica Moraga; 2016-10-04 - 18180 - Thomas Gibble-Found 1 evap fan motor with wires shorted out. Trip to Johnstone for replacement. Removed and replaced fan motor, run test, check condensing unit on roof. - Gail Jackson; 2016-10-04 - 18180 - Gail Jackson-Found 1 evap fan motor with wires shorted out. Trip to Johnstone for replacement. Removed and replaced fan motor, run test, check condensing unit on roof. - Gail Jackson; 2016-10-06 - 18180 - REOPENED WORK ORDER. CUSTOMER CALLED AND SAID THE FREEZER IS RUNNING WARMER THAN IT SHOULD BE. CALLED TO JOHN H. MM - Monica Moraga; 2016-10-11 - 18180 - Thomas Gibble-replaced evap fan and LL value. - Thomas Gibble; 2016-10-11 - 18180 - Gail Jackson-replaced evap fan and LL value. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-04 | 234417 | POLY-113782 | Please check the ventilation system for the Ironwood Building, in particular Room 110. Allergies flare up when we are in the building and go away when we are not. The air filters may need to be changed. 42AEI79 | NA | Please check the ventilation system for the Ironwood Building, in particular Room 110. Allergies flare up when we are in the building and go away when we are not. The air filters may need to be changed. 42AEI79 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-05 | 57085 | TMPE-193072 | MWO LSA L1-61A !! Fume Hood # 10557 in LSA L1-61A is not working and is turned off. Please look at unit and determine why the fume hood is off and provide EH&S a date when then fume hood will be turned on. Thanks. 42C6AFK | 2016-10-26 - 18190 - John Holloway-Hood is located in 61A but the on/off is located in 61B Verified fan operation spoke to occupant - John Holloway | MWO LSA L1-61A !! Fume Hood # 10557 in LSA L1-61A is not working and is turned off. Please look at unit and determine why the fume hood is off and provide EH&S a date when then fume hood will be turned on. Thanks. 42C6AFK 2016-10-26 - 18190 - John Holloway-Hood is located in 61A but the on/off is located in 61B Verified fan operation spoke to occupant - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-05 | 57111 | TMPE-193046 | MWO TOWERA A202 HVAC There are two issues, both of which I spoke to John Howell about. In room A202 there a piece of flex duct that is unattached and blowing into the area above the drop ceiling. In room A204 there is not air. The room is hot or cold depending on the season. I ha. . . | 2016-10-07 - 18010 - Carl Karr-Locate open duct in ceiling, needs end cap. - Carl Karr; 2016-10-10 - 18010 - Carl Karr-Repaired duct in room a204. Started a/h #4 for room a202. May want to check amp draw on motor,and motor heaters. - Carl Karr | MWO TOWERA A202 HVAC There are two issues, both of which I spoke to John Howell about. In room A202 there a piece of flex duct that is unattached and blowing into the area above the drop ceiling. In room A204 there is not air. The room is hot or cold depending on the season. I ha. . . 2016-10-07 - 18010 - Carl Karr-Locate open duct in ceiling, needs end cap. - Carl Karr; 2016-10-10 - 18010 - Carl Karr-Repaired duct in room a204. Started a/h #4 for room a202. May want to check amp draw on motor,and motor heaters. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-10-05 | 57127 | TMPE-193030 | MWO: PSF 74 There is a lot of vibration in the room and black particles are coming out. Please contact Garrett asap. | 2016-11-26 - 18010 - Roque Garcia-Replaced both pillar block bearings and the noise subsided and left a note with faculty member located in the space. - Roque Garcia | MWO: PSF 74 There is a lot of vibration in the room and black particles are coming out. Please contact Garrett asap. 2016-11-26 - 18010 - Roque Garcia-Replaced both pillar block bearings and the noise subsided and left a note with faculty member located in the space. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-10-05 | 57211 | TMPE-192946 | MWO: LSD - Aquatic Terrestrial: This unit has 3 fans. Now that we\\u2019ve replaced the first one and then had to call you out to replace the second one, the third fan is now going out and needs replaced asap. | 2016-10-18 - 18010 - Gail Jackson-check operation - Gail Jackson; 2016-10-18 - 18010 - Thomas Gibble-check operation - Gail Jackson | MWO: LSD - Aquatic Terrestrial: This unit has 3 fans. Now that we\\u2019ve replaced the first one and then had to call you out to replace the second one, the third fan is now going out and needs replaced asap. 2016-10-18 - 18010 - Gail Jackson-check operation - Gail Jackson; 2016-10-18 - 18010 - Thomas Gibble-check operation - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-05 | 57212 | TMPE-192945 | MWO Coor - 6677 - 6682: The ceiling appears to be leaking above the hallway door between rooms 6677 and 6682. It doesn't seem urgent, but I wanted to let you know in order to avoid a larger problem. | 2016-10-05 - 23000 - Donald Crowe-transfer to HVAC water is dripping from check valve on water line going to air conditioning unit materials transfer to HVAC water is dripping from check valve fitting going to air conditioning unit. materials:none - Donald Crowe | MWO Coor - 6677 - 6682: The ceiling appears to be leaking above the hallway door between rooms 6677 and 6682. It doesn't seem urgent, but I wanted to let you know in order to avoid a larger problem. 2016-10-05 - 23000 - Donald Crowe-transfer to HVAC water is dripping from check valve on water line going to air conditioning unit materials transfer to HVAC water is dripping from check valve fitting going to air conditioning unit. materials:none - Donald Crowe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-10-05 | 57224 | TMPE-192933 | SWO: MU - Main Kitchen: Please create a work order to replace several missing ceiling tiles in the bakery and the kitchen area in the main kitchen of the MU Please have 4 ceiling tiles replaced in room 95 as they were soiled from a water leak Charge this to ARAMARK Gn7 | 2016-11-01 - 13050 - Joel Hansen- Started on MU95 replaced 4 tiles and water still leaking Stopped replacing more and removed several more and cleaned mess up looked for and found Jim E He had me show Ivan Ivan says its condensate coming off the 6 freon lines to the coolers above I found a rotted cast iron 90 above 2nd cooler @ column which handles a floor drain on Engrained's patio I put a trash can sign on in front of Devil's Greens per Jim E I sent pics to Ivan and Jim E of rotted 90 - Joel Hansen; 2016-11-14 - 13050 - Joel Hansen-Checked job Got Po for 755B's and had ordered Tried to start job - Joel Hansen; 2016-12-13 - 13050 - Joel Hansen-I had Duct hangers made and I installed them per Jim E to keep ducts off grid in MU95 I also let Jim E in on my idea to put a condensation pan under the 6 condensate lines coming from the coolers in the dock area above - Joel Hansen; 2016-12-15 - 13050 - Joel Hansen-Jim E okayed me replacing a ceiling tile behind a register in Einsteins and using work order# 196457 This tile appeared to be falling and was a hazard It needs a new 4' tee as well I did not have time as it was getting really busy so I got a grid wire and wired up the 4' tee to alleviate safety issues - Joel Hansen; 2017-01-17 - 13050 - Joel Hansen-Emailed Jim Emmons about the possibility of putting condensation pan under 6 refrigerant lines to keep grid from getting soaked regularly due to insulation issues Closed out work order as no activity - Joel Hansen | SWO: MU - Main Kitchen: Please create a work order to replace several missing ceiling tiles in the bakery and the kitchen area in the main kitchen of the MU Please have 4 ceiling tiles replaced in room 95 as they were soiled from a water leak Charge this to ARAMARK Gn7 2016-11-01 - 13050 - Joel Hansen- Started on MU95 replaced 4 tiles and water still leaking Stopped replacing more and removed several more and cleaned mess up looked for and found Jim E He had me show Ivan Ivan says its condensate coming off the 6 freon lines to the coolers above I found a rotted cast iron 90 above 2nd cooler @ column which handles a floor drain on Engrained's patio I put a trash can sign on in front of Devil's Greens per Jim E I sent pics to Ivan and Jim E of rotted 90 - Joel Hansen; 2016-11-14 - 13050 - Joel Hansen-Checked job Got Po for 755B's and had ordered Tried to start job - Joel Hansen; 2016-12-13 - 13050 - Joel Hansen-I had Duct hangers made and I installed them per Jim E to keep ducts off grid in MU95 I also let Jim E in on my idea to put a condensation pan under the 6 condensate lines coming from the coolers in the dock area above - Joel Hansen; 2016-12-15 - 13050 - Joel Hansen-Jim E okayed me replacing a ceiling tile behind a register in Einsteins and using work order# 196457 This tile appeared to be falling and was a hazard It needs a new 4' tee as well I did not have time as it was getting really busy so I got a grid wire and wired up the 4' tee to alleviate safety issues - Joel Hansen; 2017-01-17 - 13050 - Joel Hansen-Emailed Jim Emmons about the possibility of putting condensation pan under 6 refrigerant lines to keep grid from getting soaked regularly due to insulation issues Closed out work order as no activity - Joel Hansen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2016-10-05 | 57230 | TMPE-192927 | MWO: HVAC 1st call local control dx unit. PEBW - 240: This should now be one of many complaints, from multiple people, who include faculty members, staff (me), and most likely students. PEBW 240 is a ballet studio, a room with windows that do not open and a door that sounds an alarm when kept . . . | 2016-11-04 - 18290 - Robert Dauscher-Units share transformer between two units. A low voltage ground somewhere in one of the two units heating sides caused transformer to trip its breaker immediately. Removed wire from board inside unit with transformer to allow unit operation. Call finished by another tech - Robert Dauscher | MWO: HVAC 1st call local control dx unit. PEBW - 240: This should now be one of many complaints, from multiple people, who include faculty members, staff (me), and most likely students. PEBW 240 is a ballet studio, a room with windows that do not open and a door that sounds an alarm when kept . . . 2016-11-04 - 18290 - Robert Dauscher-Units share transformer between two units. A low voltage ground somewhere in one of the two units heating sides caused transformer to trip its breaker immediately. Removed wire from board inside unit with transformer to allow unit operation. Call finished by another tech - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-05 | 175840 | RFMT-132491 | !! AC is broken! 4NM1EC6 | 2016-10-06 - 18010 - Thor Millsaps-Replaced compressor, liquid line filter/dryer, charged with 6 lbs R-22. System up and running. Compressor part # H22J293ABCA Compressor serial #21016073709. Compressor not in TMA. - Thor Millsaps | !! AC is broken! 4NM1EC6 2016-10-06 - 18010 - Thor Millsaps-Replaced compressor, liquid line filter/dryer, charged with 6 lbs R-22. System up and running. Compressor part # H22J293ABCA Compressor serial #21016073709. Compressor not in TMA. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-10-05 | 175878 | RFMT-132453 | RES LIFE / Thor: Please check operation of west end ceiling a/c unit | 2016-10-05 - 18010 - Thor Millsaps-Reattached cool actuator to base. Tightened heat actuator to valve shaft. Both actuators working properly. - Thor Millsaps | RES LIFE / Thor: Please check operation of west end ceiling a/c unit 2016-10-05 - 18010 - Thor Millsaps-Reattached cool actuator to base. Tightened heat actuator to valve shaft. Both actuators working properly. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-10-05 | 175891 | RFMT-132440 | !! To fix the A/C because it does not work as it should, it gets a really humid feeling in this dorm during the day and that feels very uncomfortable, so my request is to have someone come figure out the problem A/C Contact Name: Contact Phone Number: 9282745854 Contact Email: 4NOF7I5 | 2016-10-05 - 18010 - Thomas Zambrano-flushed unit and wrap pipes. temperatures is 62\\xb0 now. the top chiller valve has a broken handle anddd there is on'y one flush valve which is a hose bib.the hose bib get clogged with debris when flushing which is why we should install full port ball vaves. Need hvac techs to blow the lines out and replace valve, ive done all i could do.temps are usally around 57\\xb0. - Thomas Zambrano | !! To fix the A/C because it does not work as it should, it gets a really humid feeling in this dorm during the day and that feels very uncomfortable, so my request is to have someone come figure out the problem A/C Contact Name: Contact Phone Number: 9282745854 Contact Email: 4NOF7I5 2016-10-05 - 18010 - Thomas Zambrano-flushed unit and wrap pipes. temperatures is 62\\xb0 now. the top chiller valve has a broken handle anddd there is on'y one flush valve which is a hose bib.the hose bib get clogged with debris when flushing which is why we should install full port ball vaves. Need hvac techs to blow the lines out and replace valve, ive done all i could do.temps are usally around 57\\xb0. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 4
2016-10-05 | 234352 | POLY-113847 | replace motor in fan coil 4O216EO | NA | replace motor in fan coil 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-06 | 4217 | WEST-107032 | The filtered water dispenser on the 3rd floor of UCB is not working and has not been working since the summer. It appears as though the fountain part work, yet the dispenser for filling water bottles does not work. | 2016-10-07 - 23080 - Tim Jowers-tested the power board and found that the transformer is not putting out any voltage. talked with stores and we are checking on a new bottle filler electronics kit. - Tim Jowers; 2016-10-07 - 23080 - Joseph Danielek-tested the circuit boards. - Tim Jowers; 2016-10-13 - 23080 - Tim Jowers-gave the salesman the info from the bottle filler he contacted the parts dept. about replacement./ warranty. - Tim Jowers; 2016-10-21 - 23080 - Tim Jowers-the Elkay corp. is sending out a replacement bottle filler as a warranty item. The unit should ship in 5 to 10 days - Tim Jowers; 2016-11-03 - 23080 - Tim Jowers-installed the new circuit boards and the fountain works properly. - Tim Jowers | The filtered water dispenser on the 3rd floor of UCB is not working and has not been working since the summer. It appears as though the fountain part work, yet the dispenser for filling water bottles does not work. 2016-10-07 - 23080 - Tim Jowers-tested the power board and found that the transformer is not putting out any voltage. talked with stores and we are checking on a new bottle filler electronics kit. - Tim Jowers; 2016-10-07 - 23080 - Joseph Danielek-tested the circuit boards. - Tim Jowers; 2016-10-13 - 23080 - Tim Jowers-gave the salesman the info from the bottle filler he contacted the parts dept. about replacement./ warranty. - Tim Jowers; 2016-10-21 - 23080 - Tim Jowers-the Elkay corp. is sending out a replacement bottle filler as a warranty item. The unit should ship in 5 to 10 days - Tim Jowers; 2016-11-03 - 23080 - Tim Jowers-installed the new circuit boards and the fountain works properly. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-06 | 56920 | TMPE-193237 | WD- comfort systems completed the work valve not working properly - needs repair or replace | NA | WD- comfort systems completed the work valve not working properly - needs repair or replace NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-10-06 | 56923 | TMPE-193234 | WD- comfort systems completed the work valve not working properly - needs repair or replace | NA | WD- comfort systems completed the work valve not working properly - needs repair or replace NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-10-06 | 56926 | TMPE-193231 | WD- comfort systems completed the work valve not working properly - needs repair or replace | NA | WD- comfort systems completed the work valve not working properly - needs repair or replace NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-10-06 | 56949 | TMPE-193208 | MWO GHALL 147 HVAC-The A/C in this room is not working correctly. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 | 2016-11-14 - 18290 - Carl Karr-Fabricate cover for ac unit. - Carl Karr; 2016-11-22 - 18290 - Jennifer Moyer-This A/C unit was completely clogged. It was disassembled and cleaned. The motor is showing signs of distress and needs to be changed. - Jennifer Moyer [Modified: 2016-11-22 Jennifer Moyer]; 2016-11-28 - 18290 - Jennifer Moyer-Ordered motor. - Jennifer Moyer; 2016-11-29 - 18290 - Jennifer Moyer-Check on status of motor order. - Jennifer Moyer; 2016-12-21 - 18290 - Jennifer Moyer-Replaced motor and transformer. - Jennifer Moyer; 2016-12-21 - 18290 - Zhi Yu-Replaced motor and transformer. - Jennifer Moyer | MWO GHALL 147 HVAC-The A/C in this room is not working correctly. Can someone please be sent out to take a look at this? Thank you. 4O25GF6 2016-11-14 - 18290 - Carl Karr-Fabricate cover for ac unit. - Carl Karr; 2016-11-22 - 18290 - Jennifer Moyer-This A/C unit was completely clogged. It was disassembled and cleaned. The motor is showing signs of distress and needs to be changed. - Jennifer Moyer [Modified: 2016-11-22 Jennifer Moyer]; 2016-11-28 - 18290 - Jennifer Moyer-Ordered motor. - Jennifer Moyer; 2016-11-29 - 18290 - Jennifer Moyer-Check on status of motor order. - Jennifer Moyer; 2016-12-21 - 18290 - Jennifer Moyer-Replaced motor and transformer. - Jennifer Moyer; 2016-12-21 - 18290 - Zhi Yu-Replaced motor and transformer. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-06 | 56955 | TMPE-193202 | MWO: !! The air conditioning is perpetually broken in the dance studios. This is unsafe for dancers, so please fix ASAP. P.S. I'm not sure which circulation area is broken, so I just chose one from the dropdown menu in order to submit the request. The unit I selected may not actually be the o. . . | 2016-11-04 - 18010 - Robert Dauscher-Units share transformer between two units. A low voltage ground somewhere in one of the two units heating sides caused transformer to trip its breaker immediately. Removed wire from board inside unit with transformer to allow unit operation. Call completed by another tech. - Robert Dauscher | MWO: !! The air conditioning is perpetually broken in the dance studios. This is unsafe for dancers, so please fix ASAP. P.S. I'm not sure which circulation area is broken, so I just chose one from the dropdown menu in order to submit the request. The unit I selected may not actually be the o. . . 2016-11-04 - 18010 - Robert Dauscher-Units share transformer between two units. A low voltage ground somewhere in one of the two units heating sides caused transformer to trip its breaker immediately. Removed wire from board inside unit with transformer to allow unit operation. Call completed by another tech. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-10-06 | 56987 | TMPE-193170 | MWO: Grady - Work order for grounds Gammage Air compressor area needs to be cleaned out, vegetation cut back and cleared See pictures. | 2016-10-21 - 19000 - Dana Pomploon-Clean up the compressor area. - Rigoberto Polanco | MWO: Grady - Work order for grounds Gammage Air compressor area needs to be cleaned out, vegetation cut back and cleared See pictures. 2016-10-21 - 19000 - Dana Pomploon-Clean up the compressor area. - Rigoberto Polanco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-06 | 175792 | RFMT-132539 | The AC vent in between the sinks is leaking onto the floor. 4NNH9C0 | 2016-10-07 - 18010 - Thomas Zambrano-troubleshoot unit and found chiller lines not wrapped and pan clogged. wrap pipes and clear pan. - Thomas Zambrano | The AC vent in between the sinks is leaking onto the floor. 4NNH9C0 2016-10-07 - 18010 - Thomas Zambrano-troubleshoot unit and found chiller lines not wrapped and pan clogged. wrap pipes and clear pan. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-06 | 175800 | RFMT-132531 | Delivered 2 portable air conditioner units to H208 & H210 | 2016-10-06 - 18010 - Joe Swan-installed portable to room - Joe Swan | Delivered 2 portable air conditioner units to H208 & H210 2016-10-06 - 18010 - Joe Swan-installed portable to room - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-06 | 175803 | RFMT-132528 | !! We would appreciate a new filter for our A/C. It is covered in dust. Thank you. 4O11MHC | 2016-10-07 - 18170 - Casey Faultner-Replaced A/C Filter. 1- 12X16 - Casey Faultner | !! We would appreciate a new filter for our A/C. It is covered in dust. Thank you. 4O11MHC 2016-10-07 - 18170 - Casey Faultner-Replaced A/C Filter. 1- 12X16 - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-06 | 215403 | RACC-113207 | The main air conditioning unit in the quad makes a knocking noise when the thermostat is on. 4O003L9 | NA | The main air conditioning unit in the quad makes a knocking noise when the thermostat is on. 4O003L9 NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-06 | 215411 | RACC-113199 | AC filter needs changing, the filter was left outside the room but wasn't changed. | NA | AC filter needs changing, the filter was left outside the room but wasn't changed. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-06 | 234286 | POLY-113913 | AC is not working. It feels like the heat is on in all the little offices within Centre 160. | 2016-10-11 - 18290 - Steve Clark-10/6 - Per Steve, the problem was due to the chiller being repaired. - Gayle Swenson | AC is not working. It feels like the heat is on in all the little offices within Centre 160. 2016-10-11 - 18290 - Steve Clark-10/6 - Per Steve, the problem was due to the chiller being repaired. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-07 | 56850 | TMPE-193307 | The motor has been removed from the exhaust fan. | 2016-10-21 - 18230 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced motor - Thomas Gibble | The motor has been removed from the exhaust fan. 2016-10-21 - 18230 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced motor - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-07 | 56853 | TMPE-193304 | SPECIAL FUNDING: replace the REYMSA cooling tower fan. | 2016-10-18 - 18110 - Michael Kelley-closing carl ticket on my t.m.a. - Kenneth Kamptner; 2016-11-09 - 18110 - Michael Kelley-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Midhat Mukanovic-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Roque Garcia-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Michael Kelley-Put together fan motor electrical, grease lines - Michael Kelley; 2016-11-09 - 18110 - Midhat Mukanovic-Put together fan motor electrical, grease lines - Michael Kelley; 2016-11-09 - 18110 - Roque Garcia-Put together fan motor electrical, grease lines - Michael Kelley | SPECIAL FUNDING: replace the REYMSA cooling tower fan. 2016-10-18 - 18110 - Michael Kelley-closing carl ticket on my t.m.a. - Kenneth Kamptner; 2016-11-09 - 18110 - Michael Kelley-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Midhat Mukanovic-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Roque Garcia-Tempe Crane Pulled temp fan wall. Pulled Colling Replaced Temp. fans Returned Colling to shop. Secure Temp. Fan to Tower - Michael Kelley; 2016-11-09 - 18110 - Michael Kelley-Put together fan motor electrical, grease lines - Michael Kelley; 2016-11-09 - 18110 - Midhat Mukanovic-Put together fan motor electrical, grease lines - Michael Kelley; 2016-11-09 - 18110 - Roque Garcia-Put together fan motor electrical, grease lines - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-07 | 56855 | TMPE-193302 | The motor is bad on the exhaust fan. | 2016-10-18 - 18230 - Thomas Gibble-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-18 - 18230 - Thomas Gibble-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-18 - 18230 - Gail Jackson-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-21 - 18230 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced motor - Thomas Gibble | The motor is bad on the exhaust fan. 2016-10-18 - 18230 - Thomas Gibble-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-18 - 18230 - Thomas Gibble-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-18 - 18230 - Gail Jackson-replaced exfan with one from payless but it had bad motor. order one motor - Thomas Gibble; 2016-10-21 - 18230 - Thomas Gibble-replaced motor - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced motor - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-07 | 175757 | RFMT-132574 | RES LIFE / Thor: Chapter room A/C not working | 2016-10-07 - 18290 - Thor Millsaps-Replaced condenser fan motor and 45/5 mfd dual capacitor. System is up and running. - Thor Millsaps | RES LIFE / Thor: Chapter room A/C not working 2016-10-07 - 18290 - Thor Millsaps-Replaced condenser fan motor and 45/5 mfd dual capacitor. System is up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-07 | 175762 | RFMT-132569 | RES LIFE / Thor: Please repair kitchen cooling unit condenser | 2016-10-07 - 18110 - Thor Millsaps-Replaced 1 of 2 condenser fan motors. 1/3 HP, 1100 RPM, 460v, CW rot. Carrier part # HC39GE471 - Thor Millsaps | RES LIFE / Thor: Please repair kitchen cooling unit condenser 2016-10-07 - 18110 - Thor Millsaps-Replaced 1 of 2 condenser fan motors. 1/3 HP, 1100 RPM, 460v, CW rot. Carrier part # HC39GE471 - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-07 | 175765 | RFMT-132566 | !! Room needs a new A/C Filter Contact Name: Contact Phone Number: 6233631854 Contact Email: 4N6H0A9 | 2016-10-10 - 18170 - Joe Swan-Replace filter - Joe Swan | !! Room needs a new A/C Filter Contact Name: Contact Phone Number: 6233631854 Contact Email: 4N6H0A9 2016-10-10 - 18170 - Joe Swan-Replace filter - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-07 | 215358 | RACC-113252 | !! The air conditioning has completely stopped working and it is the same temperature inside as it is outside (too hot). The control panel is fine, it just has no effect whatsoever on the air systems. 4NGKHEG | NA | !! The air conditioning has completely stopped working and it is the same temperature inside as it is outside (too hot). The control panel is fine, it just has no effect whatsoever on the air systems. 4NGKHEG NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-07 | 37359 | TMPE-212798 | The Car Shop oil filter synthetic blend air filter wiper blades wiper blades assembly total: 95.89 | NA | The Car Shop oil filter synthetic blend air filter wiper blades wiper blades assembly total: 95.89 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-08 | 57606 | TMPE-192551 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57607 | TMPE-192550 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57608 | TMPE-192549 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57609 | TMPE-192548 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57651 | TMPE-192506 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57652 | TMPE-192505 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57653 | TMPE-192504 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57654 | TMPE-192503 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57655 | TMPE-192502 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57656 | TMPE-192501 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57657 | TMPE-192500 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57658 | TMPE-192499 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 57756 | TMPE-192401 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57757 | TMPE-192400 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57758 | TMPE-192399 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57759 | TMPE-192398 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57760 | TMPE-192397 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57761 | TMPE-192396 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57762 | TMPE-192395 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57763 | TMPE-192394 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57764 | TMPE-192393 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57765 | TMPE-192392 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57766 | TMPE-192391 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57767 | TMPE-192390 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57768 | TMPE-192389 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 57769 | TMPE-192388 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 58033 | TMPE-192124 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 58034 | TMPE-192123 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-08 | 58062 | TMPE-192095 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 58065 | TMPE-192092 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 58066 | TMPE-192091 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 58067 | TMPE-192090 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-08 | 175738 | RFMT-132593 | !! Air conditioner is broken and needs to be fixed. The air will not get cold. Contact Name: Makayla Contact Phone Number: Contact Email: 4NK1FA4 | 2016-10-10 - 18010 - Casey Faultner-Condenser was froze up. Shut the unit down and let it thaw out. Turned unit back on and everything is working properly at this time. - Casey Faultner | !! Air conditioner is broken and needs to be fixed. The air will not get cold. Contact Name: Makayla Contact Phone Number: Contact Email: 4NK1FA4 2016-10-10 - 18010 - Casey Faultner-Condenser was froze up. Shut the unit down and let it thaw out. Turned unit back on and everything is working properly at this time. - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-10-09 | 234243 | POLY-113956 | !! Fridge is not working. The fridge and freezer won't maintain a safe temperature, is currently at 53 degrees and 5 degrees respectively. The temperature is slowly rising despite being on the coldest setting. 4NC3GJM | NA | !! Fridge is not working. The fridge and freezer won't maintain a safe temperature, is currently at 53 degrees and 5 degrees respectively. The temperature is slowly rising despite being on the coldest setting. 4NC3GJM NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-10 | 56042 | TMPE-194115 | MWO: UCENT C 103 Hello, We are having a critical outage of some of our A/C units. One of our training rooms is not getting any cold air and is completely unusable at the moment and it is having an impact our production. This issue requires immediate response. Please create an emergency ticket fo. . . | 2016-10-10 - 18290 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-11 - 18290 - 10/11/2016 1OT 12am-1am Robert Ecabert - UCENT C University Center Building C - Found air handler tripped off, reset breaker on AH#3 still need to work on another A/H - Kerri Perkins; 2016-10-11 - 18290 - 10/10/2016 4OT 8pm-12am Robert Ecabert - UCENT C University Building Center C - 180C found air tripped off, reset breaker on AH#3 still need to work on another one. - Kerri Perkins; 2016-10-13 - 18290 - Robert Ecabert-Found the dx airhandler had no power to it so I found the breaker to the unit and it was shut off so I turned it back on and the room cooled down nicely again. - Robert Ecabert | MWO: UCENT C 103 Hello, We are having a critical outage of some of our A/C units. One of our training rooms is not getting any cold air and is completely unusable at the moment and it is having an impact our production. This issue requires immediate response. Please create an emergency ticket fo. . . 2016-10-10 - 18290 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-11 - 18290 - 10/11/2016 1OT 12am-1am Robert Ecabert - UCENT C University Center Building C - Found air handler tripped off, reset breaker on AH#3 still need to work on another A/H - Kerri Perkins; 2016-10-11 - 18290 - 10/10/2016 4OT 8pm-12am Robert Ecabert - UCENT C University Building Center C - 180C found air tripped off, reset breaker on AH#3 still need to work on another one. - Kerri Perkins; 2016-10-13 - 18290 - Robert Ecabert-Found the dx airhandler had no power to it so I found the breaker to the unit and it was shut off so I turned it back on and the room cooled down nicely again. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-10-10 | 56072 | TMPE-194085 | MWO UNCNTRB 120 Please adjust the AC in this area, it is far too hot. | 2016-10-10 - 18290 - CALLED TO BRIAN Q. - Monica Moraga; 2016-12-09 - 18290 - Roque Garcia-Found the blower motor shorted and needs to be replaced. The building structure support is in the way of repairs. The FCU needs to be dropped completely from ceiling - Roque Garcia | MWO UNCNTRB 120 Please adjust the AC in this area, it is far too hot. 2016-10-10 - 18290 - CALLED TO BRIAN Q. - Monica Moraga; 2016-12-09 - 18290 - Roque Garcia-Found the blower motor shorted and needs to be replaced. The building structure support is in the way of repairs. The FCU needs to be dropped completely from ceiling - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-10 | 56083 | TMPE-194074 | Compressor is not running on fountain. | 2016-12-18 - 18010 - Robert Dauscher-Unit void of refrigerant,compressor bad. drain rusted out. bottle fill broken. older unit, condemned unit by AC and Plumbing. NEEDS replacement. - Robert Dauscher; 2016-12-18 - 18010 - Gregory Wann-Unit void of refrigerant,compressor bad. drain rusted out. bottle fill broken. older unit, condemned unit by AC and Plumbing. NEEDS replacement. - Robert Dauscher | Compressor is not running on fountain. 2016-12-18 - 18010 - Robert Dauscher-Unit void of refrigerant,compressor bad. drain rusted out. bottle fill broken. older unit, condemned unit by AC and Plumbing. NEEDS replacement. - Robert Dauscher; 2016-12-18 - 18010 - Gregory Wann-Unit void of refrigerant,compressor bad. drain rusted out. bottle fill broken. older unit, condemned unit by AC and Plumbing. NEEDS replacement. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-10-10 | 56093 | TMPE-194064 | The contactor for the exhaust fan is noisy. The contactor is located in 119U1 | 2016-10-18 - 18160 - Gail Jackson-Diagnose, transfer to electrical shop - Gail Jackson; 2016-10-18 - 18160 - Thomas Gibble-Diagnose, transfer to electrical shop - Gail Jackson | The contactor for the exhaust fan is noisy. The contactor is located in 119U1 2016-10-18 - 18160 - Gail Jackson-Diagnose, transfer to electrical shop - Gail Jackson; 2016-10-18 - 18160 - Thomas Gibble-Diagnose, transfer to electrical shop - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-10 | 56116 | TMPE-194041 | MWO MUSIC Library BT to HVAC There is a leak coming from the vent and the ceiling on and around column number M1700. | 2016-10-10 - 23040 - Called out to Bryan - Amanda Thomas; 2016-10-18 - 23040 - Thomas Gibble-find hose leaking in planter on the 5th floor - Thomas Gibble; 2016-10-18 - 23040 - Gail Jackson-find hose leaking in planter on the 5th floor - Thomas Gibble | MWO MUSIC Library BT to HVAC There is a leak coming from the vent and the ceiling on and around column number M1700. 2016-10-10 - 23040 - Called out to Bryan - Amanda Thomas; 2016-10-18 - 23040 - Thomas Gibble-find hose leaking in planter on the 5th floor - Thomas Gibble; 2016-10-18 - 23040 - Gail Jackson-find hose leaking in planter on the 5th floor - Thomas Gibble | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-10 | 56141 | TMPE-194016 | MWO MUSIC Library There is a leak coming from the vent and the ceiling on and around column number M1700. | 2016-10-10 - 13050 - Called out to Bryan - Amanda Thomas; 2016-10-10 - 13050 - Bryan LaForais-Complete Received radio call for this WO to go and check out leak and then let service center know who to assign it to. Leak is more than likely coming from condensation from the ductwork, but the lid is a hard lid and I can't get above it to see it exactly. Recommended service center assign it to HVAC. - Bryan LaForais | MWO MUSIC Library There is a leak coming from the vent and the ceiling on and around column number M1700. 2016-10-10 - 13050 - Called out to Bryan - Amanda Thomas; 2016-10-10 - 13050 - Bryan LaForais-Complete Received radio call for this WO to go and check out leak and then let service center know who to assign it to. Leak is more than likely coming from condensation from the ductwork, but the lid is a hard lid and I can't get above it to see it exactly. Recommended service center assign it to HVAC. - Bryan LaForais | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-10-10 | 56190 | TMPE-193967 | MWO PSC Roof !! AH #1, located on w-s of c-wing roof, is alarming due to dirty pre-filters. Send to HVAC for filter changeout ASAP. 42B213C | 2016-10-10 - 18170 - Jennifer Moyer-help jose to put. filters at roof. job in progress - Jose Mazon; 2016-10-10 - 18170 - Jose Mazon-job in progress - Jose Mazon; 2016-10-11 - 18170 - Jose Mazon-filters change complete ..and HI, change complete ....we change the HI. because we planed last time en july to do it,HI are very bad condition after 2years of used. jod complete done .. - Jose Mazon | MWO PSC Roof !! AH #1, located on w-s of c-wing roof, is alarming due to dirty pre-filters. Send to HVAC for filter changeout ASAP. 42B213C 2016-10-10 - 18170 - Jennifer Moyer-help jose to put. filters at roof. job in progress - Jose Mazon; 2016-10-10 - 18170 - Jose Mazon-job in progress - Jose Mazon; 2016-10-11 - 18170 - Jose Mazon-filters change complete ..and HI, change complete ....we change the HI. because we planed last time en july to do it,HI are very bad condition after 2years of used. jod complete done .. - Jose Mazon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-10 | 56193 | TMPE-193964 | SWO: 10/10/16 CCC staff report that a thermostat in the hall by the kitchen is not working properly. Bill to TL502001138. 42A042B | 2016-10-17 - 18010 - Roque Garcia-Found disconnect off at condenser unit. Reenergized and unit check refrigerant level and amps at unit disconnect. - Roque Garcia | SWO: 10/10/16 CCC staff report that a thermostat in the hall by the kitchen is not working properly. Bill to TL502001138. 42A042B 2016-10-17 - 18010 - Roque Garcia-Found disconnect off at condenser unit. Reenergized and unit check refrigerant level and amps at unit disconnect. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-10 | 56194 | TMPE-193963 | SWO: BARRETT DINING HALL Please send someone to check on my freezer asap. Yesterday there was a cart #9626 in the loading dock and someone was laying on top of the walk in cooler doing some work and there was grinding noise. Now the freezer isn't working. This seemed suspicious because I never se. . . | 2016-10-10 - 18180 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-10 - 18180 - Zhi Yu-Arrrived the Freezer @ 15deg. We diagnose the Compressor Running L.R.A. I notice the compressor was install mid 2015 by outside contractor. I talk to Andy West the compressor still under warranties. - Zhi Yu | SWO: BARRETT DINING HALL Please send someone to check on my freezer asap. Yesterday there was a cart #9626 in the loading dock and someone was laying on top of the walk in cooler doing some work and there was grinding noise. Now the freezer isn't working. This seemed suspicious because I never se. . . 2016-10-10 - 18180 - CALLED TO BRIAN Q. - Monica Moraga; 2016-10-10 - 18180 - Zhi Yu-Arrrived the Freezer @ 15deg. We diagnose the Compressor Running L.R.A. I notice the compressor was install mid 2015 by outside contractor. I talk to Andy West the compressor still under warranties. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-10 | 56207 | TMPE-193950 | Special Funding - LSE Roof Drain. The roof drain pipe in LSE has broken inside the AHU ( Air Handling Unit ) and needs to be replaced. Please see attached photos. At every rain water enters this unit some spilling on one of our 4\\u2019 blower units. In conjunction with making necessary repairs to this . . . | NA | Special Funding - LSE Roof Drain. The roof drain pipe in LSE has broken inside the AHU ( Air Handling Unit ) and needs to be replaced. Please see attached photos. At every rain water enters this unit some spilling on one of our 4\\u2019 blower units. In conjunction with making necessary repairs to this . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-10-10 | 175679 | RFMT-132652 | !! The a/c isn't working. Submitted by 4NID637 | 2016-10-11 - 18010 - Joe Swan-installed A/C portables in room 310 &amp; 312 because A/C was blowing hot air and I could not fix it. - Joe Swan; 2016-10-11 - 18010 - Res. Life HVAC Dept techs were copied on this w.o. to follow up and repair. - Gregory Stetka | !! The a/c isn't working. Submitted by 4NID637 2016-10-11 - 18010 - Joe Swan-installed A/C portables in room 310 &amp; 312 because A/C was blowing hot air and I could not fix it. - Joe Swan; 2016-10-11 - 18010 - Res. Life HVAC Dept techs were copied on this w.o. to follow up and repair. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-10 | 175696 | RFMT-132635 | !! RL Lock - please fix or replace the lock on this unit. The key keeps sticking and does not work properly. Check with Sal Marasco if you have any questions. 4NEI9DN | 2016-10-10 - 11000 - Harry Legrand-Checked lock. Lock working properly. Sal's key is worn and its causing the issue. - Harry Legrand | !! RL Lock - please fix or replace the lock on this unit. The key keeps sticking and does not work properly. Check with Sal Marasco if you have any questions. 4NEI9DN 2016-10-10 - 11000 - Harry Legrand-Checked lock. Lock working properly. Sal's key is worn and its causing the issue. - Harry Legrand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-10-10 | 175712 | RFMT-132619 | Aramark staff reports the exhaust fan in the small bathroom near the lobby of Hayden Hall does not work. Contact Name: Pat Jimenez Contact Phone Number: 480-965-0774 Contact Email: Jimenez-Patricia@aramark.com 4NMH8FI | 2016-10-10 - 18160 - Salvatore Marasco Jr-Looked inside ceiling vent in bathroom finding out that there is not an exhaust fan or duct work at all in the ceiling from the room. The vent is only a grill that is open to the area between the cement above and the plaster drop ceiling. Holes would need to be cut through walls and duct work would need to be installed to vent this room to the outside. One idea would be to join the restroom to the kitchen duct and install new exhaust fan in kitchen, using one blower to exhaust both rooms up the kitchens exhaust vent to roof. - Salvatore Marasco Jr; 2016-10-14 - 18160 - Copied Res. Life HVAC Dept Simon and Thor to check. - Gregory Stetka | Aramark staff reports the exhaust fan in the small bathroom near the lobby of Hayden Hall does not work. Contact Name: Pat Jimenez Contact Phone Number: 480-965-0774 Contact Email: Jimenez-Patricia@aramark.com 4NMH8FI 2016-10-10 - 18160 - Salvatore Marasco Jr-Looked inside ceiling vent in bathroom finding out that there is not an exhaust fan or duct work at all in the ceiling from the room. The vent is only a grill that is open to the area between the cement above and the plaster drop ceiling. Holes would need to be cut through walls and duct work would need to be installed to vent this room to the outside. One idea would be to join the restroom to the kitchen duct and install new exhaust fan in kitchen, using one blower to exhaust both rooms up the kitchens exhaust vent to roof. - Salvatore Marasco Jr; 2016-10-14 - 18160 - Copied Res. Life HVAC Dept Simon and Thor to check. - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-10-10 | 234220 | POLY-113979 | !! Main breaker box blew causing an outage. Needs repaired asap because of outage in the house. Thank You Contact Name: Jennifer Thornbug Contact Phone Number: Contact Email: Jennifer.Thornburg@asu.edu 4NG9B74 | NA | !! Main breaker box blew causing an outage. Needs repaired asap because of outage in the house. Thank You Contact Name: Jennifer Thornbug Contact Phone Number: Contact Email: Jennifer.Thornburg@asu.edu 4NG9B74 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-10 | 234221 | POLY-113978 | !! Repeat Request. Air condition has been out for two days. Student reported that it had been making loud noises for a day. Student has filed reports on this incident before. Student shut off AC earlier, and when he turned it on again it started leaking. Contact Name: Anderson Cadell Contact Phon. . . | NA | !! Repeat Request. Air condition has been out for two days. Student reported that it had been making loud noises for a day. Student has filed reports on this incident before. Student shut off AC earlier, and when he turned it on again it started leaking. Contact Name: Anderson Cadell Contact Phon. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 55933 | TMPE-194224 | MWO: We still have a problem with the air conditioner condensation or some source of water leaking from the ceiling and dripping down. Someone stopped by to look at this earlier, after a ceiling tile fell down on the floor, and they cleaned up the ceiling tile and worked on it, but there is stil. . . | 2016-10-17 - 18010 - Jennifer Moyer-Traced condensate line and vacuumed line. Found cracks in condensate drain pan.(needs replaced) - Jennifer Moyer; 2016-10-24 - 18010 - Mitchell Andrews-Installed new drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Remove broken drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Place order and pick up drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Remove old drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Install new pan. - Jennifer Moyer | MWO: We still have a problem with the air conditioner condensation or some source of water leaking from the ceiling and dripping down. Someone stopped by to look at this earlier, after a ceiling tile fell down on the floor, and they cleaned up the ceiling tile and worked on it, but there is stil. . . 2016-10-17 - 18010 - Jennifer Moyer-Traced condensate line and vacuumed line. Found cracks in condensate drain pan.(needs replaced) - Jennifer Moyer; 2016-10-24 - 18010 - Mitchell Andrews-Installed new drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Remove broken drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Place order and pick up drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Remove old drain pan. - Jennifer Moyer; 2016-10-26 - 18010 - Jennifer Moyer-Install new pan. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-10-11 | 55988 | TMPE-194169 | MWO: I need the air vent in my office cleaned. It is spraying black stuff all over me and my desk. I have taken a picture but the system will not allow me to upload it. This stuff is creating a mess on my desk and causing my to have allergy issues when I am at work. Thanks, Lisa 4. . . | 2016-11-16 - 18170 - Jennifer Moyer-Called customer a couple times. I will stop by tomorrow. - Jennifer Moyer; 2016-11-16 - 18170 - Jennifer Moyer-Removed register for cleaning or replacement. Cleaned and photographed debris on the window sill and desk. Customer states that this debris is a problem every 6 months. - Jennifer Moyer; 2016-11-21 - 18170 - Jennifer Moyer- I bead blasted the supply grill and primed. Customer states this issue occurs approximately every 6 months. This may be caused by the filters being changed without shutting down the air handler. This is probably done to save time. - Jennifer Moyer; 2016-11-21 - 18170 - Jennifer Moyer-Installed interior filter to catch extra debris and secured to wall. Email sent to supervisors and to customer requesting shut down when filters are changed. - Jennifer Moyer | MWO: I need the air vent in my office cleaned. It is spraying black stuff all over me and my desk. I have taken a picture but the system will not allow me to upload it. This stuff is creating a mess on my desk and causing my to have allergy issues when I am at work. Thanks, Lisa 4. . . 2016-11-16 - 18170 - Jennifer Moyer-Called customer a couple times. I will stop by tomorrow. - Jennifer Moyer; 2016-11-16 - 18170 - Jennifer Moyer-Removed register for cleaning or replacement. Cleaned and photographed debris on the window sill and desk. Customer states that this debris is a problem every 6 months. - Jennifer Moyer; 2016-11-21 - 18170 - Jennifer Moyer- I bead blasted the supply grill and primed. Customer states this issue occurs approximately every 6 months. This may be caused by the filters being changed without shutting down the air handler. This is probably done to save time. - Jennifer Moyer; 2016-11-21 - 18170 - Jennifer Moyer-Installed interior filter to catch extra debris and secured to wall. Email sent to supervisors and to customer requesting shut down when filters are changed. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-11 | 56019 | TMPE-194138 | MWO: Bio A - AL1-57: !! Please send to AC shop We have a booster supply fan that is located in al1-57 on the east side of room above ceiling that is making a squealing noise and distracting researchers. This unit boosts supply air into room al1-57a .Please repair ASAP ! 4N07O4A | 2016-10-13 - 18010 - Duane Rider-Greased fan and motor bearing - Duane Rider; 2016-10-24 - 18010 - Duane Rider-completed - Duane Rider | MWO: Bio A - AL1-57: !! Please send to AC shop We have a booster supply fan that is located in al1-57 on the east side of room above ceiling that is making a squealing noise and distracting researchers. This unit boosts supply air into room al1-57a .Please repair ASAP ! 4N07O4A 2016-10-13 - 18010 - Duane Rider-Greased fan and motor bearing - Duane Rider; 2016-10-24 - 18010 - Duane Rider-completed - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-11 | 56024 | TMPE-194133 | MWO: This morning Sharalyn Barnby reports that "the HVAC unit in Stauffer 232 seems really loud and vibrating." Could you send someone out to check on it? Thanks. | 2016-10-19 - 18010 - Zhi Yu-we removed the blower housing assembly back to shop for repair. Call Ems to ramp up VAV to 50% - Zhi Yu [Modified: 2016-10-20 Zhi Yu]; 2016-11-09 - 18010 - Zhi Yu-We assemble the motor and blower wheel in the shop. schedule back installation on Wednesday. - Zhi Yu; 2016-11-09 - 18010 - Zhi Yu-We install the blower assembly - Zhi Yu | MWO: This morning Sharalyn Barnby reports that "the HVAC unit in Stauffer 232 seems really loud and vibrating." Could you send someone out to check on it? Thanks. 2016-10-19 - 18010 - Zhi Yu-we removed the blower housing assembly back to shop for repair. Call Ems to ramp up VAV to 50% - Zhi Yu [Modified: 2016-10-20 Zhi Yu]; 2016-11-09 - 18010 - Zhi Yu-We assemble the motor and blower wheel in the shop. schedule back installation on Wednesday. - Zhi Yu; 2016-11-09 - 18010 - Zhi Yu-We install the blower assembly - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 175600 | RFMT-132731 | Best C 3rd , 2nd and 1st floor door to door program. | 2016-10-13 - 10010 - Salvatore Marasco Jr-Checked all rooms for need of repairs and changed all A.C. air filters. - Salvatore Marasco Jr | Best C 3rd , 2nd and 1st floor door to door program. 2016-10-13 - 10010 - Salvatore Marasco Jr-Checked all rooms for need of repairs and changed all A.C. air filters. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 175613 | RFMT-132718 | !! The a/c isn't working. Submitted by 4NID637 | 2016-10-12 - 18010 - Thor Millsaps-Checked ac unit. Added 1 lb R-22. System up and running. Followed up on 10/12. Residents said ac has been working fine last 24 hours. Removed portable ac units from rooms. - Thor Millsaps | !! The a/c isn't working. Submitted by 4NID637 2016-10-12 - 18010 - Thor Millsaps-Checked ac unit. Added 1 lb R-22. System up and running. Followed up on 10/12. Residents said ac has been working fine last 24 hours. Removed portable ac units from rooms. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 175653 | RFMT-132678 | !! Resident says that the thermostat does not work or respond, and the air conditioning is not working in the suite. 4NJL8GC | 2016-10-12 - 18010 - Gabriel Figueroa-repaired a/c no parts used. all is working good. - Gabriel Figueroa | !! Resident says that the thermostat does not work or respond, and the air conditioning is not working in the suite. 4NJL8GC 2016-10-12 - 18010 - Gabriel Figueroa-repaired a/c no parts used. all is working good. - Gabriel Figueroa | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 215313 | RACC-113297 | Open the air vent near the window. We have tried to open it but cannot seem to get it to move. The flaps inside are making triangles so no air is coming out. 4NO8N2I | NA | Open the air vent near the window. We have tried to open it but cannot seem to get it to move. The flaps inside are making triangles so no air is coming out. 4NO8N2I NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 234147 | POLY-114052 | Freezer Isn't working very well. Still is somewhat cold but seems to be getting worse. Had to throw out food. Contact Name: Contact Phone Number: 6238894882 Contact Email: 4NL3HF9 | NA | Freezer Isn't working very well. Still is somewhat cold but seems to be getting worse. Had to throw out food. Contact Name: Contact Phone Number: 6238894882 Contact Email: 4NL3HF9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 234176 | POLY-114023 | BILLED BILLED JC5-7011 $140.16 FOR LABOR ON #JC2II008355 ON 4/24/17 A/C unit is too cold CHARGE BACK TO CENTURY HALL | 2016-10-13 - 18300 - Suresh Nair-10/11 - Allan and Suresh checked and reset the unit, and cleaned the filter. Tested with software. - Gayle Swenson | BILLED BILLED JC5-7011 $140.16 FOR LABOR ON #JC2II008355 ON 4/24/17 A/C unit is too cold CHARGE BACK TO CENTURY HALL 2016-10-13 - 18300 - Suresh Nair-10/11 - Allan and Suresh checked and reset the unit, and cleaned the filter. Tested with software. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 234177 | POLY-114022 | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008342 ON 4/21/17 The A/C is out and is not cooling and the vent needs to be cleaned out. Particulars are growing on the vent. CHARGE BACK TO CENTURY HALL | 2016-10-14 - 18010 - Allan Blair-10/11 - Suresh and Allan got the A/C working, and cleaned the filter. - Gayle Swenson | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008342 ON 4/21/17 The A/C is out and is not cooling and the vent needs to be cleaned out. Particulars are growing on the vent. CHARGE BACK TO CENTURY HALL 2016-10-14 - 18010 - Allan Blair-10/11 - Suresh and Allan got the A/C working, and cleaned the filter. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-11 | 234187 | POLY-114012 | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008317 ON 4/21/17 A/C is not working properly-not blowing cold air. CHARGE BACK TO CENTURY HALL | 2016-10-13 - 18010 - Suresh Nair-10/11 - Suresh and Allen checked system, and got it working. Cleaned filter. - Gayle Swenson | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008317 ON 4/21/17 A/C is not working properly-not blowing cold air. CHARGE BACK TO CENTURY HALL 2016-10-13 - 18010 - Suresh Nair-10/11 - Suresh and Allen checked system, and got it working. Cleaned filter. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 234188 | POLY-114011 | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008305 ON 4/20/17 A/C unit is blowing out warm air, and the unit needs to be cleaned out. CHARGE BACK TO CENTURY HALL | 2016-10-13 - 18010 - Suresh Nair-10/11 - Suresh and Allen checked unit and cleaned filter. Resident says it is working fine. - Gayle Swenson | BILLED BILLED JC5-7011 $93.44 FOR LABOR ON #JC2II008305 ON 4/20/17 A/C unit is blowing out warm air, and the unit needs to be cleaned out. CHARGE BACK TO CENTURY HALL 2016-10-13 - 18010 - Suresh Nair-10/11 - Suresh and Allen checked unit and cleaned filter. Resident says it is working fine. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-11 | 234189 | POLY-114010 | BILLED BILLED JC5-7011 $46.72 FOR LABOR ON #JC2II008303 ON 4/20/17 A/C unit needs to be cleaned out-vent is dirty. CHARGE BACK TO CENTURY HALL | 2016-10-13 - 18010 - Suresh Nair-10/11 - Allan and Suresh repaired, and cleaned filter. - Gayle Swenson | BILLED BILLED JC5-7011 $46.72 FOR LABOR ON #JC2II008303 ON 4/20/17 A/C unit needs to be cleaned out-vent is dirty. CHARGE BACK TO CENTURY HALL 2016-10-13 - 18010 - Suresh Nair-10/11 - Allan and Suresh repaired, and cleaned filter. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-12 | 54601 | TMPE-195556 | SWO: !! Would like a quotation for a new ice machine and filter system to replace a damage ice machine in PSH-246. Contact Name: Contact Phone Number: 4809657215 Contact Email: 42AIG49 EST-154661 | 2016-10-24 - 18210 - Gail Jackson-Trip to Phx ARS to pick up ice machine, ACE hardware for PLUMBING parts and warehouse foe pvc. Remove and install new ice machine and filter system, run test; COMPLETE. - Gail Jackson; 2016-10-24 - 18210 - Thomas Gibble-Trip to Phx ARS to pick up ice machine, ACE hardware for PLUMBING parts and warehouse foe pvc. Remove and install new ice machine and filter system, run test; COMPLETE. - Gail Jackson | SWO: !! Would like a quotation for a new ice machine and filter system to replace a damage ice machine in PSH-246. Contact Name: Contact Phone Number: 4809657215 Contact Email: 42AIG49 EST-154661 2016-10-24 - 18210 - Gail Jackson-Trip to Phx ARS to pick up ice machine, ACE hardware for PLUMBING parts and warehouse foe pvc. Remove and install new ice machine and filter system, run test; COMPLETE. - Gail Jackson; 2016-10-24 - 18210 - Thomas Gibble-Trip to Phx ARS to pick up ice machine, ACE hardware for PLUMBING parts and warehouse foe pvc. Remove and install new ice machine and filter system, run test; COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-12 | 55794 | TMPE-194363 | MWO: !! The A/C is not working in this office. Please send someone asap. 4NF62MD | 2016-10-18 - 18290 - Nicholas Sizow-HP1-16 bad fan motor, AC to replace RM 104-09 HP 1-19 is working fine, the room was below setpoint. Adjusted cooling setpoint. - Nicholas Sizow | MWO: !! The A/C is not working in this office. Please send someone asap. 4NF62MD 2016-10-18 - 18290 - Nicholas Sizow-HP1-16 bad fan motor, AC to replace RM 104-09 HP 1-19 is working fine, the room was below setpoint. Adjusted cooling setpoint. - Nicholas Sizow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-12 | 55795 | TMPE-194362 | MWO PSH H332 !! hello, The ice machine in PSH-332 is not making ice again, and we just paid $250 to have it repaired. Please reference WO #179362. Please send someone ASAP? 42AE9GB | 2016-10-19 - 18210 - Gail Jackson-Cleaned unit, adjusted float. - Gail Jackson; 2016-10-19 - 18210 - Thomas Gibble-Cleaned unit, adjusted float. - Gail Jackson; 2016-10-19 - 18210 - Gail Jackson-Talked with factory Tech. this old Scotsman is prone for this issue of ice pressure switch problems. Scrubbed out ice shut, run test. Rechecked next day unit running making ice. - Gail Jackson; 2016-10-19 - 18210 - Thomas Gibble-Talked with factory Tech. this old Scotsman is prone for this issue of ice pressure switch problems. Scrubbed out ice shut, run test. Rechecked next day unit running making ice. - Gail Jackson | MWO PSH H332 !! hello, The ice machine in PSH-332 is not making ice again, and we just paid $250 to have it repaired. Please reference WO #179362. Please send someone ASAP? 42AE9GB 2016-10-19 - 18210 - Gail Jackson-Cleaned unit, adjusted float. - Gail Jackson; 2016-10-19 - 18210 - Thomas Gibble-Cleaned unit, adjusted float. - Gail Jackson; 2016-10-19 - 18210 - Gail Jackson-Talked with factory Tech. this old Scotsman is prone for this issue of ice pressure switch problems. Scrubbed out ice shut, run test. Rechecked next day unit running making ice. - Gail Jackson; 2016-10-19 - 18210 - Thomas Gibble-Talked with factory Tech. this old Scotsman is prone for this issue of ice pressure switch problems. Scrubbed out ice shut, run test. Rechecked next day unit running making ice. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-12 | 175517 | RFMT-132814 | !! Fire alarm battery is dead. Also, the air conditioning is not working at all. Thank you! 4NOCK2C ASUHC - Kahlea Cranford - 23:11 Description: Student Sheila Doane reporting AC broken in McClintock Hall Room 309 Who was dispatched: Joe Swan623-694-7006 Time of dispatch: 23:17 -Obtained 15-2. . . | 2016-10-13 - 10010 - Joe Swan-Found that the a/c motor had quit working and needed replaced. It was midnight and the occupant didn't wont me working any later in her room so turned it over to Mike Romero for in the morning - Joe Swan | !! Fire alarm battery is dead. Also, the air conditioning is not working at all. Thank you! 4NOCK2C ASUHC - Kahlea Cranford - 23:11 Description: Student Sheila Doane reporting AC broken in McClintock Hall Room 309 Who was dispatched: Joe Swan623-694-7006 Time of dispatch: 23:17 -Obtained 15-2. . . 2016-10-13 - 10010 - Joe Swan-Found that the a/c motor had quit working and needed replaced. It was midnight and the occupant didn't wont me working any later in her room so turned it over to Mike Romero for in the morning - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2016-10-12 | 234107 | POLY-114092 | Fan in main bathroom creates very loud whining noise. Jostling the box it rests in sometimes alleviates the noise, but not always, and the noise always returns eventually. 4NG2FFE | NA | Fan in main bathroom creates very loud whining noise. Jostling the box it rests in sometimes alleviates the noise, but not always, and the noise always returns eventually. 4NG2FFE NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-13 | 4197 | WEST-107052 | Air Compressor - Monthly Maintenance | 2016-10-14 - xPM-0100-M - Robert Gailey-checked fluids and tires, operated compressor - Robert Gailey | Air Compressor - Monthly Maintenance 2016-10-14 - xPM-0100-M - Robert Gailey-checked fluids and tires, operated compressor - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-13 | 55555 | TMPE-194602 | MWO: USE 103 The room is very hot. | 2016-10-13 - 18290 - CALLED TO BRIAN. - Monica Moraga; 2016-10-23 - 18290 - Robert Dauscher-Reset condenser. was locked out on CLO. verify unit operation Call complete - Robert Dauscher | MWO: USE 103 The room is very hot. 2016-10-13 - 18290 - CALLED TO BRIAN. - Monica Moraga; 2016-10-23 - 18290 - Robert Dauscher-Reset condenser. was locked out on CLO. verify unit operation Call complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-10-13 | 55658 | TMPE-194499 | MWO: Centerpoint 104 Suite Transferred call to HVAC to check HP1-16 (located between 104AC & 104BA) the blower motor doesn't work. Questions, please contact Nick Sizow @ 48.321.5710. EMS WO#194363, HVAC WO#194499. !! The A/C is not working in this office. Please send someone asap. 4NF62MD | NA | MWO: Centerpoint 104 Suite Transferred call to HVAC to check HP1-16 (located between 104AC & 104BA) the blower motor doesn't work. Questions, please contact Nick Sizow @ 48.321.5710. EMS WO#194363, HVAC WO#194499. !! The A/C is not working in this office. Please send someone asap. 4NF62MD NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-13 | 55738 | TMPE-194419 | MWO: Bio A - AL1-57: CRF to HVAC Please transfer to HVAC. Duane has done all he can, but Robert needs further assistance ORIG REQUEST !! Please send to AC shop We have a booster supply fan that is located in al1-57 on the east side of room above ceiling that is making a squealing noise and. . . | 2016-10-13 - 18010 - Brian Qualls-John, Robert and Tom Mason have come up with an alternate plan for this. - Brian Qualls | MWO: Bio A - AL1-57: CRF to HVAC Please transfer to HVAC. Duane has done all he can, but Robert needs further assistance ORIG REQUEST !! Please send to AC shop We have a booster supply fan that is located in al1-57 on the east side of room above ceiling that is making a squealing noise and. . . 2016-10-13 - 18010 - Brian Qualls-John, Robert and Tom Mason have come up with an alternate plan for this. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-13 | 175502 | RFMT-132829 | Please check and report source of odor in Laundry room 133. Thank you. | 2016-10-13 - 18020 - Salvatore Marasco Jr-Found that the odor was coming from the laundry room dryer vent. Went up to the roof to the exhaust fan finding it out of order. There is power to the motor but the motor is not running. Appears to be burned out. The FacMan mechanic was up on roof doing PM's last week and saw this motor not working. Don't know if he reported it. This work order should be turned over to FacMan mechanical shop. - Salvatore Marasco Jr; 2016-10-13 - 18020 - created work order for FACMAN mech. shop. - Gregory Stetka | Please check and report source of odor in Laundry room 133. Thank you. 2016-10-13 - 18020 - Salvatore Marasco Jr-Found that the odor was coming from the laundry room dryer vent. Went up to the roof to the exhaust fan finding it out of order. There is power to the motor but the motor is not running. Appears to be burned out. The FacMan mechanic was up on roof doing PM's last week and saw this motor not working. Don't know if he reported it. This work order should be turned over to FacMan mechanical shop. - Salvatore Marasco Jr; 2016-10-13 - 18020 - created work order for FACMAN mech. shop. - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-13 | 215250 | RACC-113360 | !! New air filter imediatly 4NJ1JH8 | NA | !! New air filter imediatly 4NJ1JH8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-13 | 255589 | DTPC-112949 | Elevator in the Parking Garage is not working. | 2016-10-13 - 16000 - Steve Skibbe-checked out called ThyssenKrupp. Bad coil keeping unit down ThyssenKrupp will replace asap - Steve Skibbe [Modified: 2016-10-18 Julie Fowler] | Elevator in the Parking Garage is not working. 2016-10-13 - 16000 - Steve Skibbe-checked out called ThyssenKrupp. Bad coil keeping unit down ThyssenKrupp will replace asap - Steve Skibbe [Modified: 2016-10-18 Julie Fowler] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-14 | 4124 | WEST-107125 | The Washing machine has malfunctioned and began to spill water on the floors. It is temporarily stopped and will not open back up. | 2016-10-14 - 23070 - Robert Gailey-Called Coin $ Professional Equip. and scheduled service for Monday. - Robert Gailey; 2016-10-18 - 23070 - Tim Jowers-called out cpec equipment repair and they found that the motor on the drain valve was bad. replaced the drain valve and the machine is working correctly. - Tim Jowers | The Washing machine has malfunctioned and began to spill water on the floors. It is temporarily stopped and will not open back up. 2016-10-14 - 23070 - Robert Gailey-Called Coin $ Professional Equip. and scheduled service for Monday. - Robert Gailey; 2016-10-18 - 23070 - Tim Jowers-called out cpec equipment repair and they found that the motor on the drain valve was bad. replaced the drain valve and the machine is working correctly. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-10-14 | 55421 | TMPE-194736 | MWO: HVAC Student in A218 complained that her room was warm. Upon inspection, all the rooms on the second floor are warm. In addition; HVAC Sheet Metal Technician to get with Paul Iannone for information on room that is not getting any air. 42B1A9B | 2016-10-17 - 18290 - Brian Qualls-Found heaters tripped. Heaters and starter are undersized for this and previous motor. Will have Electricians added to this to replace with proper starter and also new fused disconnect. - Brian Qualls; 2016-10-26 - 18290 - Jennifer Moyer-Reset Chiller - Jennifer Moyer; 2016-10-31 - 18290 - Waiting on electrician to replace heaters/disconnect. - Jennifer Moyer; 2016-10-31 - 18290 - Carl Karr-Disconnect and starter changed out. No further work required from sheet metal. - Carl Karr | MWO: HVAC Student in A218 complained that her room was warm. Upon inspection, all the rooms on the second floor are warm. In addition; HVAC Sheet Metal Technician to get with Paul Iannone for information on room that is not getting any air. 42B1A9B 2016-10-17 - 18290 - Brian Qualls-Found heaters tripped. Heaters and starter are undersized for this and previous motor. Will have Electricians added to this to replace with proper starter and also new fused disconnect. - Brian Qualls; 2016-10-26 - 18290 - Jennifer Moyer-Reset Chiller - Jennifer Moyer; 2016-10-31 - 18290 - Waiting on electrician to replace heaters/disconnect. - Jennifer Moyer; 2016-10-31 - 18290 - Carl Karr-Disconnect and starter changed out. No further work required from sheet metal. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-14 | 55448 | TMPE-194709 | MWO: Zhi Yu will join forces with EMS to find out what the Sequence of Operations is for BA AHU's. EMS to check programming to find out why Supply Fans and Return fans are not working together. Supply fans are ramping up which increases the noise level the AHU are putting out. All Fans are on VF. . . | 2016-10-14 - 18050 - John Howell went over to BA-449U1 to check out the noise. I spoke to the gentleman just outside the door to confirm that he is usually there and he confirmed he is there daily. I asked him if he had noticed any new noises and he indicates that there have not been any changes in the level of noise and does not notice the noises that are currently being heard. He said he just tunes them out. There are three AHU's in the room each with a Supply Fan and a Return Fan. All three Supply fans are running but none of the Return fans are running. They are all on VFD's and the displays are all missing. I called John Holloway at EMS to turn on RAF-1 to 30%, the noise level decreased a fair amount. He then returned it to Auto. I am assuming that all three Return fans should be running with the Supply fans for a Push/Pull operation. We will have EMS and HVAC work together to find the Sequence of operations for the building and specifically AHU-1,2 &amp; 3. If it turns out that there is a programming issue and the return fans should be operating, the noise level will drop similar to the test today. - John Howell; 2016-10-14 - 18050 - John Howell called Tim McLaughlin to discuss the service call that came in on BA-449U1. Tim is unaware of any new noises. HVAC &amp; EMS will be investigating the Sequence of operations and the programming to determine if changes or repairs are need. - John Howell; 2016-10-14 - 18050 - Called Susan Cosgrove 480-965-5516 and she wanted me to speak to Tim McLaughlin. - John Howell; 2017-03-08 - 18050 - Zhi Yu-The damper are in sequence operation. - Zhi Yu | MWO: Zhi Yu will join forces with EMS to find out what the Sequence of Operations is for BA AHU's. EMS to check programming to find out why Supply Fans and Return fans are not working together. Supply fans are ramping up which increases the noise level the AHU are putting out. All Fans are on VF. . . 2016-10-14 - 18050 - John Howell went over to BA-449U1 to check out the noise. I spoke to the gentleman just outside the door to confirm that he is usually there and he confirmed he is there daily. I asked him if he had noticed any new noises and he indicates that there have not been any changes in the level of noise and does not notice the noises that are currently being heard. He said he just tunes them out. There are three AHU's in the room each with a Supply Fan and a Return Fan. All three Supply fans are running but none of the Return fans are running. They are all on VFD's and the displays are all missing. I called John Holloway at EMS to turn on RAF-1 to 30%, the noise level decreased a fair amount. He then returned it to Auto. I am assuming that all three Return fans should be running with the Supply fans for a Push/Pull operation. We will have EMS and HVAC work together to find the Sequence of operations for the building and specifically AHU-1,2 &amp; 3. If it turns out that there is a programming issue and the return fans should be operating, the noise level will drop similar to the test today. - John Howell; 2016-10-14 - 18050 - John Howell called Tim McLaughlin to discuss the service call that came in on BA-449U1. Tim is unaware of any new noises. HVAC &amp; EMS will be investigating the Sequence of operations and the programming to determine if changes or repairs are need. - John Howell; 2016-10-14 - 18050 - Called Susan Cosgrove 480-965-5516 and she wanted me to speak to Tim McLaughlin. - John Howell; 2017-03-08 - 18050 - Zhi Yu-The damper are in sequence operation. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-14 | 55461 | TMPE-194696 | MWO USB Wes needs a work order to make repairs on the spare compressor | 2017-01-13 - 18030 - Gail Jackson-Unit past it useful service life, scrap. - Gail Jackson; 2017-01-13 - 18030 - Thomas Gibble-Unit past it useful service life, scrap. - Gail Jackson | MWO USB Wes needs a work order to make repairs on the spare compressor 2017-01-13 - 18030 - Gail Jackson-Unit past it useful service life, scrap. - Gail Jackson; 2017-01-13 - 18030 - Thomas Gibble-Unit past it useful service life, scrap. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-14 | 55476 | TMPE-194681 | MWO: !! We received a complaint from faculty that the AC is not working in the building. They said it sounds like the AC is running, but no cool air is coming out. Please fix ASAP - thank you. 4O3A12D | 2016-10-20 - 18290 - Gail Jackson-Found unit flat on R22, will need to pressure test unit and leak check. Unit is 30 years old and past it useful service life. - Gail Jackson; 2016-10-20 - 18290 - Thomas Gibble-Found unit flat on R22, will need to pressure test unit and leak check. Unit is 30 years old and past it useful service life. - Gail Jackson; 2016-10-26 - 18290 - Gail Jackson-found leak in high side isolation valve, tightened. pressurized with 250 psi nitrogen; sniffer and bubbles. Used Jennifer's vacuum pump as neither Tom or I have one. Charged unit with 10.5 lbs R22. Unit needs replaced it has out lived its useful service life at 30 yrs old. - Gail Jackson; 2016-10-26 - 18290 - Thomas Gibble-found leak in high side isolation valve, tightened. pressurized with 250 psi nitrogen; sniffer and bubbles. Used Jennifer's vacuum pump as neither Tom or I have one. Charged unit with 10.5 lbs R22. Unit needs replaced it has out lived its useful service life at 30 yrs old. - Gail Jackson | MWO: !! We received a complaint from faculty that the AC is not working in the building. They said it sounds like the AC is running, but no cool air is coming out. Please fix ASAP - thank you. 4O3A12D 2016-10-20 - 18290 - Gail Jackson-Found unit flat on R22, will need to pressure test unit and leak check. Unit is 30 years old and past it useful service life. - Gail Jackson; 2016-10-20 - 18290 - Thomas Gibble-Found unit flat on R22, will need to pressure test unit and leak check. Unit is 30 years old and past it useful service life. - Gail Jackson; 2016-10-26 - 18290 - Gail Jackson-found leak in high side isolation valve, tightened. pressurized with 250 psi nitrogen; sniffer and bubbles. Used Jennifer's vacuum pump as neither Tom or I have one. Charged unit with 10.5 lbs R22. Unit needs replaced it has out lived its useful service life at 30 yrs old. - Gail Jackson; 2016-10-26 - 18290 - Thomas Gibble-found leak in high side isolation valve, tightened. pressurized with 250 psi nitrogen; sniffer and bubbles. Used Jennifer's vacuum pump as neither Tom or I have one. Charged unit with 10.5 lbs R22. Unit needs replaced it has out lived its useful service life at 30 yrs old. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-10-14 | 175404 | RFMT-132927 | Please repair fan coil unit in Irish B 101. | 2016-10-14 - 18010 - Thor Millsaps-Replaced blower motor. Installed a used D291 motor that was taken from Cholla. - Thor Millsaps | Please repair fan coil unit in Irish B 101. 2016-10-14 - 18010 - Thor Millsaps-Replaced blower motor. Installed a used D291 motor that was taken from Cholla. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-14 | 175422 | RFMT-132909 | RES LIFE: A/C wall pak outside of elevator lobby missing adjustment wheel | 2016-10-18 - 18010 - Scott Berndt-replaced knob,need to order parts for squiel cage - Scott Berndt | RES LIFE: A/C wall pak outside of elevator lobby missing adjustment wheel 2016-10-18 - 18010 - Scott Berndt-replaced knob,need to order parts for squiel cage - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-14 | 175434 | RFMT-132897 | Aramark staff reports the exhaust fan in the small bathroom near the lobby of Hayden Hall does not work. Contact Name: Pat Jimenez Contact Phone Number: 480-965-0774 Contact Email: Jimenez-Patricia@aramark.com 4NMH8FI | 2016-10-18 - 18160 - Thor Millsaps-Inspected bathroom. No exhaust fan exists in bathroom. There is currently no way to exhaust bathroom. Recommend installing new fan motor in adjacent kitchen, run 4" duct through wall into bathroom, install 2-way electrical switches in kitchen and bathroom. Exhaust fan motor will then exhaust kitchen and bathroom simultaneously. There is already existing ductwork above kitchen ceiling for exhaust to exit building through roof. - Thor Millsaps | Aramark staff reports the exhaust fan in the small bathroom near the lobby of Hayden Hall does not work. Contact Name: Pat Jimenez Contact Phone Number: 480-965-0774 Contact Email: Jimenez-Patricia@aramark.com 4NMH8FI 2016-10-18 - 18160 - Thor Millsaps-Inspected bathroom. No exhaust fan exists in bathroom. There is currently no way to exhaust bathroom. Recommend installing new fan motor in adjacent kitchen, run 4" duct through wall into bathroom, install 2-way electrical switches in kitchen and bathroom. Exhaust fan motor will then exhaust kitchen and bathroom simultaneously. There is already existing ductwork above kitchen ceiling for exhaust to exit building through roof. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-10-14 | 234070 | POLY-114129 | CALLED STEVE SIM 139a air conditioner is not working leaks water into sim 139 ceiling, water stained ceiling tile. 4N43440 | NA | CALLED STEVE SIM 139a air conditioner is not working leaks water into sim 139 ceiling, water stained ceiling tile. 4N43440 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-14 | 255560 | DTPC-112978 | A/C in up stairs office not working per George | 2016-10-14 - 18010 - Robert Bartels-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels; 2016-10-14 - 18010 - Bruce Pickford-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels; 2016-10-14 - 18010 - Bruce Pickford-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels | A/C in up stairs office not working per George 2016-10-14 - 18010 - Robert Bartels-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels; 2016-10-14 - 18010 - Bruce Pickford-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels; 2016-10-14 - 18010 - Bruce Pickford-A/C in up stairs office not working per George, checked out unit, call Ralph to bring tools, found pinched wire on control side - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-15 | 56238 | TMPE-193919 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56268 | TMPE-193889 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-15 | 56269 | TMPE-193888 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-15 | 56329 | TMPE-193828 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-15 | 56330 | TMPE-193827 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-15 | 56372 | TMPE-193785 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pumps unplugged, water turned off, water drained from pan.Power to unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pumps unplugged, water turned off, water drained from pan.Power to unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56373 | TMPE-193784 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, and water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, and water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56374 | TMPE-193783 | Evaporative Cooler- Biannual | 2016-10-11 - xPM-2000-B - Belt replaced under TMPE-167813. - Jennifer Moyer; 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off to unit, water drained from the pan. Power left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-10-11 - xPM-2000-B - Belt replaced under TMPE-167813. - Jennifer Moyer; 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off to unit, water drained from the pan. Power left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56375 | TMPE-193782 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56376 | TMPE-193781 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan. Power to unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56377 | TMPE-193780 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan.Power to unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pump unplugged, water turned off, water drained from pan.Power to unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56378 | TMPE-193779 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56379 | TMPE-193778 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pumps unplugged, water turned off, and water drained from the pan. Unit left on for airflow. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Condensate pumps unplugged, water turned off, and water drained from the pan. Unit left on for airflow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-15 | 56380 | TMPE-193777 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56381 | TMPE-193776 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Unit turned off and water turned off. Doors rusted shut so water could not be emptied. Low humidity should allow the water to evaporate soon. No mosquitos in any of the 11 units I looked at. This unit is scheduled to be replaced. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Unit turned off and water turned off. Doors rusted shut so water could not be emptied. Low humidity should allow the water to evaporate soon. No mosquitos in any of the 11 units I looked at. This unit is scheduled to be replaced. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56382 | TMPE-193775 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56383 | TMPE-193774 | Evaporative Cooler- Biannual | 2016-11-23 - xPM-2000-B - Jennifer Moyer-Unit turned off and water turned off. Doors rusted shut so water could not be emptied. With low humidity, the water should evaporate soon. No sign of mosquitos in any of the 11 units I looked at so far. This unit is scheduled to be replaced. - Jennifer Moyer [Modified: 2016-11-23 Jennifer Moyer] | Evaporative Cooler- Biannual 2016-11-23 - xPM-2000-B - Jennifer Moyer-Unit turned off and water turned off. Doors rusted shut so water could not be emptied. With low humidity, the water should evaporate soon. No sign of mosquitos in any of the 11 units I looked at so far. This unit is scheduled to be replaced. - Jennifer Moyer [Modified: 2016-11-23 Jennifer Moyer] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56384 | TMPE-193773 | Evaporative Cooler- Biannual | 2016-12-30 - xPM-2000-B - Jennifer Moyer-Shut down for winter. Turn off power/water, and clean out tray. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-12-30 - xPM-2000-B - Jennifer Moyer-Shut down for winter. Turn off power/water, and clean out tray. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56385 | TMPE-193772 | Evaporative Cooler- Biannual | 2016-12-22 - xPM-2000-B - Jennifer Moyer-Turn water/power off. Clean water tray for winter. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-12-22 - xPM-2000-B - Jennifer Moyer-Turn water/power off. Clean water tray for winter. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56386 | TMPE-193771 | Evaporative Cooler- Biannual | 2016-12-22 - xPM-2000-B - Jennifer Moyer-Shut down water/power. Clean out water tray for winter. - Jennifer Moyer | Evaporative Cooler- Biannual 2016-12-22 - xPM-2000-B - Jennifer Moyer-Shut down water/power. Clean out water tray for winter. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56630 | TMPE-193527 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 56631 | TMPE-193526 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-15 | 234060 | POLY-114139 | !! The fan in our freezer is making a rattling sound and I am worried the freezer will stop working. 4N2JI84 | NA | !! The fan in our freezer is making a rattling sound and I am worried the freezer will stop working. 4N2JI84 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-16 | 215191 | RACC-113419 | AC is broke 4NOFGC3 | NA | AC is broke 4NOFGC3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-10-16 | 215229 | RACC-113381 | Air conditioner not working on C/D side; bathtub drain in A clogged. 4NK10H0 | NA | Air conditioner not working on C/D side; bathtub drain in A clogged. 4NK10H0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-17 | 54867 | TMPE-195290 | MWO EDB L1-04U1 HWS HWP4 shows as running but the pump is not physically running and the bucket is set to Auto. MCC appears to have been replaced in the last 6 months. Electrical shop needs to check the wiring of the pump. Thanks 42BE2F4 | 2016-10-26 - 15000 - Jose Lopez-turned on manually from NCC, motor runs, amps fine, but when put on automatic it doesn't work, when not on heating, signal not getting there call Jose from AC shop with any questions - Juliana Blusiewicz | MWO EDB L1-04U1 HWS HWP4 shows as running but the pump is not physically running and the bucket is set to Auto. MCC appears to have been replaced in the last 6 months. Electrical shop needs to check the wiring of the pump. Thanks 42BE2F4 2016-10-26 - 15000 - Jose Lopez-turned on manually from NCC, motor runs, amps fine, but when put on automatic it doesn't work, when not on heating, signal not getting there call Jose from AC shop with any questions - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-17 | 54925 | TMPE-195232 | MWO ALMDB 124 there is a high pitched constant noise near the roof of the warehouse (large storage area) at the north end of Alameda building. It started about mid week 10/12 and is still present this morning 10/17. It may be something to do with one of the A/C units on the roof, or other electri. . . | 2016-10-19 - 18010 - Roque Garcia-Investigated the high pitch sound that is located in the Alameda warehouse. It is not any of the HVAC systems. I contacted and spoke with Charlie from fire alarm systems and he was going to reset EST panel. I returned and found the same audible still making noise so I called and spoke with Danny the fire tech. He meet me at Alameda warehouse and we investigated audible and he concluded that it wasnt a fire system problem. So walked the warehouse and it sounded like it was comiing from within the locked cages that belong to several different departments. Danny passed this info along to Charlie and we hope to gain access and resolve problem. We contatcted and spoke with Ayrlene from Archeology dept. and was updated and aware of what was going to be done. - Roque Garcia | MWO ALMDB 124 there is a high pitched constant noise near the roof of the warehouse (large storage area) at the north end of Alameda building. It started about mid week 10/12 and is still present this morning 10/17. It may be something to do with one of the A/C units on the roof, or other electri. . . 2016-10-19 - 18010 - Roque Garcia-Investigated the high pitch sound that is located in the Alameda warehouse. It is not any of the HVAC systems. I contacted and spoke with Charlie from fire alarm systems and he was going to reset EST panel. I returned and found the same audible still making noise so I called and spoke with Danny the fire tech. He meet me at Alameda warehouse and we investigated audible and he concluded that it wasnt a fire system problem. So walked the warehouse and it sounded like it was comiing from within the locked cages that belong to several different departments. Danny passed this info along to Charlie and we hope to gain access and resolve problem. We contatcted and spoke with Ayrlene from Archeology dept. and was updated and aware of what was going to be done. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-10-17 | 54947 | TMPE-195210 | MWO: add EMS for assist: Zhi Yu will join forces with EMS to find out what the Sequence of Operations is for BA AHU's. EMS to check programming to find out why Supply Fans and Return fans are not working together. Supply fans are ramping up which increases the noise level the AHU are putting ou. . . | 2016-10-18 - 18050 - Jeffrey Green-met with Zhi and Ameresco to discuss noise the filters were dirty and sounds like 2 motors have bearing issues made some minor adjustments to equalize static return fans run to maintain bldg. pressure accordingly - Jeffrey Green | MWO: add EMS for assist: Zhi Yu will join forces with EMS to find out what the Sequence of Operations is for BA AHU's. EMS to check programming to find out why Supply Fans and Return fans are not working together. Supply fans are ramping up which increases the noise level the AHU are putting ou. . . 2016-10-18 - 18050 - Jeffrey Green-met with Zhi and Ameresco to discuss noise the filters were dirty and sounds like 2 motors have bearing issues made some minor adjustments to equalize static return fans run to maintain bldg. pressure accordingly - Jeffrey Green | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-17 | 175265 | RFMT-133066 | clean the air vents in each individual room 4NC67OD | 2016-10-18 - 18010 - Joe Swan-clean A/C vent - Joe Swan | clean the air vents in each individual room 4NC67OD 2016-10-18 - 18010 - Joe Swan-clean A/C vent - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-17 | 175268 | RFMT-133063 | !! Our air conditioning system is broken. Contact Name: nick Contact Phone Number: Contact Email: 4O1BHA7 | 2016-10-18 - 18010 - Rene Arrieta-replace filter - Rene Arrieta | !! Our air conditioning system is broken. Contact Name: nick Contact Phone Number: Contact Email: 4O1BHA7 2016-10-18 - 18010 - Rene Arrieta-replace filter - Rene Arrieta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-10-17 | 175286 | RFMT-133045 | Res. Life HVAC Shop: Simon and Thor; Please repair or replace Hayden South Laundry Rooms Roof Top Exhaust Fan. Thank you. | 2016-10-18 - 18010 - Simon Fernandez-removed and replaced exhaust motor. Cleaned dryer vent, reinstalled venting. - Simon Fernandez | Res. Life HVAC Shop: Simon and Thor; Please repair or replace Hayden South Laundry Rooms Roof Top Exhaust Fan. Thank you. 2016-10-18 - 18010 - Simon Fernandez-removed and replaced exhaust motor. Cleaned dryer vent, reinstalled venting. - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-17 | 234022 | POLY-114177 | !! The air conditioning unit for the house is not working. Our house has a combined AC/Heating unit, and it is currently incapable of functioning for either purpose. Thank you! 4NCEM9H | NA | !! The air conditioning unit for the house is not working. Our house has a combined AC/Heating unit, and it is currently incapable of functioning for either purpose. Thank you! 4NCEM9H NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-17 | 255472 | DTPC-113066 | Perform fan coil maintenance on units 1-A, 1-C, 1-H, and 1-J. | 2016-10-17 - 18010 - James Hermann-perform maintenance checks and service to these fan coil units. They also need belt changes and adjustments. - James Hermann; 2016-10-23 - 18010 - James Hermann-Work complete as Ross requested to finish fan coils. - James Hermann | Perform fan coil maintenance on units 1-A, 1-C, 1-H, and 1-J. 2016-10-17 - 18010 - James Hermann-perform maintenance checks and service to these fan coil units. They also need belt changes and adjustments. - James Hermann; 2016-10-23 - 18010 - James Hermann-Work complete as Ross requested to finish fan coils. - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-17 | 255502 | DTPC-113036 | Filter | 2016-10-19 - 18170 - Ralph Lemons-Filters have been completed. There was one unit that would not turn back on and has since been fixed. All is working great at this time! - Ralph Lemons | Filter 2016-10-19 - 18170 - Ralph Lemons-Filters have been completed. There was one unit that would not turn back on and has since been fixed. All is working great at this time! - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-18 | 54648 | TMPE-195509 | GM Motors Important safety Recall your vehicle is involved in GM recall 49152. The vehicle is presently safe to drive, there is no need to take action now. You will be notified when parts are available to remedy your vehicle. The propellant in some types of Takata airbag inflators can degrade ov. . . | NA | GM Motors Important safety Recall your vehicle is involved in GM recall 49152. The vehicle is presently safe to drive, there is no need to take action now. You will be notified when parts are available to remedy your vehicle. The propellant in some types of Takata airbag inflators can degrade ov. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-18 | 54655 | TMPE-195502 | MWO: PSD 18 Fume hood alarming: due to duct work being disconnected from Exhaust Fan Y#3658 on west side of D Wing roof. | 2016-10-19 - 30000 - Michael Cozens-Found that the duct work on the roof had broken away from the exhaust fan. I turned over to HVAC sheetmetal for ASAP repair. - Mike Cozens | MWO: PSD 18 Fume hood alarming: due to duct work being disconnected from Exhaust Fan Y#3658 on west side of D Wing roof. 2016-10-19 - 30000 - Michael Cozens-Found that the duct work on the roof had broken away from the exhaust fan. I turned over to HVAC sheetmetal for ASAP repair. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 4
2016-10-18 | 54673 | TMPE-195484 | SWO: !! Good Afternoon. Weatherup center room 114U1 is too warm for the UPS equipment in the room. Room temp is in the 90's and needs to be mid to low 70's. Please have the A/C corrected to cool the room. Thank you 42B13D7 | 2016-10-20 - 18290 - Roque Garcia-Found the unit low of refrigerant R410. Nitrogen tested and found no leaks. Reassembly the unit and rechecked for leaks and no leaks found. Checked and tested good. - Roque Garcia | SWO: !! Good Afternoon. Weatherup center room 114U1 is too warm for the UPS equipment in the room. Room temp is in the 90's and needs to be mid to low 70's. Please have the A/C corrected to cool the room. Thank you 42B13D7 2016-10-20 - 18290 - Roque Garcia-Found the unit low of refrigerant R410. Nitrogen tested and found no leaks. Reassembly the unit and rechecked for leaks and no leaks found. Checked and tested good. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-18 | 54694 | TMPE-195463 | MWO Centerpoint 214-11 !! Repeat Request. The AC is not working in room 214-11 of the Centerpoint building again. Thermostat is completely off. Previous service requests were 233945 and 233763. Thank you. 4MO5454 | 2016-10-18 - 18010 - Brian Qualls-I pulled 2 techs off of jobs to bring spot coolers to this area. They are taking the coolers from other areas on campus to help at Center Point. - Brian Qualls; 2016-10-19 - 18010 - Zhi Yu-deliver and install portable A/C unit. - Zhi Yu; 2016-10-19 - 18010 - Jennifer Moyer-deliver and install portable A/C unit. - Zhi Yu; 2016-10-20 - 18010 - Zhi Yu-We diagnose the secondary transformer Common side wire loosen from the space terminal. We replaced space terminal. We cycle unit 3 time and split @ 20deg. - Zhi Yu; 2016-10-31 - 18010 - Jennifer Moyer-pick up portable ac. - Jennifer Moyer | MWO Centerpoint 214-11 !! Repeat Request. The AC is not working in room 214-11 of the Centerpoint building again. Thermostat is completely off. Previous service requests were 233945 and 233763. Thank you. 4MO5454 2016-10-18 - 18010 - Brian Qualls-I pulled 2 techs off of jobs to bring spot coolers to this area. They are taking the coolers from other areas on campus to help at Center Point. - Brian Qualls; 2016-10-19 - 18010 - Zhi Yu-deliver and install portable A/C unit. - Zhi Yu; 2016-10-19 - 18010 - Jennifer Moyer-deliver and install portable A/C unit. - Zhi Yu; 2016-10-20 - 18010 - Zhi Yu-We diagnose the secondary transformer Common side wire loosen from the space terminal. We replaced space terminal. We cycle unit 3 time and split @ 20deg. - Zhi Yu; 2016-10-31 - 18010 - Jennifer Moyer-pick up portable ac. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-18 | 54704 | TMPE-195453 | MWO MUSIC Library transferred to ac shop. There is a leak coming from the vent and the ceiling on and around column number M1700. | 2016-10-18 - 18010 - CANCEL PER BRIAN Q. DUPLICATE TO WO #194041. MM - Monica Moraga | MWO MUSIC Library transferred to ac shop. There is a leak coming from the vent and the ceiling on and around column number M1700. 2016-10-18 - 18010 - CANCEL PER BRIAN Q. DUPLICATE TO WO #194041. MM - Monica Moraga | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-18 | 54711 | TMPE-195446 | MWO GGMA 14 TRANSFER BT TO EL As far as I can tell it\\u2019s not the fuses. The paint wall goes down but does not come back up. URGENT! *ORIGINAL* The paint frame (used to paint backgrounds for sets) is not going up. Last time this broke it was a simple fuse. Please trouble shoot as soon as possibl. . . | 2016-10-27 - 15000 - Edward Howell-Checked all contactors and connections. the motor is bad and will not reverse. - Edward Howell | MWO GGMA 14 TRANSFER BT TO EL As far as I can tell it\\u2019s not the fuses. The paint wall goes down but does not come back up. URGENT! *ORIGINAL* The paint frame (used to paint backgrounds for sets) is not going up. Last time this broke it was a simple fuse. Please trouble shoot as soon as possibl. . . 2016-10-27 - 15000 - Edward Howell-Checked all contactors and connections. the motor is bad and will not reverse. - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-10-18 | 54768 | TMPE-195389 | SWO: ISTB1 336 The incubator that's outside of the alcove is not working. It's not reaching 37 degrees and it has killed our cells. Please send someone immediately. | 2016-10-25 - 18010 - Duane Rider-Bad compressor, heating element and door seal. Hi Melanie, Thank you for sending the estimate. Since the incubator is too old, we are not going to invest more money to repair it anymore. We have decided to purchase a new one. Best, Ying - Duane Rider | SWO: ISTB1 336 The incubator that's outside of the alcove is not working. It's not reaching 37 degrees and it has killed our cells. Please send someone immediately. 2016-10-25 - 18010 - Duane Rider-Bad compressor, heating element and door seal. Hi Melanie, Thank you for sending the estimate. Since the incubator is too old, we are not going to invest more money to repair it anymore. We have decided to purchase a new one. Best, Ying - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-18 | 255464 | DTPC-113074 | !! Several rooms, 462, 464, 466 all have no air flow from the AC system in the building, please adjust airflow 4NEK4FJ | 2016-10-18 - 18290 - Richard Noland-Saw WO, got tools and ladder. A/C unit is tripping out on high head pressure. Cleaned in line screen. Spoke on phone to a/c company that Stephen wants us to use. They will send quote to check out unit. Received quote and forward it to Sherry and Stephen for approval. - Richard Noland; 2016-10-19 - 18290 - Richard Noland-Met Mike from BLS Mechanical, he checked out unit and verified that it is a refrigerant issue causing the malfunctioning, he will submit a quote for repairs. - Richard Noland; 2016-11-10 - 18290 - Richard Noland-Part for heat pump repair has come in from MFG, they are scheduled to come out Thursday to repair unit. - Richard Noland; 2016-11-10 - 18290 - Richard Noland-Met vendor, took him to lobby at Health South. Building elevators are malfunctioning, made some phone calls, elevator still not working. They left and will be back next Tuesday for repair work. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Met vendor and took him to 4th floor, they are here to repair a/c unit. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Met vendor again to let him into 4th floor. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Vendor has finished repair, checked BMS and unit is working great. Let Tony know since is also supplies cool air for his office. Checked area, looks clean. WO is complete. - Richard Noland | !! Several rooms, 462, 464, 466 all have no air flow from the AC system in the building, please adjust airflow 4NEK4FJ 2016-10-18 - 18290 - Richard Noland-Saw WO, got tools and ladder. A/C unit is tripping out on high head pressure. Cleaned in line screen. Spoke on phone to a/c company that Stephen wants us to use. They will send quote to check out unit. Received quote and forward it to Sherry and Stephen for approval. - Richard Noland; 2016-10-19 - 18290 - Richard Noland-Met Mike from BLS Mechanical, he checked out unit and verified that it is a refrigerant issue causing the malfunctioning, he will submit a quote for repairs. - Richard Noland; 2016-11-10 - 18290 - Richard Noland-Part for heat pump repair has come in from MFG, they are scheduled to come out Thursday to repair unit. - Richard Noland; 2016-11-10 - 18290 - Richard Noland-Met vendor, took him to lobby at Health South. Building elevators are malfunctioning, made some phone calls, elevator still not working. They left and will be back next Tuesday for repair work. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Met vendor and took him to 4th floor, they are here to repair a/c unit. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Met vendor again to let him into 4th floor. - Richard Noland; 2016-11-15 - 18290 - Richard Noland-Vendor has finished repair, checked BMS and unit is working great. Let Tony know since is also supplies cool air for his office. Checked area, looks clean. WO is complete. - Richard Noland | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-19 | 54464 | TMPE-195693 | H.P Has bad motor, changed Cap. unit not running. | 2016-10-21 - 18230 - Thomas Gibble-replaced blower motor on HP 101 - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced blower motor on HP 101 - Thomas Gibble | H.P Has bad motor, changed Cap. unit not running. 2016-10-21 - 18230 - Thomas Gibble-replaced blower motor on HP 101 - Thomas Gibble; 2016-10-21 - 18230 - Gail Jackson-replaced blower motor on HP 101 - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-19 | 54509 | TMPE-195648 | MWO PSD D310 Low duct static airflow alarm for AH 4, Y#3642, came in due to dirty air filters. Send to HVAC for air filter change out ASAP. 42B213C | 2016-10-21 - 18170 - Thomas Gibble-replaced air filters - Thomas Gibble; 2016-10-21 - 18170 - Gail Jackson-replaced air filters - Thomas Gibble | MWO PSD D310 Low duct static airflow alarm for AH 4, Y#3642, came in due to dirty air filters. Send to HVAC for air filter change out ASAP. 42B213C 2016-10-21 - 18170 - Thomas Gibble-replaced air filters - Thomas Gibble; 2016-10-21 - 18170 - Gail Jackson-replaced air filters - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-10-19 | 54574 | TMPE-195583 | MWO: Assign to Bruce Feldhusen. Install unit service switches, alarm reset button, wait light and alarm light for the 8 lab exhaust fans. 4NI7MHC | NA | MWO: Assign to Bruce Feldhusen. Install unit service switches, alarm reset button, wait light and alarm light for the 8 lab exhaust fans. 4NI7MHC NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-19 | 54611 | TMPE-195546 | MWO Bio A: change to EMS: This is in the control side of fan coil. We have a Fan coil unit that makes a loud vibrating noise when it is in auto at the RIB. Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A | 2016-11-04 - 18090 - Michael Cozens-Found chattering fan coil contactor. Turned over to HVAC to checkout. - Mike Cozens | MWO Bio A: change to EMS: This is in the control side of fan coil. We have a Fan coil unit that makes a loud vibrating noise when it is in auto at the RIB. Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A 2016-11-04 - 18090 - Michael Cozens-Found chattering fan coil contactor. Turned over to HVAC to checkout. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-19 | 215084 | RACC-113526 | Clean vents. 4O17G8F | NA | Clean vents. 4O17G8F NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-19 | 215087 | RACC-113523 | One sink is clogged, the other will probably be clogged soon, so both need to be cleaned out. Our air conditioning filters were never changed out The door lock doesn't work properly Contact Name: Contact Phone Number: 7606601785 Contact Email: 4NND633 | NA | One sink is clogged, the other will probably be clogged soon, so both need to be cleaned out. Our air conditioning filters were never changed out The door lock doesn't work properly Contact Name: Contact Phone Number: 7606601785 Contact Email: 4NND633 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-10-19 | 255427 | DTPC-113111 | Their office is frigid cold. This has been an ongoing problem and the temp adjustments have not been working. They want to know if the vent can be covered or partially blocked off. | 2016-10-19 - 18300 - Steve Skibbe-valve and heat not responding changed config of unit for now to only run when called will investigate further at later date - Steve Skibbe; 2016-11-21 - 18300 - Steve Skibbe-valve inaccessible refer to Stephen about getting climatec involved - Steve Skibbe; 2016-11-23 - 18300 - Steve Skibbe-Brian with Climatec verified that the valve is bad and is working on a solution for replacement of plunger type retrofit pneumatic valve with ball valve and ddc operator - Steve Skibbe; 2016-12-20 - 18300 - Steve Skibbe-contacted Climatec they are still working on proposal sales man will have to come out and look at this too - Steve Skibbe | Their office is frigid cold. This has been an ongoing problem and the temp adjustments have not been working. They want to know if the vent can be covered or partially blocked off. 2016-10-19 - 18300 - Steve Skibbe-valve and heat not responding changed config of unit for now to only run when called will investigate further at later date - Steve Skibbe; 2016-11-21 - 18300 - Steve Skibbe-valve inaccessible refer to Stephen about getting climatec involved - Steve Skibbe; 2016-11-23 - 18300 - Steve Skibbe-Brian with Climatec verified that the valve is bad and is working on a solution for replacement of plunger type retrofit pneumatic valve with ball valve and ddc operator - Steve Skibbe; 2016-12-20 - 18300 - Steve Skibbe-contacted Climatec they are still working on proposal sales man will have to come out and look at this too - Steve Skibbe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3
2016-10-20 | 4025 | WEST-107224 | Please increase air flow to electric room. The transformer is running hot and there appears to only be a small exhaust vent. | 2016-10-26 - 18290 - Alfred Rohe-Inspected situation and found room supplied with a 6 in. supply duct with no return capability. The supply will have to be increased and a return added to properly cool this room. - Alfred Rohe; 2016-10-26 - 18290 - Chad T Ball-Assisted with inspection of area. - Alfred Rohe; 2016-11-08 - 18290 - Alfred Rohe-Cut a hole in ceiling and installed vent to area above hard lid. - Chad T Ball | Please increase air flow to electric room. The transformer is running hot and there appears to only be a small exhaust vent. 2016-10-26 - 18290 - Alfred Rohe-Inspected situation and found room supplied with a 6 in. supply duct with no return capability. The supply will have to be increased and a return added to properly cool this room. - Alfred Rohe; 2016-10-26 - 18290 - Chad T Ball-Assisted with inspection of area. - Alfred Rohe; 2016-11-08 - 18290 - Alfred Rohe-Cut a hole in ceiling and installed vent to area above hard lid. - Chad T Ball | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-10-20 | 54365 | TMPE-195792 | Add EL shop: Inspect noisy starter. Per Wesley Jackson HVAC Shop The contactor for the exhaust fan is noisy. The contactor is located in 119U1 | 2016-10-26 - 15000 - Edward Howell-Found no Unusual noises - Edward Howell | Add EL shop: Inspect noisy starter. Per Wesley Jackson HVAC Shop The contactor for the exhaust fan is noisy. The contactor is located in 119U1 2016-10-26 - 15000 - Edward Howell-Found no Unusual noises - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-20 | 54418 | TMPE-195739 | MWO: !! attn: Maintenance and HVAC, and Pest Control I am writing to request work on CSB 227, door on ramp to outside area and the ventilation in the room. The room fills with dirt and debris blown in from the outside area because of large gaps around the door and at the bottom. the door needs. . . | 2016-11-04 - 18010 - Robert Dauscher-Cleaned coil and replaced filter. Very obvious that room hasn't been occupied in a very long time. Numerous spider webs, and dust in area. HVAC items complete..... - Robert Dauscher | MWO: !! attn: Maintenance and HVAC, and Pest Control I am writing to request work on CSB 227, door on ramp to outside area and the ventilation in the room. The room fills with dirt and debris blown in from the outside area because of large gaps around the door and at the bottom. the door needs. . . 2016-11-04 - 18010 - Robert Dauscher-Cleaned coil and replaced filter. Very obvious that room hasn't been occupied in a very long time. Numerous spider webs, and dust in area. HVAC items complete..... - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-20 | 175110 | RFMT-133221 | Please repair Adelphi I J 208 HVAC evap unit condensation system. | 2016-10-21 - 18010 - Thor Millsaps-Cleaned primary and secondary drain pipes. Re-ran pipes for better flow. - Thor Millsaps | Please repair Adelphi I J 208 HVAC evap unit condensation system. 2016-10-21 - 18010 - Thor Millsaps-Cleaned primary and secondary drain pipes. Re-ran pipes for better flow. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-20 | 175111 | RFMT-133220 | Please repair Adelphi I J 208 HVAC evap unit condensation drain system. | 2016-10-21 - 18010 - Simon Fernandez-reworked condensate drain line,using 3/4 pvc fittings and pipe - Simon Fernandez | Please repair Adelphi I J 208 HVAC evap unit condensation drain system. 2016-10-21 - 18010 - Simon Fernandez-reworked condensate drain line,using 3/4 pvc fittings and pipe - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-20 | 175116 | RFMT-133215 | Please repair Adelphi I M 212 HVAC evap units condensation line system and check exhaust fan rough in. | 2016-10-20 - 18010 - Checked exhaust fan rough in very minor gap. Needs to be caulked - will contact project manager. - Gregory Stetka | Please repair Adelphi I M 212 HVAC evap units condensation line system and check exhaust fan rough in. 2016-10-20 - 18010 - Checked exhaust fan rough in very minor gap. Needs to be caulked - will contact project manager. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-20 | 175117 | RFMT-133214 | Please repair Adelphi I M 212 HVAC evap units condensation line system and check exhaust fan rough in. | 2016-10-21 - 18010 - Thor Millsaps-Cleaned condensate drain pipes. Re-ran primary and secondary pipes for better flow. - Thor Millsaps | Please repair Adelphi I M 212 HVAC evap units condensation line system and check exhaust fan rough in. 2016-10-21 - 18010 - Thor Millsaps-Cleaned condensate drain pipes. Re-ran primary and secondary pipes for better flow. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-20 | 175118 | RFMT-133213 | Please repair M 212 HVAC evap units condensation line system and check exhaust fan rough in. | 2016-10-20 - 18010 - Simon Fernandez-reworked condensate drain line - Simon Fernandez | Please repair M 212 HVAC evap units condensation line system and check exhaust fan rough in. 2016-10-20 - 18010 - Simon Fernandez-reworked condensate drain line - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-20 | 175120 | RFMT-133211 | Rewire the AC motor only works on high | 2016-10-21 - 18010 - Simon Fernandez-removed and replaced motor, ops checked okay - Simon Fernandez | Rewire the AC motor only works on high 2016-10-21 - 18010 - Simon Fernandez-removed and replaced motor, ops checked okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-20 | 175144 | RFMT-133187 | Please repair / adjust fan coil blower motor fir Hayden E 106. Thank you. | 2016-10-21 - 18010 - Thor Millsaps-Checked blower motor, belt, pully, bearings. Tightened loose connections on motor bracket and pully. Tested belt. System up and running. - Thor Millsaps | Please repair / adjust fan coil blower motor fir Hayden E 106. Thank you. 2016-10-21 - 18010 - Thor Millsaps-Checked blower motor, belt, pully, bearings. Tightened loose connections on motor bracket and pully. Tested belt. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-20 | 175145 | RFMT-133186 | Please repair / adjust fan coil blower motor fir Hayden E 106. Thank you. | 2016-10-20 - 18010 - Simon Fernandez-Checked a/c unit,motor assembly,spider assembly,and belt, all checked okay. Replaced (3) 16X25X2 filters. - Simon Fernandez | Please repair / adjust fan coil blower motor fir Hayden E 106. Thank you. 2016-10-20 - 18010 - Simon Fernandez-Checked a/c unit,motor assembly,spider assembly,and belt, all checked okay. Replaced (3) 16X25X2 filters. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-20 | 233937 | POLY-114262 | Service needed: Please change the outside air filter for the fan / ac (feel free to leave an extra one or two and I will change them during the cooler season) Special notes: Please call or text first If you need to enter the home, please be mindful that our silly 'ol dog Sandy lives here a. . . | NA | Service needed: Please change the outside air filter for the fan / ac (feel free to leave an extra one or two and I will change them during the cooler season) Special notes: Please call or text first If you need to enter the home, please be mindful that our silly 'ol dog Sandy lives here a. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-21 | 54076 | TMPE-196081 | ASUHC-Gabriel Ortiz Description: Both elevators are down and not working. Need to be fixed as soon as possible. Kid with a broken knee needs to get down but the elevators are down so he can't. Who was dispatched: Joe Swan Time of dispatch: 09:58PM ASUHC-jbreeze 1009pm Joe Swan called in with: . . . | NA | ASUHC-Gabriel Ortiz Description: Both elevators are down and not working. Need to be fixed as soon as possible. Kid with a broken knee needs to get down but the elevators are down so he can't. Who was dispatched: Joe Swan Time of dispatch: 09:58PM ASUHC-jbreeze 1009pm Joe Swan called in with: . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-10-21 | 54266 | TMPE-195891 | MWO: WILSON 217 The thermostat in my office (Wilson Hall 217) is broken, so that I receive max a/c or heat at all times (depending on what is on in the building). I have contacted facilities management multiple times over the past year (directly and through the school\\u2019s office manager), but the. . . | 2016-11-26 - 18010 - Roque Garcia-Replaced the faulty tstat and spoke with faculty member occupying the space and explained the work provided and the results. - Roque Garcia | MWO: WILSON 217 The thermostat in my office (Wilson Hall 217) is broken, so that I receive max a/c or heat at all times (depending on what is on in the building). I have contacted facilities management multiple times over the past year (directly and through the school\\u2019s office manager), but the. . . 2016-11-26 - 18010 - Roque Garcia-Replaced the faulty tstat and spoke with faculty member occupying the space and explained the work provided and the results. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-10-21 | 255364 | DTPC-113174 | There is a burning smell. It smells like it's coming from the HVAC | 2016-10-21 - 18020 - Steve Skibbe-smell like motor going bad shut off unit via ems - Steve Skibbe; 2016-10-24 - 18020 - Steve Skibbe-took unit apart to access motor and diagnose changed start cap to no avail determined it is a bad motor getting a quote to change motor - Steve Skibbe; 2016-11-16 - 18020 - Steve Skibbe-motor was replaced by vendor - Steve Skibbe | There is a burning smell. It smells like it's coming from the HVAC 2016-10-21 - 18020 - Steve Skibbe-smell like motor going bad shut off unit via ems - Steve Skibbe; 2016-10-24 - 18020 - Steve Skibbe-took unit apart to access motor and diagnose changed start cap to no avail determined it is a bad motor getting a quote to change motor - Steve Skibbe; 2016-11-16 - 18020 - Steve Skibbe-motor was replaced by vendor - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-21 | 255372 | DTPC-113166 | Pool heater repairs on unit #2/ blower motor and control board | 2016-10-21 - 24000 - Keith Griffin-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin; 2016-10-21 - 24000 - Robert Bartels-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin; 2016-10-21 - 24000 - Jose Acero-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin | Pool heater repairs on unit #2/ blower motor and control board 2016-10-21 - 24000 - Keith Griffin-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin; 2016-10-21 - 24000 - Robert Bartels-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin; 2016-10-21 - 24000 - Jose Acero-Pool heater repairs on unit #2/ blower motor and control board - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-22 | 55089 | TMPE-195068 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-22 | 55090 | TMPE-195067 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-22 | 215015 | RACC-113595 | !! Water is leaking from air conditioning duck 4NJDBA8 | NA | !! Water is leaking from air conditioning duck 4NJDBA8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-22 | 233877 | POLY-114322 | !! Resident says air conditioning went out. Claims that the fan is not circulating air. 4NL3HF9 | NA | !! Resident says air conditioning went out. Claims that the fan is not circulating air. 4NL3HF9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-23 | 53869 | TMPE-196288 | SWO: ASUHC-Agent: Kyle Van Bergen Description: alarm - room temp AC unit is tripped off Who was dispatched: Robert Dauscher Time of dispatch: 11:42am | 2016-10-25 - 30000 - 10-23-16 When I checked, I found that the room temperature was 88 degrees and that the DX unit was no longer cooling. I requested that HVAC tech be called in to check out AC unit. sb - Mike Cozens | SWO: ASUHC-Agent: Kyle Van Bergen Description: alarm - room temp AC unit is tripped off Who was dispatched: Robert Dauscher Time of dispatch: 11:42am 2016-10-25 - 30000 - 10-23-16 When I checked, I found that the room temperature was 88 degrees and that the DX unit was no longer cooling. I requested that HVAC tech be called in to check out AC unit. sb - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-23 | 54049 | TMPE-196108 | SWO: ASUHC-Agent: Kyle Van Bergen Description: alarm - room temp AC unit is tripped off Who was dispatched: Robert Dauscher Time of dispatch: 11:42am | 2016-11-04 - 18010 - Robert Dauscher-Found wire shorted phase to phase on contactor that had rubbed through wire casing. replaced contactor (burnt) and replaced wire. Call Complete. - Robert Dauscher | SWO: ASUHC-Agent: Kyle Van Bergen Description: alarm - room temp AC unit is tripped off Who was dispatched: Robert Dauscher Time of dispatch: 11:42am 2016-11-04 - 18010 - Robert Dauscher-Found wire shorted phase to phase on contactor that had rubbed through wire casing. replaced contactor (burnt) and replaced wire. Call Complete. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-24 | 53875 | TMPE-196282 | SWO HONHAL Hello, We are hearing a really loud motor on the roof that keeps kicking in and out. ACC said it was a main one with the hood system. Are you able to call someone out right away? It appears to have stopped all together. Thanks | 2016-11-04 - 18010 - Robert Dauscher-ACC escorted us to unit. Unit running properly. Not making any noise. Call complete. - Robert Dauscher; 2016-11-04 - 18010 - Thomas Gibble-ACC escorted us to unit. Unit running properly. Not making any noise. Call complete. - Robert Dauscher | SWO HONHAL Hello, We are hearing a really loud motor on the roof that keeps kicking in and out. ACC said it was a main one with the hood system. Are you able to call someone out right away? It appears to have stopped all together. Thanks 2016-11-04 - 18010 - Robert Dauscher-ACC escorted us to unit. Unit running properly. Not making any noise. Call complete. - Robert Dauscher; 2016-11-04 - 18010 - Thomas Gibble-ACC escorted us to unit. Unit running properly. Not making any noise. Call complete. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-24 | 53876 | TMPE-196281 | MWO: UCENT C I need to get the portable a/c unit out tomorrow 10/25/16 from the generator storage area located out back of Building C. Please coordinate with James Lawrence between 10:00am-1:00pm to have someone open the door. | 2016-10-28 - 11040 - Thomas Gibble-job was done - Thomas Gibble; 2016-10-28 - 11040 - Gail Jackson-job was done - Thomas Gibble | MWO: UCENT C I need to get the portable a/c unit out tomorrow 10/25/16 from the generator storage area located out back of Building C. Please coordinate with James Lawrence between 10:00am-1:00pm to have someone open the door. 2016-10-28 - 11040 - Thomas Gibble-job was done - Thomas Gibble; 2016-10-28 - 11040 - Gail Jackson-job was done - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-24 | 53926 | TMPE-196231 | MWO SCOB 290 !! CEM tested the fume hood in SCOB 290 (TAG # 10901) and the fume hood has no power. Please inform EH&S of the status of the repair and when the repair is completed so CEM can retest the fume hood. Contact Name: Contact Phone Number: 4809657673 Contact Email: | 2016-10-28 - 15000 - Samuel Gladden-Fixed problem with the circuit, proper voltage is at the motor , but motor is not working, HVAC should be contacted. - Samuel Gladden | MWO SCOB 290 !! CEM tested the fume hood in SCOB 290 (TAG # 10901) and the fume hood has no power. Please inform EH&S of the status of the repair and when the repair is completed so CEM can retest the fume hood. Contact Name: Contact Phone Number: 4809657673 Contact Email: 2016-10-28 - 15000 - Samuel Gladden-Fixed problem with the circuit, proper voltage is at the motor , but motor is not working, HVAC should be contacted. - Samuel Gladden | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-24 | 53946 | TMPE-196211 | MWO: Replace grounded motor on air compressor. Attn: Roque Garcia | 2016-11-26 - 18030 - Roque Garcia-Replaced the motor and tested ok. - Roque Garcia | MWO: Replace grounded motor on air compressor. Attn: Roque Garcia 2016-11-26 - 18030 - Roque Garcia-Replaced the motor and tested ok. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-24 | 53954 | TMPE-196203 | MWO: ASUHC-Agent: Ahmed Khalil Description: Flood in 3rd floor men's bathroom from sink and is leaking down to 2nd floor and no air conditioning. Who was dispatched: Tim for plumbing and Mike Cozens for AC Time of dispatch: 11:05AM ASUHC-Agent: Ahmed Khalil Tim called back to dispatch Olympu. . . | 2016-10-25 - 23070 - Timothy Handley-found bottle caps and paper towels stuffed in drain. pulled trap apart and cleared it. the aerator was gone so I replaced it with a new one - Timothy Handley | MWO: ASUHC-Agent: Ahmed Khalil Description: Flood in 3rd floor men's bathroom from sink and is leaking down to 2nd floor and no air conditioning. Who was dispatched: Tim for plumbing and Mike Cozens for AC Time of dispatch: 11:05AM ASUHC-Agent: Ahmed Khalil Tim called back to dispatch Olympu. . . 2016-10-25 - 23070 - Timothy Handley-found bottle caps and paper towels stuffed in drain. pulled trap apart and cleared it. the aerator was gone so I replaced it with a new one - Timothy Handley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-24 | 53962 | TMPE-196195 | MWO LSA Roof !! LSA, room 321, fume hood exhaust fan will not run. Please create a MWO for HVAC to troubleshoot Exhaust Fan Motor, y717, located on the roof so EH&S can certify the Hood. 42DIM5O | 2016-10-26 - 18190 - HVAC needs to troubleshoot then possibly replace fan motor - John Holloway; 2016-11-03 - 18190 - This MWO was sent to HVAC - John Holloway | MWO LSA Roof !! LSA, room 321, fume hood exhaust fan will not run. Please create a MWO for HVAC to troubleshoot Exhaust Fan Motor, y717, located on the roof so EH&S can certify the Hood. 42DIM5O 2016-10-26 - 18190 - HVAC needs to troubleshoot then possibly replace fan motor - John Holloway; 2016-11-03 - 18190 - This MWO was sent to HVAC - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-24 | 53988 | TMPE-196169 | MWO ISTB1 We need to have the air handler filters replaced 42DIMEB | NA | MWO ISTB1 We need to have the air handler filters replaced 42DIMEB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-24 | 174957 | RFMT-133374 | Please repair HVAV Evap unit condensate system in F 216. | 2016-10-25 - 18010 - Thor Millsaps-Disconnected primary drain line from air handler and re-ran new drain line. - Thor Millsaps | Please repair HVAV Evap unit condensate system in F 216. 2016-10-25 - 18010 - Thor Millsaps-Disconnected primary drain line from air handler and re-ran new drain line. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-24 | 174959 | RFMT-133372 | Please repair HVAV Evap unit condensate system in F 210. | 2016-10-25 - 18010 - Thor Millsaps-Disconnected primary drain line from air handler and re-ran new drain line. - Thor Millsaps | Please repair HVAV Evap unit condensate system in F 210. 2016-10-25 - 18010 - Thor Millsaps-Disconnected primary drain line from air handler and re-ran new drain line. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-24 | 214968 | RACC-113642 | AC broke,fifth or sixth time it has happened | NA | AC broke,fifth or sixth time it has happened NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-10-25 | 53732 | TMPE-196425 | MWO: Send to HVAC shop. Customer reports the EQ room above rm 135(up the stairs) has knocking sound. Airhandler MZ1 seems to be making the sound. I checked the belts. They look ok. Please check the AHU MZ1 AND maybe the other AHUs. 42C3NC4 | 2016-11-08 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2016-11-08 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2017-02-10 - 18050 - Jose Lopez-replaced two sets of belts was not able to find any other problem - Jose Lopez | MWO: Send to HVAC shop. Customer reports the EQ room above rm 135(up the stairs) has knocking sound. Airhandler MZ1 seems to be making the sound. I checked the belts. They look ok. Please check the AHU MZ1 AND maybe the other AHUs. 42C3NC4 2016-11-08 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2016-11-08 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2017-02-10 - 18050 - Jose Lopez-replaced two sets of belts was not able to find any other problem - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 53759 | TMPE-196398 | MWO: CSB - Air Compressor went into alarm and isn't running. HVAC to restart air compressor. 10/25/2016 2:50:35 PM 130.BOILERS.116ADX100.COMP-A Alarm 51 130.BOILERS.116DX100 Compressor Alarm Value Alarm Site Name ACADEMIC Item Descriptio. . . | 2016-10-25 - 18030 - Brian Qualls-Roque had been working on this today, had it turned to install belt. Advised him to call EMS whenhe does this to notify that they may get an alarm. Unit was running upon arrival. - Brian Qualls | MWO: CSB - Air Compressor went into alarm and isn't running. HVAC to restart air compressor. 10/25/2016 2:50:35 PM 130.BOILERS.116ADX100.COMP-A Alarm 51 130.BOILERS.116DX100 Compressor Alarm Value Alarm Site Name ACADEMIC Item Descriptio. . . 2016-10-25 - 18030 - Brian Qualls-Roque had been working on this today, had it turned to install belt. Advised him to call EMS whenhe does this to notify that they may get an alarm. Unit was running upon arrival. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-25 | 53856 | TMPE-196301 | Float switch in bad | 2016-10-25 - 18010 - Duane Rider-Troubleshoot unit, replaced contact in float switch - Duane Rider; 2016-12-05 - 18010 - Duane Rider-adjusted float and checked panel - Duane Rider | Float switch in bad 2016-10-25 - 18010 - Duane Rider-Troubleshoot unit, replaced contact in float switch - Duane Rider; 2016-12-05 - 18010 - Duane Rider-adjusted float and checked panel - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 53859 | TMPE-196298 | Heat Pump - Coil is dirty requires cleaning. | 2017-03-07 - 18090 - Jennifer Moyer-Look at job to schedule maintenance/repair. - Jennifer Moyer; 2017-05-11 - 18090 - Room is scheduled for Wednesday May 17th 7am-10am. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer-Cleaning scheduled wednesday 7-10 - Jennifer Moyer; 2017-05-17 - 18090 - Jennifer Moyer-Changed filter (old one plugged solid). Coil didn't look too bad, but I put foaming coil cleaner on it anyway. - Jennifer Moyer | Heat Pump - Coil is dirty requires cleaning. 2017-03-07 - 18090 - Jennifer Moyer-Look at job to schedule maintenance/repair. - Jennifer Moyer; 2017-05-11 - 18090 - Room is scheduled for Wednesday May 17th 7am-10am. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer-Cleaning scheduled wednesday 7-10 - Jennifer Moyer; 2017-05-17 - 18090 - Jennifer Moyer-Changed filter (old one plugged solid). Coil didn't look too bad, but I put foaming coil cleaner on it anyway. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-10-25 | 53868 | TMPE-196289 | Heat pump has dirty coil, requires cleaning. | 2017-03-07 - 18090 - Jennifer Moyer-Locate job and schedule maintenance/repair. - Jennifer Moyer; 2017-03-22 - 18090 - Jennifer Moyer-Clean evaporator coil. - Jennifer Moyer | Heat pump has dirty coil, requires cleaning. 2017-03-07 - 18090 - Jennifer Moyer-Locate job and schedule maintenance/repair. - Jennifer Moyer; 2017-03-22 - 18090 - Jennifer Moyer-Clean evaporator coil. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-25 | 174923 | RFMT-133408 | Door to door program for Adelphi I Clusters C & D. | 2016-10-26 - 10010 - Salvatore Marasco Jr-Located A.C. air filters and familiarized myself with job location, completed door to door process of the Adelphi 1 C&amp;D. - Salvatore Marasco Jr | Door to door program for Adelphi I Clusters C & D. 2016-10-26 - 10010 - Salvatore Marasco Jr-Located A.C. air filters and familiarized myself with job location, completed door to door process of the Adelphi 1 C&amp;D. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 214881 | RACC-113729 | !! Water is leaking from the AC unit that is in my bathroom and the same AC unit works sporadically. 4N835AE | NA | !! Water is leaking from the AC unit that is in my bathroom and the same AC unit works sporadically. 4N835AE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 214882 | RACC-113728 | Air conditioning unit no longer working or responding to thermostat. 4N835AE | NA | Air conditioning unit no longer working or responding to thermostat. 4N835AE NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 255257 | DTPC-113281 | A/c sensor on wall is malfunctioning, check it out. 42DI58M | 2016-10-25 - 18010 - Richard Noland-A/C sensor for heat pump 3-15 is malfunctioning. Removed it and put sensor from IDF room in its place. Heat pump 3-15 is functioning correctly now. IDR unit is now malfunctioning. A new sensor was ordered and received on Monday. Installed new sensor in IDF room and that a/c unit is functioning correctly. Checked BMS thru out day is all OK. WO is complete. - Richard Noland | A/c sensor on wall is malfunctioning, check it out. 42DI58M 2016-10-25 - 18010 - Richard Noland-A/C sensor for heat pump 3-15 is malfunctioning. Removed it and put sensor from IDF room in its place. Heat pump 3-15 is functioning correctly now. IDR unit is now malfunctioning. A new sensor was ordered and received on Monday. Installed new sensor in IDF room and that a/c unit is functioning correctly. Checked BMS thru out day is all OK. WO is complete. - Richard Noland | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-25 | 255262 | DTPC-113276 | Package unit for the hallway is not cooling and the thermostat is blank. Please troubleshoot. | 2016-10-25 - 18290 - James Hermann-Went to roof and reset unit as well as blown low voltage fuse. Unit ran for 5 minutes and lockout again. Checked components and found a bad econ board. Had BLS confirm the diagnosis and Mike will submit a price for replacement. - James Hermann | Package unit for the hallway is not cooling and the thermostat is blank. Please troubleshoot. 2016-10-25 - 18290 - James Hermann-Went to roof and reset unit as well as blown low voltage fuse. Unit ran for 5 minutes and lockout again. Checked components and found a bad econ board. Had BLS confirm the diagnosis and Mike will submit a price for replacement. - James Hermann | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-10-25 | 255264 | DTPC-113274 | No cooling in data and electrical room for building "A". Thermostat is blank. Please troubleshoot. | 2016-10-25 - 18290 - James Hermann-Replaced batteries in the thermostat. Unit still did not cool. Checked condensing unit on roof and their was no call from the evaporator unit. Traced duct work in suite A150. Evap unit for the electrical room is located in A130. Unit was not running and BLS finished the troubleshoot and found a blown low voltage fuse. Work is complete. - James Hermann | No cooling in data and electrical room for building "A". Thermostat is blank. Please troubleshoot. 2016-10-25 - 18290 - James Hermann-Replaced batteries in the thermostat. Unit still did not cool. Checked condensing unit on roof and their was no call from the evaporator unit. Traced duct work in suite A150. Evap unit for the electrical room is located in A130. Unit was not running and BLS finished the troubleshoot and found a blown low voltage fuse. Work is complete. - James Hermann | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-10-25 | 255285 | DTPC-113253 | Check into why heat pump 3-20 is showing NR in BMS. 42DI58M | 2016-10-25 - 18010 - Richard Noland-While checking BMS notice heat pump 3-20 was not on line, showed NR. Got tools and checked out heat pump. Had to move fire alarm notice in ceiling tile front of disconnect. Once that was done, found center fuse blown in electrical disconnect. Replaced fuse and a/c unit is back on line and cooling. WO is complete. - Richard Noland | Check into why heat pump 3-20 is showing NR in BMS. 42DI58M 2016-10-25 - 18010 - Richard Noland-While checking BMS notice heat pump 3-20 was not on line, showed NR. Got tools and checked out heat pump. Had to move fire alarm notice in ceiling tile front of disconnect. Once that was done, found center fuse blown in electrical disconnect. Replaced fuse and a/c unit is back on line and cooling. WO is complete. - Richard Noland | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-26 | 53560 | TMPE-196597 | MWO: My ophthalmologist recently recommended that I adjust my office environment to combat eye strain. I was wondering if we could do something about the section of florescent lights that create glare on my computer screen and the air vent in those lights that blows dust directly down on my desk. . . | 2016-10-27 - 18010 - Jeffrey Burnett-blocked air supply vents directly over desk per customers request. - Jeffrey Burnett | MWO: My ophthalmologist recently recommended that I adjust my office environment to combat eye strain. I was wondering if we could do something about the section of florescent lights that create glare on my computer screen and the air vent in those lights that blows dust directly down on my desk. . . 2016-10-27 - 18010 - Jeffrey Burnett-blocked air supply vents directly over desk per customers request. - Jeffrey Burnett | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-10-26 | 53561 | TMPE-196596 | MWO: My ophthalmologist recently recommended that I adjust my office environment to combat eye strain. I was wondering if we could do something about the section of florescent lights that create glare on my computer screen and the air vent in those lights that blows dust directly down on my desk. . . | 2016-10-27 - 15040 - Jeffrey Burnett-removed 2 bulbs from fixture per customer request. - Jeffrey Burnett | MWO: My ophthalmologist recently recommended that I adjust my office environment to combat eye strain. I was wondering if we could do something about the section of florescent lights that create glare on my computer screen and the air vent in those lights that blows dust directly down on my desk. . . 2016-10-27 - 15040 - Jeffrey Burnett-removed 2 bulbs from fixture per customer request. - Jeffrey Burnett | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-26 | 53601 | TMPE-196556 | The condensate return pump seal is leaking | 2016-12-30 - 23100 - Jose Lopez-work in progress on pump#1 this work order has 2 pumps not working - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose is working on pumps #1 &amp; #2. both are going to be replaced, as of 3/3/17 work is in progress, this will take the rest of the month as he waiting for condensation to stop. JB - Juliana Blusiewicz; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez | The condensate return pump seal is leaking 2016-12-30 - 23100 - Jose Lopez-work in progress on pump#1 this work order has 2 pumps not working - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose is working on pumps #1 &amp; #2. both are going to be replaced, as of 3/3/17 work is in progress, this will take the rest of the month as he waiting for condensation to stop. JB - Juliana Blusiewicz; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-26 | 53626 | TMPE-196531 | SWO: !! Transferred to EL Shop to wire from air handler f disconnect thru hand off Auto to motor contactor so air handler f can be run in hand. Please see Mike Cozens for further details 480.330.3235. EMS WO#179494, EL WO#179494. 2nd floor meeting space air conditioning not working I have a. . . | 2016-10-28 - 15000 - Semeon Haile-Wired in RIB relay to serve as hand switch - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Resolve AH F problem - Gary Conover; 2016-10-28 - 15000 - Gary Conover-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Gary Conover-AH F repairs complete - Gary Conover | SWO: !! Transferred to EL Shop to wire from air handler f disconnect thru hand off Auto to motor contactor so air handler f can be run in hand. Please see Mike Cozens for further details 480.330.3235. EMS WO#179494, EL WO#179494. 2nd floor meeting space air conditioning not working I have a. . . 2016-10-28 - 15000 - Semeon Haile-Wired in RIB relay to serve as hand switch - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Semeon Haile-Resolve AH F problem - Gary Conover; 2016-10-28 - 15000 - Gary Conover-Troubleshoot AH F - Gary Conover; 2016-10-28 - 15000 - Gary Conover-AH F repairs complete - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-10-26 | 53651 | TMPE-196506 | SWO VBHALL Dining Hall There is a cooling unit that isnt holding temp, is freezing up and also there is an electrical type of smell coming from the back of it. Please inspect asap. Thank you! | 2016-10-26 - 18100 - Called out to Steve - Amanda Thomas; 2016-10-27 - 18100 - Zhi Yu-Arrived we didn't smell burning wire. Notice Evap coil ice-up. We Check defrost timer not turning of the solenoid valve, and termination switch malfunction. We need to schedule to rewire. - Zhi Yu; 2016-10-27 - 18100 - Oner Munoz-Arrived we didn't smell burning wire. Notice Evap coil ice-up. We Check defrost timer not turning of the solenoid valve, and termination switch malfunction. We need to schedule to rewire. - Zhi Yu; 2016-10-31 - 18100 - Zhi Yu-We rewire the pizza reach-in cooler,adjust timer, bypass drain heater and reroute drain line the nears floor drain. - Zhi Yu; 2016-11-02 - 18100 - Zhi Yu-follow-up two cooler holding @ 37deg. - Zhi Yu | SWO VBHALL Dining Hall There is a cooling unit that isnt holding temp, is freezing up and also there is an electrical type of smell coming from the back of it. Please inspect asap. Thank you! 2016-10-26 - 18100 - Called out to Steve - Amanda Thomas; 2016-10-27 - 18100 - Zhi Yu-Arrived we didn't smell burning wire. Notice Evap coil ice-up. We Check defrost timer not turning of the solenoid valve, and termination switch malfunction. We need to schedule to rewire. - Zhi Yu; 2016-10-27 - 18100 - Oner Munoz-Arrived we didn't smell burning wire. Notice Evap coil ice-up. We Check defrost timer not turning of the solenoid valve, and termination switch malfunction. We need to schedule to rewire. - Zhi Yu; 2016-10-31 - 18100 - Zhi Yu-We rewire the pizza reach-in cooler,adjust timer, bypass drain heater and reroute drain line the nears floor drain. - Zhi Yu; 2016-11-02 - 18100 - Zhi Yu-follow-up two cooler holding @ 37deg. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2016-10-26 | 174804 | RFMT-133527 | Please order spare evap unit blower motor for shelf stock. | 2016-10-27 - 18010 - Thor Millsaps-Will wait to order motor until one fails and model/part # is obtained. - Thor Millsaps | Please order spare evap unit blower motor for shelf stock. 2016-10-27 - 18010 - Thor Millsaps-Will wait to order motor until one fails and model/part # is obtained. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-26 | 174805 | RFMT-133526 | Please order spare evap unit blower motor for shelf stock. | 2016-11-01 - 18010 - Thor Millsaps-Tino has 2 ECM blower motors in stock at warehouse. - Thor Millsaps | Please order spare evap unit blower motor for shelf stock. 2016-11-01 - 18010 - Thor Millsaps-Tino has 2 ECM blower motors in stock at warehouse. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-26 | 174816 | RFMT-133515 | RES LIFE / Thor: A/C wall pak coil leak on hot side. Please repair. | 2016-12-14 - 18010 - Thor Millsaps-Removed coil and repaired leak on heating water side. Brazed coil to seal leak. System up and running. Tested in heating and cooling. - Thor Millsaps | RES LIFE / Thor: A/C wall pak coil leak on hot side. Please repair. 2016-12-14 - 18010 - Thor Millsaps-Removed coil and repaired leak on heating water side. Brazed coil to seal leak. System up and running. Tested in heating and cooling. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-26 | 174875 | RFMT-133456 | Adelphi I - H, J & K Cluster door to door program. | 2016-10-26 - 10010 - Salvatore Marasco Jr-Completed door to door process and changed all A.C. filters. - Salvatore Marasco Jr | Adelphi I - H, J & K Cluster door to door program. 2016-10-26 - 10010 - Salvatore Marasco Jr-Completed door to door process and changed all A.C. filters. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-26 | 28448 | TMPE-221709 | Tennant Sales and service company machine tested and running service labor, site visit, machine tested, hub, adapter, brush, cable, gvl, ,pivot wldt brush, side bracket, mtg, motor side brush total: 866.71 | NA | Tennant Sales and service company machine tested and running service labor, site visit, machine tested, hub, adapter, brush, cable, gvl, ,pivot wldt brush, side bracket, mtg, motor side brush total: 866.71 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 53432 | TMPE-196725 | SWO UNIVT 105 !! Parking & Transit Office: Room 105. A/C serving area behind Permit Sales is Blowing Hot air. Employees say TEMP offfice is at 80 degrees. COP: Cathy Harrison 42B9D6L | 2016-10-27 - 18290 - Matthew Smith-Found unit low on refrigerant. Added 2.5 lbs of R-22 and cleaned the evaporator. Was unable to locate the leak. Submitted a request to the AC shop to look into replacing the unit as the unit is over 30 years old. Unit had a 20 degree split between the supply and return when the tech left. - Matthew Smith | SWO UNIVT 105 !! Parking & Transit Office: Room 105. A/C serving area behind Permit Sales is Blowing Hot air. Employees say TEMP offfice is at 80 degrees. COP: Cathy Harrison 42B9D6L 2016-10-27 - 18290 - Matthew Smith-Found unit low on refrigerant. Added 2.5 lbs of R-22 and cleaned the evaporator. Was unable to locate the leak. Submitted a request to the AC shop to look into replacing the unit as the unit is over 30 years old. Unit had a 20 degree split between the supply and return when the tech left. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-27 | 53435 | TMPE-196722 | Motor needs bearing replaced, 6313, 6312 | 2016-11-15 - 18050 - Duane Rider-Replaced bearing on 200hp motor - Duane Rider | Motor needs bearing replaced, 6313, 6312 2016-11-15 - 18050 - Duane Rider-Replaced bearing on 200hp motor - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-27 | 53484 | TMPE-196673 | Bad exhaust fan. Roque, See me before you go on this, Check to see if this is the same fan we were talking about for the laundry room. Electricians connected power to that one on Friday 10/28. We need to see what should control it. SP | 2017-02-07 - 18160 - Roque Garcia-Checked and found no power at the MCC bucket - Roque Garcia | Bad exhaust fan. Roque, See me before you go on this, Check to see if this is the same fan we were talking about for the laundry room. Electricians connected power to that one on Friday 10/28. We need to see what should control it. SP 2017-02-07 - 18160 - Roque Garcia-Checked and found no power at the MCC bucket - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 53532 | TMPE-196625 | MWO PSD D18 inline fan motor not operating.need mechanical shop. contact Mike Cozens @ 480-330-3235.Low airflow to clean room. Send to EMS Mike Cozens 42B213C | 2016-11-03 - 18010 - Gail Jackson-Carl showed me location of unit, we determined motor mounts had broke damaged motor and squirrel cage. Carpenter shop required for safe removal and minimize damage to equipment. - Gail Jackson; 2016-11-03 - 18010 - Carl Karr-Carl showed me location of unit, we determined motor mounts had broke damaged motor and squirrel cage. Carpenter shop required for safe removal and minimize damage to equipment. - Gail Jackson; 2016-11-03 - 18010 - Gail Jackson-Removed ceiling tile, lights and blower assembly. Reinstalled tiles and lights. Trip to Grainger, Webbs, Johnstone and RSD for parts. Order motor Johnstone, Blower wheel RSD.next day air. - Gail Jackson; 2016-11-03 - 18010 - Derek Gittings-Removed ceiling tile, lights and blower assembly. Reinstalled tiles and lights. Trip to Grainger, Webbs, Johnstone and RSD for parts. Order motor Johnstone, Blower wheel RSD.next day air. - Gail Jackson; 2016-11-04 - 18010 - Gail Jackson-Trip to Johnstone to pick up motor - Gail Jackson; 2016-11-04 - 18010 - Thomas Gibble-Trip to Johnstone to pick up motor - Gail Jackson; 2016-11-08 - 18010 - Gail Jackson-Trip to RSD Mesa to pick up part. - Gail Jackson; 2016-11-09 - 18010 - Gail Jackson-Assembled fan blower in shop; bench run test. Installed blower back in housing, run test adjust air flow. - Gail Jackson; 2016-11-09 - 18010 - Carl Karr-Assembled fan blower in shop; bench run test. Installed blower back in housing, run test adjust air flow. Trip to shop for tools. - Gail Jackson | MWO PSD D18 inline fan motor not operating.need mechanical shop. contact Mike Cozens @ 480-330-3235.Low airflow to clean room. Send to EMS Mike Cozens 42B213C 2016-11-03 - 18010 - Gail Jackson-Carl showed me location of unit, we determined motor mounts had broke damaged motor and squirrel cage. Carpenter shop required for safe removal and minimize damage to equipment. - Gail Jackson; 2016-11-03 - 18010 - Carl Karr-Carl showed me location of unit, we determined motor mounts had broke damaged motor and squirrel cage. Carpenter shop required for safe removal and minimize damage to equipment. - Gail Jackson; 2016-11-03 - 18010 - Gail Jackson-Removed ceiling tile, lights and blower assembly. Reinstalled tiles and lights. Trip to Grainger, Webbs, Johnstone and RSD for parts. Order motor Johnstone, Blower wheel RSD.next day air. - Gail Jackson; 2016-11-03 - 18010 - Derek Gittings-Removed ceiling tile, lights and blower assembly. Reinstalled tiles and lights. Trip to Grainger, Webbs, Johnstone and RSD for parts. Order motor Johnstone, Blower wheel RSD.next day air. - Gail Jackson; 2016-11-04 - 18010 - Gail Jackson-Trip to Johnstone to pick up motor - Gail Jackson; 2016-11-04 - 18010 - Thomas Gibble-Trip to Johnstone to pick up motor - Gail Jackson; 2016-11-08 - 18010 - Gail Jackson-Trip to RSD Mesa to pick up part. - Gail Jackson; 2016-11-09 - 18010 - Gail Jackson-Assembled fan blower in shop; bench run test. Installed blower back in housing, run test adjust air flow. - Gail Jackson; 2016-11-09 - 18010 - Carl Karr-Assembled fan blower in shop; bench run test. Installed blower back in housing, run test adjust air flow. Trip to shop for tools. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2016-10-27 | 53533 | TMPE-196624 | MWO SCOB 338D PL transfer to AC: make repairs to the Heating Coil at Schwada from Plumbing's work order # 191536 from all the way back in September 30, Severe leak in the roof/ceiling of this room. Possibly a burst pipe. Lots of water on the floor... | 2016-11-17 - 18090 - Zhi Yu-We when over to schwada room 338D. No leaks appears and I contact requestor Pamela Downs. she said the leaks is repair and tiles replaced on the 11/14/16. - Zhi Yu | MWO SCOB 338D PL transfer to AC: make repairs to the Heating Coil at Schwada from Plumbing's work order # 191536 from all the way back in September 30, Severe leak in the roof/ceiling of this room. Possibly a burst pipe. Lots of water on the floor... 2016-11-17 - 18090 - Zhi Yu-We when over to schwada room 338D. No leaks appears and I contact requestor Pamela Downs. she said the leaks is repair and tiles replaced on the 11/14/16. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-27 | 53539 | TMPE-196618 | MWO: Good morning, last night in ECA-141 we had a under the floor water detection alarm. We checked and found leakage from the chilled water Liebert A/C unit in the room on the south wall. We shut off the A/C unit and water has dried. Could I have one of the A/C guys meet me tomorrow morni. . . | 2016-10-28 - 18010 - Carl Karr-Clear condensate line. - Carl Karr; 2016-10-28 - 18010 - Gail Jackson-Clear condensate line. - Carl Karr; 2016-10-28 - 18010 - Midhat Mukanovic-Clear condensate line. - Carl Karr; 2016-10-31 - 18010 - Carl Karr-Insulate chilled water lines. - Carl Karr | MWO: Good morning, last night in ECA-141 we had a under the floor water detection alarm. We checked and found leakage from the chilled water Liebert A/C unit in the room on the south wall. We shut off the A/C unit and water has dried. Could I have one of the A/C guys meet me tomorrow morni. . . 2016-10-28 - 18010 - Carl Karr-Clear condensate line. - Carl Karr; 2016-10-28 - 18010 - Gail Jackson-Clear condensate line. - Carl Karr; 2016-10-28 - 18010 - Midhat Mukanovic-Clear condensate line. - Carl Karr; 2016-10-31 - 18010 - Carl Karr-Insulate chilled water lines. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-27 | 53554 | TMPE-196603 | Found pump in Tunnel entrance not working shaft/motor seized. | NA | Found pump in Tunnel entrance not working shaft/motor seized. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-27 | 174746 | RFMT-133585 | Please repair Adelphi I E 212 HVAC condensation drain system. | 2016-11-01 - 18010 - Thor Millsaps-Removed primary drain line from air handler and re-ran new drain line. Room is actually B210, not E210 - Thor Millsaps | Please repair Adelphi I E 212 HVAC condensation drain system. 2016-11-01 - 18010 - Thor Millsaps-Removed primary drain line from air handler and re-ran new drain line. Room is actually B210, not E210 - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 174751 | RFMT-133580 | !! AC need to be fixed 4NM28MA | 2016-10-28 - 18290 - Joe Swan-A/C was working when I arrived. Did so occupant were the on and off switch was located. - Joe Swan | !! AC need to be fixed 4NM28MA 2016-10-28 - 18290 - Joe Swan-A/C was working when I arrived. Did so occupant were the on and off switch was located. - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 174771 | RFMT-133560 | Big burner on over is not working. Bathroom smells terrible if we don't have fan on, also bathroom ceiling and walls have mildew all over them. Room is very dusty, air vents are blowing out dust, can see black dust on the ceiling by the living room air vent. 4NO14EG | 2016-10-28 - 10010 - Thomas Zambrano-repaired burner. bath room smell is not from anything that pertains to maint., changed filer on a/c unit. the mildew needs to be cleaned and there is dust on the ceilin that needs cleaned. - Thomas Zambrano | Big burner on over is not working. Bathroom smells terrible if we don't have fan on, also bathroom ceiling and walls have mildew all over them. Room is very dusty, air vents are blowing out dust, can see black dust on the ceiling by the living room air vent. 4NO14EG 2016-10-28 - 10010 - Thomas Zambrano-repaired burner. bath room smell is not from anything that pertains to maint., changed filer on a/c unit. the mildew needs to be cleaned and there is dust on the ceilin that needs cleaned. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-27 | 174789 | RFMT-133542 | !! Our air conditioning is broken; this has happened twice already this semester - maintenance had to come in and 'de-freeze' the air conditioning. 4NJOCK2 | 2016-10-27 - 18290 - Salvatore Marasco Jr-Checked A.C. unit finding it in good working order, however there was a piece of furniture in front of the inlet vent which may have been restricting air flow through fan coil. - Salvatore Marasco Jr | !! Our air conditioning is broken; this has happened twice already this semester - maintenance had to come in and 'de-freeze' the air conditioning. 4NJOCK2 2016-10-27 - 18290 - Salvatore Marasco Jr-Checked A.C. unit finding it in good working order, however there was a piece of furniture in front of the inlet vent which may have been restricting air flow through fan coil. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2016-10-27 | 214794 | RACC-113816 | !! Fix our air conditioner controller since it is not working properly. 4O0B818 | NA | !! Fix our air conditioner controller since it is not working properly. 4O0B818 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 214810 | RACC-113800 | !! Hello, In our suite, Both hallway lightbulbs are out. The light over the kitchen island is out. The air condition unit in between rooms C & D is leaking on the floor. The right blind opener rod in our family room is disconnected. Room D's sink is clogged Room B's shower is clogged. The l. . . | NA | !! Hello, In our suite, Both hallway lightbulbs are out. The light over the kitchen island is out. The air condition unit in between rooms C & D is leaking on the floor. The right blind opener rod in our family room is disconnected. Room D's sink is clogged Room B's shower is clogged. The l. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-27 | 233741 | POLY-114458 | CALLED STEVE !! The compressed air is down to the lab in Tech 199, we have equipment that need the compressed air to run. Please either turn the air back on or let us know whats the status and when it will be back up so we can act accordingly. Thx 42B2GAA | NA | CALLED STEVE !! The compressed air is down to the lab in Tech 199, we have equipment that need the compressed air to run. Please either turn the air back on or let us know whats the status and when it will be back up so we can act accordingly. Thx 42B2GAA NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-27 | 233951 | POLY-114248 | Coils | 2017-02-17 - 18090 - Allan Blair-SERVICED UNITS, REPLACED AIR FILTERS - Steve Clark; 2017-02-17 - 18090 - Darusman Amin-SERVICED UNITS, REPLACED AIR FILTERS - Steve Clark | Coils 2017-02-17 - 18090 - Allan Blair-SERVICED UNITS, REPLACED AIR FILTERS - Steve Clark; 2017-02-17 - 18090 - Darusman Amin-SERVICED UNITS, REPLACED AIR FILTERS - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-28 | 53251 | TMPE-196906 | MWO SCOB 290 EL to AC: EL has determined that the motor is bad. !! CEM tested the fume hood in SCOB 290 (TAG # 10901) and the fume hood has no power. Please inform EH&S of the status of the repair and when the repair is completed so CEM can retest the fume hood. Contact Name: Contact Ph. . . | 2016-11-09 - 18230 - Zhi Yu-replaced motor and sheave and turn out bad blow bearing. We removed Bearing back to shop. - Zhi Yu; 2016-11-14 - 18230 - Zhi Yu-assemble the double bearing house at the shop and when back the Schwada. We install the bearing and motor. - Zhi Yu | MWO SCOB 290 EL to AC: EL has determined that the motor is bad. !! CEM tested the fume hood in SCOB 290 (TAG # 10901) and the fume hood has no power. Please inform EH&S of the status of the repair and when the repair is completed so CEM can retest the fume hood. Contact Name: Contact Ph. . . 2016-11-09 - 18230 - Zhi Yu-replaced motor and sheave and turn out bad blow bearing. We removed Bearing back to shop. - Zhi Yu; 2016-11-14 - 18230 - Zhi Yu-assemble the double bearing house at the shop and when back the Schwada. We install the bearing and motor. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-28 | 53262 | TMPE-196895 | MWO ALMDB 154 EMS transfer to AC:it's the compressor per Mike Cozens !! It is reported, "The temperature in the alcohol collection has been rather high over the past week, currently 79 degrees. Can this be adjusted?" PLEASE NOTE: Temperatures being too warm in this room could be detrimental to . . . | 2016-11-18 - 18290 - Robert Dauscher-Checked unit found tripped high pressure switches on both compressors. reset both switches and unit is now working properly - Robert Dauscher | MWO ALMDB 154 EMS transfer to AC:it's the compressor per Mike Cozens !! It is reported, "The temperature in the alcohol collection has been rather high over the past week, currently 79 degrees. Can this be adjusted?" PLEASE NOTE: Temperatures being too warm in this room could be detrimental to . . . 2016-11-18 - 18290 - Robert Dauscher-Checked unit found tripped high pressure switches on both compressors. reset both switches and unit is now working properly - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-28 | 53334 | TMPE-196823 | MWO: EMS transfer to AC: heat pump needs to be fixed, unit only putting out 70 degrees per Mike Cozens Attn: HVAC shop Our special collections room (120M) is running at too high temperature this week, near 80 degrees. It seems the A/C is not working properly, as this room should be kept cool for . . . | 2016-11-14 - 18290 - Jennifer Moyer-Trouble shoot unit.Circuit 1 was low on refrigerant. Schrader valve was loose. Circuit 2 will not activate. Purchased new filters and coil cleaner to ensure proper air flow. Both circuits are energized according to central plant operations. - Jennifer Moyer; 2016-11-14 - 18290 - Jennifer Moyer-Install new filters. Contact central plant to confirm unit I.D. and adjust set points for cooling operation. Replaced contactor. - Jennifer Moyer; 2016-11-14 - 18290 - Jennifer Moyer-Run unit through test operation. Unit is functional. - Jennifer Moyer | MWO: EMS transfer to AC: heat pump needs to be fixed, unit only putting out 70 degrees per Mike Cozens Attn: HVAC shop Our special collections room (120M) is running at too high temperature this week, near 80 degrees. It seems the A/C is not working properly, as this room should be kept cool for . . . 2016-11-14 - 18290 - Jennifer Moyer-Trouble shoot unit.Circuit 1 was low on refrigerant. Schrader valve was loose. Circuit 2 will not activate. Purchased new filters and coil cleaner to ensure proper air flow. Both circuits are energized according to central plant operations. - Jennifer Moyer; 2016-11-14 - 18290 - Jennifer Moyer-Install new filters. Contact central plant to confirm unit I.D. and adjust set points for cooling operation. Replaced contactor. - Jennifer Moyer; 2016-11-14 - 18290 - Jennifer Moyer-Run unit through test operation. Unit is functional. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2016-10-28 | 174661 | RFMT-133670 | !! Air conditioner sounds like it is working, sometimes works and stays cool other times extremely hot, does not feel frozen over we have tried shutting it off and letting it sit and still does not work. 4NH2O0F | 2016-11-01 - 18010 - Simon Fernandez-checked a/c unit found breaker tripped reset ops checked okay - Simon Fernandez | !! Air conditioner sounds like it is working, sometimes works and stays cool other times extremely hot, does not feel frozen over we have tried shutting it off and letting it sit and still does not work. 4NH2O0F 2016-11-01 - 18010 - Simon Fernandez-checked a/c unit found breaker tripped reset ops checked okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-28 | 174662 | RFMT-133669 | !! our air conditioning got worked on and now there is a constant noise coming from our drain in the sink every time the air turns on. 4NM2889 | 2016-11-08 - 18010 - Simon Fernandez-re-worked condensate drain line, checked supply vents and return - Simon Fernandez | !! our air conditioning got worked on and now there is a constant noise coming from our drain in the sink every time the air turns on. 4NM2889 2016-11-08 - 18010 - Simon Fernandez-re-worked condensate drain line, checked supply vents and return - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-28 | 174676 | RFMT-133655 | !! Air Conditioning kicks on, but no air circulating; rooms are not cooling down. Please check this and fix it. Contact Name: Karen Cabrera Contact Phone Number: 9285030590 Contact Email: karen_cabrera27@outlook.com 4NK3NL9 | 2016-10-28 - 18010 - Thor Millsaps-Replaced contactor. System up and running. - Thor Millsaps | !! Air Conditioning kicks on, but no air circulating; rooms are not cooling down. Please check this and fix it. Contact Name: Karen Cabrera Contact Phone Number: 9285030590 Contact Email: karen_cabrera27@outlook.com 4NK3NL9 2016-10-28 - 18010 - Thor Millsaps-Replaced contactor. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174677 | RFMT-133654 | !! Air Conditioning kicks on, but no air circulating; rooms are not cooling down. Please check this and fix it. Contact Name: Karen Cabrera Contact Phone Number: 9285030590 Contact Email: karen_cabrera27@outlook.com 4NK3NL9 | 2016-10-28 - 18010 - Simon Fernandez-removed and replaced contactor unit checks okay - Simon Fernandez | !! Air Conditioning kicks on, but no air circulating; rooms are not cooling down. Please check this and fix it. Contact Name: Karen Cabrera Contact Phone Number: 9285030590 Contact Email: karen_cabrera27@outlook.com 4NK3NL9 2016-10-28 - 18010 - Simon Fernandez-removed and replaced contactor unit checks okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174682 | RFMT-133649 | Please replace Cluster B rm. 114 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | Please replace Cluster B rm. 114 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174684 | RFMT-133647 | Please replace Cluster B rm. 110 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor - Gregory Stetka | Please replace Cluster B rm. 110 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174686 | RFMT-133645 | Please replace Cluster A rm.214 HVAC condensing units capacitor and contactor. | NA | Please replace Cluster A rm.214 HVAC condensing units capacitor and contactor. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-28 | 174688 | RFMT-133643 | Please replace Cluster A rm.214 HVAC condensing units capacitor and contactor. | 2016-10-28 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor and contactor - Thor Millsaps | Please replace Cluster A rm.214 HVAC condensing units capacitor and contactor. 2016-10-28 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor and contactor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-28 | 174691 | RFMT-133640 | Please replace Cluster A rm. 116 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | Please replace Cluster A rm. 116 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174692 | RFMT-133639 | Please replace Cluster A rm.114 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor only. - Gregory Stetka | Please replace Cluster A rm.114 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor only. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174693 | RFMT-133638 | Please replace Cluster A rm.110 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | Please replace Cluster A rm.110 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174698 | RFMT-133633 | Please replace Cluster A Laundry rm. HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | Please replace Cluster A Laundry rm. HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174701 | RFMT-133630 | Please replace rm. A 119 HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | Please replace rm. A 119 HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174703 | RFMT-133628 | Please replace rm. A 119 HVAC condensing units capacitor. | 2016-10-28 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Please replace rm. A 119 HVAC condensing units capacitor. 2016-10-28 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174707 | RFMT-133624 | Please replace data rooms HVAC condensing units capacitor. | 2016-10-31 - 18010 - Completed by Thor - Gregory Stetka | Please replace data rooms HVAC condensing units capacitor. 2016-10-31 - 18010 - Completed by Thor - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 174708 | RFMT-133623 | Please replace data rooms HVAC condensing units capacitor | 2016-10-28 - 18010 - Thor Millsaps-Replaced 30/5 dual capacitor. - Thor Millsaps | Please replace data rooms HVAC condensing units capacitor 2016-10-28 - 18010 - Thor Millsaps-Replaced 30/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-28 | 214759 | RACC-113851 | !! Repeat Request. The AC for rooms C & D is not working. It does not go below a certain temperature and the air it blows out has become muggy. After being looked at previously by maintenance, it makes a loud grinding sound at night. They've tried cleaning it out before. The AC does blow, but not as. . . | NA | !! Repeat Request. The AC for rooms C & D is not working. It does not go below a certain temperature and the air it blows out has become muggy. After being looked at previously by maintenance, it makes a loud grinding sound at night. They've tried cleaning it out before. The AC does blow, but not as. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-29 | 214781 | RACC-113829 | !! Bathroom Vent is blowing out house dust all over the bathroom Occupants would like someone to clean it out. Thank you! 4NC8COA | NA | !! Bathroom Vent is blowing out house dust all over the bathroom Occupants would like someone to clean it out. Thank you! 4NC8COA NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-31 | 51434 | TMPE-198723 | American Five Star Car Care Center Moose Complete Front Left/right axle kit/ shaft assy-drive,rr propeller, differential fluid, pivot works front wheel bearing kit, cap (Kawasaki), seal-oil, o-ring kit, bearing-roller, Kawasaki mule front brake drum Total: 2864.62 | NA | American Five Star Car Care Center Moose Complete Front Left/right axle kit/ shaft assy-drive,rr propeller, differential fluid, pivot works front wheel bearing kit, cap (Kawasaki), seal-oil, o-ring kit, bearing-roller, Kawasaki mule front brake drum Total: 2864.62 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-31 | 52299 | TMPE-197858 | MWO LSE 106 This AC is very loud, please check out. !! Consistent hissing noise coming from ceiling in LSE 106. Not house speakers or sound system, appears to be a consistent gaseous leak (cold air?). Noise appears to be coming from unit labeled P-22 in ceiling. This is a university classroom Le. . . | 2016-11-02 - 18010 - Called in to say the noise is still loud. emailed status request to HVAC - Amanda Thomas; 2016-12-18 - 18010 - Robert Dauscher-Had given this call to EMS back in early November. Call still not completed as of 12-17-16. called in EMS oncall to assist. EMS tech found faulty pneumatic control valve. Assisted EMS tech with replacing valve. VAV LOCATED APPROXIMATLY 15FT IN THE AIR AC Complete - Robert Dauscher | MWO LSE 106 This AC is very loud, please check out. !! Consistent hissing noise coming from ceiling in LSE 106. Not house speakers or sound system, appears to be a consistent gaseous leak (cold air?). Noise appears to be coming from unit labeled P-22 in ceiling. This is a university classroom Le. . . 2016-11-02 - 18010 - Called in to say the noise is still loud. emailed status request to HVAC - Amanda Thomas; 2016-12-18 - 18010 - Robert Dauscher-Had given this call to EMS back in early November. Call still not completed as of 12-17-16. called in EMS oncall to assist. EMS tech found faulty pneumatic control valve. Assisted EMS tech with replacing valve. VAV LOCATED APPROXIMATLY 15FT IN THE AIR AC Complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-10-31 | 52301 | TMPE-197856 | MWO: UCENT C 302 BT TO HVAC - THE LEAK IS COMING FROM THE AIR HANDLER. ***ORIGINAL REQUEST***There's a ceiling tile that's bowing and there's a steady drip coming from the ceiling. | 2016-10-31 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-01 - 18010 - CALLED TO BRIAN Q. - Monica Moraga; 2016-11-02 - 18010 - Jennifer Moyer-de-iced unit and adjusted temp. everything is ok - Thomas Gibble; 2016-11-02 - 18010 - Thomas Gibble-de-iced unit and adjusted temp. everything is ok - Thomas Gibble | MWO: UCENT C 302 BT TO HVAC - THE LEAK IS COMING FROM THE AIR HANDLER. ***ORIGINAL REQUEST***There's a ceiling tile that's bowing and there's a steady drip coming from the ceiling. 2016-10-31 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-01 - 18010 - CALLED TO BRIAN Q. - Monica Moraga; 2016-11-02 - 18010 - Jennifer Moyer-de-iced unit and adjusted temp. everything is ok - Thomas Gibble; 2016-11-02 - 18010 - Thomas Gibble-de-iced unit and adjusted temp. everything is ok - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-10-31 | 52307 | TMPE-197850 | MWO: ASU PD 107U1 There's 2 wall units that are leaking. One is on the south wall and the other is on the west wall; it's the unit that is closest to the south wall. | 2016-10-31 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-02 - 18010 - Zhi Yu-we responded to the call. We have to reschedule do to no escort service available - Zhi Yu; 2016-11-04 - 18010 - Zhi Yu-Replaced 2 little giant condensate pump and repiped. - Zhi Yu | MWO: ASU PD 107U1 There's 2 wall units that are leaking. One is on the south wall and the other is on the west wall; it's the unit that is closest to the south wall. 2016-10-31 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-02 - 18010 - Zhi Yu-we responded to the call. We have to reschedule do to no escort service available - Zhi Yu; 2016-11-04 - 18010 - Zhi Yu-Replaced 2 little giant condensate pump and repiped. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-10-31 | 52335 | TMPE-197822 | SWO MU Catering Kitchen cooler 4828 has been at 70 degrees all weekend need repair ASAP!!!!!!! | 2016-11-02 - 18240 - Zhi Yu-Arrived Walk-in @ 60deg. We check pressure its completely empty. We check for leaks, located in the Evaporator coil. We sale them New replacement. BOHN ADT104AK. - Zhi Yu; 2016-11-02 - 18240 - Zhi Yu-We replaced Evaporator ADT104AK, TXV, solenoid Valve, liquid drier, Dual pressure control. We charge R22 6lbs. - Zhi Yu; 2016-11-02 - 18240 - Gail Jackson-We replaced Evaporator ADT104AK, TXV, solenoid Valve, liquid drier, Dual pressure control. We charge R22 6lbs. - Zhi Yu; 2016-11-02 - 18240 - Zhi Yu-We follow-up, the Temperature 39deg. Adjust LPC and T/sat. - Zhi Yu; 2016-11-02 - 18240 - Gail Jackson-We follow-up, the Temperature 39deg. Adjust LPC and T/sat. - Zhi Yu; 2016-11-07 - 18240 - 11/1/2016 2CE 1:30pm-3:30pm ZhiYu - MU Urgent call in catering kitchen. I coming early to work on walkin cooler. replace evap coil. - Kerri Perkins | SWO MU Catering Kitchen cooler 4828 has been at 70 degrees all weekend need repair ASAP!!!!!!! 2016-11-02 - 18240 - Zhi Yu-Arrived Walk-in @ 60deg. We check pressure its completely empty. We check for leaks, located in the Evaporator coil. We sale them New replacement. BOHN ADT104AK. - Zhi Yu; 2016-11-02 - 18240 - Zhi Yu-We replaced Evaporator ADT104AK, TXV, solenoid Valve, liquid drier, Dual pressure control. We charge R22 6lbs. - Zhi Yu; 2016-11-02 - 18240 - Gail Jackson-We replaced Evaporator ADT104AK, TXV, solenoid Valve, liquid drier, Dual pressure control. We charge R22 6lbs. - Zhi Yu; 2016-11-02 - 18240 - Zhi Yu-We follow-up, the Temperature 39deg. Adjust LPC and T/sat. - Zhi Yu; 2016-11-02 - 18240 - Gail Jackson-We follow-up, the Temperature 39deg. Adjust LPC and T/sat. - Zhi Yu; 2016-11-07 - 18240 - 11/1/2016 2CE 1:30pm-3:30pm ZhiYu - MU Urgent call in catering kitchen. I coming early to work on walkin cooler. replace evap coil. - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-10-31 | 174663 | RFMT-133668 | Please replace all HVAC return air filters in all Community Room study rooms. | 2016-10-31 - 18010 - Salvatore Marasco Jr-Replaced all A.C. filters in study rooms. - Salvatore Marasco Jr | Please replace all HVAC return air filters in all Community Room study rooms. 2016-10-31 - 18010 - Salvatore Marasco Jr-Replaced all A.C. filters in study rooms. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-31 | 174664 | RFMT-133667 | Please replace all HVAC return air filters in all Community Room study rooms. | 2016-10-31 - 18010 - Salvatore Marasco Jr-Replaced all A.C. filters in study rooms. - Salvatore Marasco Jr | Please replace all HVAC return air filters in all Community Room study rooms. 2016-10-31 - 18010 - Salvatore Marasco Jr-Replaced all A.C. filters in study rooms. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-10-31 | 233684 | POLY-114515 | REFRIGERANT CHARGE FOR CHILLER #2 4O216EO | NA | REFRIGERANT CHARGE FOR CHILLER #2 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 52006 | TMPE-198151 | MWO SSV 215C BT to HVAC-Lots of water within the whole duct system. Also got reports from rooms 110E and 110F Steady water coming in from the air ducts. | 2016-11-01 - 18010 - Called out to Brian Q.Gave him multiple rooms experiencing flooding. - Amanda Thomas; 2016-11-02 - 18010 - Brian Qualls-Found 1/4" valve from coil open and running into condensate drain. This was filling the pan and not allowing condensate to drain. Also floor drain screen was plugged. Both problems were causing room to flood. - Brian Qualls; 2016-11-02 - 18010 - Derek Gittings-Found 1/4" valve from coil open and running into condensate drain. This was filling the pan and not allowing condensate to drain. Also floor drain screen was plugged. Both problems were causing room to flood. - Brian Qualls | MWO SSV 215C BT to HVAC-Lots of water within the whole duct system. Also got reports from rooms 110E and 110F Steady water coming in from the air ducts. 2016-11-01 - 18010 - Called out to Brian Q.Gave him multiple rooms experiencing flooding. - Amanda Thomas; 2016-11-02 - 18010 - Brian Qualls-Found 1/4" valve from coil open and running into condensate drain. This was filling the pan and not allowing condensate to drain. Also floor drain screen was plugged. Both problems were causing room to flood. - Brian Qualls; 2016-11-02 - 18010 - Derek Gittings-Found 1/4" valve from coil open and running into condensate drain. This was filling the pan and not allowing condensate to drain. Also floor drain screen was plugged. Both problems were causing room to flood. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 3
2016-11-01 | 52008 | TMPE-198149 | MWO SSV 215C **Additional info** rooms 110 E and 110 F are also experiencing water intake. Steady water coming in from the air ducts. | 2016-11-01 - 18010 - Called out to Bryan - Amanda Thomas; 2016-11-01 - 18010 - Bryan LaForais-Complete Water was coming from ductwork due to clogged drains in the EQ rooms on 2nd and 3rd floor. HVAC cleared blockage. - Bryan LaForais | MWO SSV 215C **Additional info** rooms 110 E and 110 F are also experiencing water intake. Steady water coming in from the air ducts. 2016-11-01 - 18010 - Called out to Bryan - Amanda Thomas; 2016-11-01 - 18010 - Bryan LaForais-Complete Water was coming from ductwork due to clogged drains in the EQ rooms on 2nd and 3rd floor. HVAC cleared blockage. - Bryan LaForais | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2
2016-11-01 | 52041 | TMPE-198116 | MWO: BT transfer to AC: There are 2 units making the sound. 1 unit is in room behind whiteboards. Help Center - Diana LSE 106 hissing noise doesn't smell gas, but the sound is disturbing all the students in the classroom. | 2016-11-04 - 10010 - Michael Kelley-Found pipe chase next to room 106. Did not find problem in main equipment room in sub basement. I could not find the units the BT was talking about. - Michael Kelley [Modified: 2016-11-04 Michael Kelley] | MWO: BT transfer to AC: There are 2 units making the sound. 1 unit is in room behind whiteboards. Help Center - Diana LSE 106 hissing noise doesn't smell gas, but the sound is disturbing all the students in the classroom. 2016-11-04 - 10010 - Michael Kelley-Found pipe chase next to room 106. Did not find problem in main equipment room in sub basement. I could not find the units the BT was talking about. - Michael Kelley [Modified: 2016-11-04 Michael Kelley] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-01 | 52499 | TMPE-197658 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 52500 | TMPE-197657 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 52501 | TMPE-197656 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 174483 | RFMT-133848 | !! The Air conditioner is not working. The switch is in high (temperature set to the lowest), but the AC does not cool the room. Contact Name: Alex Contact Phone Number: 72030874222 Contact Email: 4NGGFCC | 2016-11-02 - 18010 - Thomas Zambrano-unit is at 69\\xb0.cant flush unit because there is no flush valves. the bottom chiller line valve is broken also.after opening and closing top valve i was able to reach a temp. of 63\\xb0. need ac techs to troubleshoot. - Thomas Zambrano | !! The Air conditioner is not working. The switch is in high (temperature set to the lowest), but the AC does not cool the room. Contact Name: Alex Contact Phone Number: 72030874222 Contact Email: 4NGGFCC 2016-11-02 - 18010 - Thomas Zambrano-unit is at 69\\xb0.cant flush unit because there is no flush valves. the bottom chiller line valve is broken also.after opening and closing top valve i was able to reach a temp. of 63\\xb0. need ac techs to troubleshoot. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 5
2016-11-01 | 174491 | RFMT-133840 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for room M 210 unit. | 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for room M 210 unit. 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174492 | RFMT-133839 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for room M 106 unit. | 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for room M 106 unit. 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174493 | RFMT-133838 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for M Cluster Elevator eq. room unit. | 2016-11-02 - 18010 - Thor Millsaps-Replaced 30/5 dual capacitor - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for M Cluster Elevator eq. room unit. 2016-11-02 - 18010 - Thor Millsaps-Replaced 30/5 dual capacitor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174494 | RFMT-133837 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for 2nd floor M Cluster Chapter rm. unit | 2016-11-02 - 18010 - Thor Millsaps-Replaced 45/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for 2nd floor M Cluster Chapter rm. unit 2016-11-02 - 18010 - Thor Millsaps-Replaced 45/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174495 | RFMT-133836 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for rm. L 208 unit | 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for rm. L 208 unit 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174496 | RFMT-133835 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for rm. L 105 unit | 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for rm. L 105 unit 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 174497 | RFMT-133834 | Res. Life HVAC Replace HVAC condensing fan motor capacitor for 2nd floor L Cluster Chapter rm. unit | 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | Res. Life HVAC Replace HVAC condensing fan motor capacitor for 2nd floor L Cluster Chapter rm. unit 2016-11-02 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 254751 | DTPC-113787 | There is an A/C unit leaking into room 133 | 2016-11-01 - 18010 - Ralph Lemons-Clogged condensate line and dirty filter. removed cond. and cleaned primary and secondary condensate lines. It was in the room 133 not 139. - Ralph Lemons | There is an A/C unit leaking into room 133 2016-11-01 - 18010 - Ralph Lemons-Clogged condensate line and dirty filter. removed cond. and cleaned primary and secondary condensate lines. It was in the room 133 not 139. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 3834 | WEST-107415 | HVAC-GENERAL-MU Air Filters-South | 2016-11-10 - 18010 - Chad T Ball-Replaced filters - Chad T Ball | HVAC-GENERAL-MU Air Filters-South 2016-11-10 - 18010 - Chad T Ball-Replaced filters - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-01 | 3835 | WEST-107414 | HVAC-GENERAL-MU Air Filters-North | 2016-11-10 - 18010 - Chad T Ball-Replaced filters - Chad T Ball | HVAC-GENERAL-MU Air Filters-North 2016-11-10 - 18010 - Chad T Ball-Replaced filters - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-01 | 3885 | WEST-107364 | HVAC-GENERAL-EVAP-006 | 2016-11-30 - 18010 - Ronald Chaffee-Turned off power, drained water from pan. Laid up cooler for winter. - Ronald Chaffee | HVAC-GENERAL-EVAP-006 2016-11-30 - 18010 - Ronald Chaffee-Turned off power, drained water from pan. Laid up cooler for winter. - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-01 | 3886 | WEST-107363 | HVAC-GENERAL-EVAP-005 | 2016-11-18 - 18010 - Randy Randell-adjust motor and belts grease fan bearings and clean dirt and rust. - Randy Randell | HVAC-GENERAL-EVAP-005 2016-11-18 - 18010 - Randy Randell-adjust motor and belts grease fan bearings and clean dirt and rust. - Randy Randell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-01 | 3895 | WEST-107354 | Air Compressor-SAC-001 | 2016-11-30 - 18030 - Thomas Wienand-Blow down tank and checked unit - Thomas Wienand | Air Compressor-SAC-001 2016-11-30 - 18030 - Thomas Wienand-Blow down tank and checked unit - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 3896 | WEST-107353 | Air Compressor-CAC-002 | 2016-11-30 - 18030 - Thomas Wienand-Blew down tank and checked unit - Thomas Wienand | Air Compressor-CAC-002 2016-11-30 - 18030 - Thomas Wienand-Blew down tank and checked unit - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-01 | 3897 | WEST-107352 | Air Compressor-CAC-001 | 2016-12-01 - 18030 - Ronald Chaffee-Checked electrical connections. Greased motor. Checked air filter and blew out dust. - Ronald Chaffee | Air Compressor-CAC-001 2016-12-01 - 18030 - Ronald Chaffee-Checked electrical connections. Greased motor. Checked air filter and blew out dust. - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-11-02 | 51849 | TMPE-198308 | Please vaccuum outside cubicles 302BB & 302BC. The AC had leaked. The issue had been fixed but there is white particles left over from the work. 42B2DOL | NA | Please vaccuum outside cubicles 302BB & 302BC. The AC had leaked. The issue had been fixed but there is white particles left over from the work. 42B2DOL NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 51899 | TMPE-198258 | MWO PSC 02 In the utility room, the air intake is pulling sewage air up and distributing it throughout the building. Please address this urgently. | 2016-11-02 - 18020 - Called out to Brian - Amanda Thomas; 2016-11-02 - 18020 - Brian Qualls-Found condensate drain p-trap on air handler dry causing sewer gas to be pulled into unit. filled trap with water to alleviate this. Also needs sewage ejector lid penetrations sealed and air handler sheet metal joints retaped/sealed. Rescheduled to Mike Kelley. - Brian Qualls; 2016-11-03 - 18020 - Michael Kelley-Cleaned sewage ejector lid. applied 7 tubes of silicone. Taped ac unit around seals. Contacted John and let him know it was finished. - Michael Kelley | MWO PSC 02 In the utility room, the air intake is pulling sewage air up and distributing it throughout the building. Please address this urgently. 2016-11-02 - 18020 - Called out to Brian - Amanda Thomas; 2016-11-02 - 18020 - Brian Qualls-Found condensate drain p-trap on air handler dry causing sewer gas to be pulled into unit. filled trap with water to alleviate this. Also needs sewage ejector lid penetrations sealed and air handler sheet metal joints retaped/sealed. Rescheduled to Mike Kelley. - Brian Qualls; 2016-11-03 - 18020 - Michael Kelley-Cleaned sewage ejector lid. applied 7 tubes of silicone. Taped ac unit around seals. Contacted John and let him know it was finished. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 174418 | RFMT-133913 | My room is really getting really absurdly cold these past 2 days, cold air is blowing constantly out of the vent. 4NO8AEH | 2016-11-03 - 18010 - Forwarded request to FACMAN - Yvette Castro | My room is really getting really absurdly cold these past 2 days, cold air is blowing constantly out of the vent. 4NO8AEH 2016-11-03 - 18010 - Forwarded request to FACMAN - Yvette Castro | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 174422 | RFMT-133909 | !! Air conditioning is not working properly. 4NJNAOK | 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Simon Fernandez-chiller #1 auto-shut down for VSD over heat,#2 chiller brought on line.Cycled okay - Simon Fernandez | !! Air conditioning is not working properly. 4NJNAOK 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Simon Fernandez-chiller #1 auto-shut down for VSD over heat,#2 chiller brought on line.Cycled okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 174423 | RFMT-133908 | !! The Air conditioner at Sonora is not working. The lobby, halls and offices are hot and the thermometer controls appear to be not working/responding (in other words, it's cooking in here.) 4NIAIHJ | 2016-11-02 - 18010 - See w.o. # 133905 for results - Gregory Stetka; 2016-11-03 - 18010 - Thor Millsaps-Checked air handler in attic above offices. No chilled water being supplied to air handlers. Found Chiller #1 (model VSD351KFT-46) shut off on safety shutdwon. VSD (York VSD Part no. 371-027-67-706) overheated. Tagged out chiller #1 and referred to Johnson Controls for repair. Started Chiller #2 as a temporary backup. - Thor Millsaps | !! The Air conditioner at Sonora is not working. The lobby, halls and offices are hot and the thermometer controls appear to be not working/responding (in other words, it's cooking in here.) 4NIAIHJ 2016-11-02 - 18010 - See w.o. # 133905 for results - Gregory Stetka; 2016-11-03 - 18010 - Thor Millsaps-Checked air handler in attic above offices. No chilled water being supplied to air handlers. Found Chiller #1 (model VSD351KFT-46) shut off on safety shutdwon. VSD (York VSD Part no. 371-027-67-706) overheated. Tagged out chiller #1 and referred to Johnson Controls for repair. Started Chiller #2 as a temporary backup. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-02 | 174424 | RFMT-133907 | !! Air conditioning is not working properly. 4NJNAOK | 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Thor Millsaps-Checked air handler in attic above offices. No chilled water being supplied to air handlers. Found Chiller #1 (model VSD351KFT-46) shut off on safety shutdwon. VSD (York VSD Part no. 371-027-67-706) overheated. Tagged out chiller #1 and referred to Johnson Controls for repair. Started Chiller #2 as a temporary backup. - Thor Millsaps | !! Air conditioning is not working properly. 4NJNAOK 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Thor Millsaps-Checked air handler in attic above offices. No chilled water being supplied to air handlers. Found Chiller #1 (model VSD351KFT-46) shut off on safety shutdwon. VSD (York VSD Part no. 371-027-67-706) overheated. Tagged out chiller #1 and referred to Johnson Controls for repair. Started Chiller #2 as a temporary backup. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-02 | 174426 | RFMT-133905 | !! The Air conditioner at Sonora is not working. The lobby, halls and offices are hot and the thermometer controls appear to be not working/responding (in other words, it's cooking in here.) 4NIAIHJ | 2016-11-02 - 18010 - Simon &amp; Thor tagged first stage chiller unit out of service VFD on overload and brought on line 2nd stag chiller unit for overnight.&#x0D; Sonora chiller system is back on line and cooling.&#x0D; Will schedule Johnson Controls tomorrow morning. - Gregory Stetka; 2016-11-03 - 18010 - Simon Fernandez-#1chiller in auto-shut down for VSD over heat Notified Greg will call Johnson control to repair problem. - Simon Fernandez | !! The Air conditioner at Sonora is not working. The lobby, halls and offices are hot and the thermometer controls appear to be not working/responding (in other words, it's cooking in here.) 4NIAIHJ 2016-11-02 - 18010 - Simon &amp; Thor tagged first stage chiller unit out of service VFD on overload and brought on line 2nd stag chiller unit for overnight.&#x0D; Sonora chiller system is back on line and cooling.&#x0D; Will schedule Johnson Controls tomorrow morning. - Gregory Stetka; 2016-11-03 - 18010 - Simon Fernandez-#1chiller in auto-shut down for VSD over heat Notified Greg will call Johnson control to repair problem. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-02 | 174428 | RFMT-133903 | !! AC is not working 4NJ820F | 2016-11-03 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | !! AC is not working 4NJ820F 2016-11-03 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 174431 | RFMT-133900 | !! Having problems with the air conditioning. Not a lot of cool air blowing through even on the lowest setting. Contact Name: Contact Phone Number: 4803889925 Contact Email: 4NE1G87 | 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Gabriel Figueroa-a/c is working fine. Temp out the vent is 52 degrees - Gabriel Figueroa | !! Having problems with the air conditioning. Not a lot of cool air blowing through even on the lowest setting. Contact Name: Contact Phone Number: 4803889925 Contact Email: 4NE1G87 2016-11-02 - 18010 - See w.o. # 133905 for results. - Gregory Stetka; 2016-11-03 - 18010 - Gabriel Figueroa-a/c is working fine. Temp out the vent is 52 degrees - Gabriel Figueroa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 174433 | RFMT-133898 | Please blow out the chiller lines on a/c coil at University Towers room 510. Simon | 2016-11-04 - 18010 - Thor Millsaps-Checked motor, motor is operating properly. Student complained of poor airflow. Removed motor and cleaned coil thoroughly. Removed loose insulation partially covering coil surface. System up and running. - Thor Millsaps | Please blow out the chiller lines on a/c coil at University Towers room 510. Simon 2016-11-04 - 18010 - Thor Millsaps-Checked motor, motor is operating properly. Student complained of poor airflow. Removed motor and cleaned coil thoroughly. Removed loose insulation partially covering coil surface. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-02 | 174448 | RFMT-133883 | Please repair HVAC condensate drain system for the evap. unit in Adelphi I C 110 / 112. | 2016-11-04 - 18010 - Thor Millsaps-Disconnected pvc from air handler, cleaned primary drain pan thoroughly, vacuumed drain line from sink p-trap, re-ran primary drain line with clear tubing. Water is draining through primary drain line. - Thor Millsaps | Please repair HVAC condensate drain system for the evap. unit in Adelphi I C 110 / 112. 2016-11-04 - 18010 - Thor Millsaps-Disconnected pvc from air handler, cleaned primary drain pan thoroughly, vacuumed drain line from sink p-trap, re-ran primary drain line with clear tubing. Water is draining through primary drain line. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-02 | 233635 | POLY-114564 | Dust blown into Tech Center lobby by use of leaf blower in front of building. Heavy exhaust smell as well in front office area. Recommend scheduling this for after work hours for those with allergies. Stopped at 8:15 am. 42AH71N | NA | Dust blown into Tech Center lobby by use of leaf blower in front of building. Heavy exhaust smell as well in front office area. Recommend scheduling this for after work hours for those with allergies. Stopped at 8:15 am. 42AH71N NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-02 | 36517 | TMPE-213640 | Need to replace one of two condenser fan motors that has bad bearings. There is a tag on the access panel under the fan that is failing. The condensing section is tagged 435A. The equipment number is: 017-AC-00435-CU1A 154764 | 2017-02-08 - 18010 - Robert Ecabert-Replaced the bad condenser fan motor. - Robert Ecabert | Need to replace one of two condenser fan motors that has bad bearings. There is a tag on the access panel under the fan that is failing. The condensing section is tagged 435A. The equipment number is: 017-AC-00435-CU1A 154764 2017-02-08 - 18010 - Robert Ecabert-Replaced the bad condenser fan motor. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-03 | 51648 | TMPE-198509 | MWO LSA L1 Transfer PL to HVAC PUMPS were out. *Original message !! There is a loud alarm sounding in the LSA basement level mechanical room. Please inspect immediately. Thank you. Pump #2 needs to be removed for replacement. Mike K and Derek assigned for this. 42BLHKH | 2016-11-03 - 10010 - Brian Qualls-Found stop, lead, and lag floats defective. Replaced all 4 floats. Also #2 pump motor grounded. Assigned Derek and Mike Kelley to remove pump and get all necessary info to order replacement. #1 pump is working using lead-lag, OK. - Brian Qualls; 2016-11-03 - 10010 - Derek Gittings-Found stop, lead, and lag floats defective. Replaced all 4 floats. Also #2 pump motor grounded. Assigned Derek and Mike Kelley to remove pump and get all necessary info to order replacement. #1 pump is working using lead-lag, OK. - Brian Qualls; 2016-11-04 - 10010 - Derek Gittings-Pulled Pump. Had problems. 1. The Pump had tripped out. The room was flooder. 2. The wire to pull the pump out broke at the eye bolt. 3. The check valve leaked. 4. Water was every were. Had to clean up and spray with bleach solution. 5. Finally the Electrician showed up motor was good. Float was not working properly. 6. Set up Decontamination zone at 8am 7. - Michael Kelley; 2016-11-04 - 10010 - Michael Kelley-Pulled Pump. Had problems. 1. The Pump had tripped out. The room was flooder. 2. The wire to pull the pump out broke at the eye bolt. 3. The check valve leaked. 4. Water was every were. Had to clean up and spray with bleach solution. 5. Finally the Electrician showed up motor was good. Float was not working properly. 6. Set up Decontamination zone at 8am 7. - Michael Kelley; 2016-11-07 - 10010 - 11/3/2016 1CE 4pm-5pm Brian Qualls - LSA LSA - Worked thru lunch and breaks to get sewage ejector operating. - Kerri Perkins | MWO LSA L1 Transfer PL to HVAC PUMPS were out. *Original message !! There is a loud alarm sounding in the LSA basement level mechanical room. Please inspect immediately. Thank you. Pump #2 needs to be removed for replacement. Mike K and Derek assigned for this. 42BLHKH 2016-11-03 - 10010 - Brian Qualls-Found stop, lead, and lag floats defective. Replaced all 4 floats. Also #2 pump motor grounded. Assigned Derek and Mike Kelley to remove pump and get all necessary info to order replacement. #1 pump is working using lead-lag, OK. - Brian Qualls; 2016-11-03 - 10010 - Derek Gittings-Found stop, lead, and lag floats defective. Replaced all 4 floats. Also #2 pump motor grounded. Assigned Derek and Mike Kelley to remove pump and get all necessary info to order replacement. #1 pump is working using lead-lag, OK. - Brian Qualls; 2016-11-04 - 10010 - Derek Gittings-Pulled Pump. Had problems. 1. The Pump had tripped out. The room was flooder. 2. The wire to pull the pump out broke at the eye bolt. 3. The check valve leaked. 4. Water was every were. Had to clean up and spray with bleach solution. 5. Finally the Electrician showed up motor was good. Float was not working properly. 6. Set up Decontamination zone at 8am 7. - Michael Kelley; 2016-11-04 - 10010 - Michael Kelley-Pulled Pump. Had problems. 1. The Pump had tripped out. The room was flooder. 2. The wire to pull the pump out broke at the eye bolt. 3. The check valve leaked. 4. Water was every were. Had to clean up and spray with bleach solution. 5. Finally the Electrician showed up motor was good. Float was not working properly. 6. Set up Decontamination zone at 8am 7. - Michael Kelley; 2016-11-07 - 10010 - 11/3/2016 1CE 4pm-5pm Brian Qualls - LSA LSA - Worked thru lunch and breaks to get sewage ejector operating. - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 7
2016-11-03 | 51657 | TMPE-198500 | Requesting Electric Shop - Cooling tower #7 Fan B, CW FN07B motor control failed and will not continue to run. Contact Name: Mike Torres Contact Phone Number: 480-965-0218 Contact Email: mike.torres@asu.edu 42BH46K | 2016-11-09 - 15000 - Semeon Haile-troubleshoot and repaired safety switch on fan motor disconnect - Semeon Haile | Requesting Electric Shop - Cooling tower #7 Fan B, CW FN07B motor control failed and will not continue to run. Contact Name: Mike Torres Contact Phone Number: 480-965-0218 Contact Email: mike.torres@asu.edu 42BH46K 2016-11-09 - 15000 - Semeon Haile-troubleshoot and repaired safety switch on fan motor disconnect - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-03 | 51666 | TMPE-198491 | Central Plant - #9 condenser pump inboard bearing seal leaking. | 2017-05-16 - 30010 - not needed - Lisa Anderson | Central Plant - #9 condenser pump inboard bearing seal leaking. 2017-05-16 - 30010 - not needed - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-03 | 51717 | TMPE-198440 | SWO: Rooms 312 and 313 are having issues with dirt and debris coming out of the duct vents and onto their desks. Filters may need changed in air handler# 19. Please investigate. Thanks Submitted by 4O33E90 | 2016-11-08 - 18170 - FacMan, Please cancel work order# 198440. Our filter crew is currently changing filters through out the whole building and this area will be addressed. Thank you, Brian mm - Monica Moraga | SWO: Rooms 312 and 313 are having issues with dirt and debris coming out of the duct vents and onto their desks. Filters may need changed in air handler# 19. Please investigate. Thanks Submitted by 4O33E90 2016-11-08 - 18170 - FacMan, Please cancel work order# 198440. Our filter crew is currently changing filters through out the whole building and this area will be addressed. Thank you, Brian mm - Monica Moraga | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-11-03 | 174365 | RFMT-133966 | Please meet with Johnson Controls Mech. Andrew: regarding Chiller # 1 off line due to VFD overheating. | 2016-11-04 - 18010 - Thor Millsaps-Met with Andrew from JCI at Central Plant South. Andrew diagnosed problem with overheating VSD is due to low coolant level in VSD cooling system. Topped off coolant and tested system. VSD maintained temp at 84 degrees and is operating properly. Andrew lubed motor bearing as per warning and cleared warning. Found coolant leak in top cap of coolant reservoir. Sealed threads on cap with teflon tape. Andrew calibrated vane sensor. Chiller #1 is back on and operating normally. - Thor Millsaps | Please meet with Johnson Controls Mech. Andrew: regarding Chiller # 1 off line due to VFD overheating. 2016-11-04 - 18010 - Thor Millsaps-Met with Andrew from JCI at Central Plant South. Andrew diagnosed problem with overheating VSD is due to low coolant level in VSD cooling system. Topped off coolant and tested system. VSD maintained temp at 84 degrees and is operating properly. Andrew lubed motor bearing as per warning and cleared warning. Found coolant leak in top cap of coolant reservoir. Sealed threads on cap with teflon tape. Andrew calibrated vane sensor. Chiller #1 is back on and operating normally. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-03 | 214601 | RACC-114009 | !! Our freezer has stopped working. We have tried setting it at both high and low levels, but neither will keep the food cold and the freezer is currently not emitting any cold air. 4ND0IDN | 2016-11-10 - 10010 - replaced frig - Jim Deal | !! Our freezer has stopped working. We have tried setting it at both high and low levels, but neither will keep the food cold and the freezer is currently not emitting any cold air. 4ND0IDN 2016-11-10 - 10010 - replaced frig - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-03 | 214605 | RACC-114005 | !! The AC filter that was just installed in my room is making the air smell bad. My roommate says that it smells like charcoal, but I find the smell more reminiscent of spoiled mushrooms. Please replace the filter with one that does not stink. 4ND6D19 | NA | !! The AC filter that was just installed in my room is making the air smell bad. My roommate says that it smells like charcoal, but I find the smell more reminiscent of spoiled mushrooms. Please replace the filter with one that does not stink. 4ND6D19 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-03 | 233568 | POLY-114631 | Filter in A/C needs to be changed. 4NFHC4M | NA | Filter in A/C needs to be changed. 4NFHC4M NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-03 | 233570 | POLY-114629 | New air filter for the AC/Heating unit. Thanks, Erika Lankton 480-440-0086 42B769J | NA | New air filter for the AC/Heating unit. Thanks, Erika Lankton 480-440-0086 42B769J NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-03 | 233577 | POLY-114622 | Repair work to return structure to preloss condition, air duct cleaning. | NA | Repair work to return structure to preloss condition, air duct cleaning. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2016-11-03 | 3780 | WEST-107469 | Replace condenser fan motor on Carrier AC unit. | 2016-11-03 - 18010 - Chad T Ball-Replaced condenser fan motor. - Chad T Ball | Replace condenser fan motor on Carrier AC unit. 2016-11-03 - 18010 - Chad T Ball-Replaced condenser fan motor. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-04 | 51497 | TMPE-198660 | MWO: The south ceiling exhaust fan in MHall, 234 is not working. I have checked the breakers but none seem to be tripped. The switch is located on the back wall of enlarging station #4. Thanks 42ALG1L | 2016-11-14 - 18160 - Thomas Gibble-re-set breaker - Thomas Gibble; 2016-11-14 - 18160 - Gail Jackson-re-set breaker - Thomas Gibble | MWO: The south ceiling exhaust fan in MHall, 234 is not working. I have checked the breakers but none seem to be tripped. The switch is located on the back wall of enlarging station #4. Thanks 42ALG1L 2016-11-14 - 18160 - Thomas Gibble-re-set breaker - Thomas Gibble; 2016-11-14 - 18160 - Gail Jackson-re-set breaker - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-04 | 51538 | TMPE-198619 | MWO: !! There is dirty oil sputtering from the air valves in the PSE wing lab rooms. This means: 1. That the seals are leaking on the compressor and they need to be replaced ASAP 2. Someone needs to change the oil on the compressor ASAP. Thank you. Attachment(s) 42AE9GB | 2017-01-25 - 18030 - Jose Lopez-check two compressors found no problems.call requestor(Alexis Broune)explain what i found she will call if there's any more problems - Jose Lopez | MWO: !! There is dirty oil sputtering from the air valves in the PSE wing lab rooms. This means: 1. That the seals are leaking on the compressor and they need to be replaced ASAP 2. Someone needs to change the oil on the compressor ASAP. Thank you. Attachment(s) 42AE9GB 2017-01-25 - 18030 - Jose Lopez-check two compressors found no problems.call requestor(Alexis Broune)explain what i found she will call if there's any more problems - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2016-11-04 | 51542 | TMPE-198615 | Fan is locked up | 2016-11-15 - 18160 - Gail Jackson-Found fan worn out in need of replacement. - Gail Jackson; 2016-11-15 - 18160 - Thomas Gibble-Found fan worn out in need of replacement. - Gail Jackson; 2016-11-17 - 18160 - Gail Jackson-Disassembled unit, found fan motor locked up and housing loose from vibration, all rivets loose or falling out. Billy Jackson said all exhaust units to be included in building remodel. - Gail Jackson; 2016-11-17 - 18160 - Thomas Gibble-Disassembled unit, found fan motor locked up and housing loose from vibration, all rivets loose or falling out. Billy Jackson said all exhaust units to be included in building remodel. - Gail Jackson | Fan is locked up 2016-11-15 - 18160 - Gail Jackson-Found fan worn out in need of replacement. - Gail Jackson; 2016-11-15 - 18160 - Thomas Gibble-Found fan worn out in need of replacement. - Gail Jackson; 2016-11-17 - 18160 - Gail Jackson-Disassembled unit, found fan motor locked up and housing loose from vibration, all rivets loose or falling out. Billy Jackson said all exhaust units to be included in building remodel. - Gail Jackson; 2016-11-17 - 18160 - Thomas Gibble-Disassembled unit, found fan motor locked up and housing loose from vibration, all rivets loose or falling out. Billy Jackson said all exhaust units to be included in building remodel. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-11-04 | 51547 | TMPE-198610 | The fan has a bad vibration | 2016-11-17 - 18160 - Gail Jackson-Found fan motor burned out, Billy Jackson says unit to be included in bid for building remodel for replace. - Gail Jackson | The fan has a bad vibration 2016-11-17 - 18160 - Gail Jackson-Found fan motor burned out, Billy Jackson says unit to be included in bid for building remodel for replace. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-04 | 51560 | TMPE-198597 | MWO: SDFC for AC shop Jose Lopez need contactors for condensate units in EQ room basement (request from Mike PL shop) | NA | MWO: SDFC for AC shop Jose Lopez need contactors for condensate units in EQ room basement (request from Mike PL shop) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-04 | 51569 | TMPE-198588 | MWO Bio A: TRANSFER EMS TO HVAC - FAN COIL CONTACTOR IS CHATTERING. ***ORIGINAL REQUEST***change to EMS: This is in the control side of fan coil. We have a Fan coil unit that makes a loud vibrating noise when it is in auto at the RIB. Contact Name: Contact Phone Number: 602350. . . | 2016-11-17 - 18090 - Zhi Yu-diagnose the contact coil getting weak. we will get contactor order and schedule for replace. - Zhi Yu; 2016-12-06 - 18090 - Zhi Yu-We replaced 480volt 3pole 24v contactor. - Zhi Yu; 2016-12-06 - 18090 - Robert Dauscher-We replaced 480volt 3pole 24v contactor. - Zhi Yu | MWO Bio A: TRANSFER EMS TO HVAC - FAN COIL CONTACTOR IS CHATTERING. ***ORIGINAL REQUEST***change to EMS: This is in the control side of fan coil. We have a Fan coil unit that makes a loud vibrating noise when it is in auto at the RIB. Contact Name: Contact Phone Number: 602350. . . 2016-11-17 - 18090 - Zhi Yu-diagnose the contact coil getting weak. we will get contactor order and schedule for replace. - Zhi Yu; 2016-12-06 - 18090 - Zhi Yu-We replaced 480volt 3pole 24v contactor. - Zhi Yu; 2016-12-06 - 18090 - Robert Dauscher-We replaced 480volt 3pole 24v contactor. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-04 | 51591 | TMPE-198566 | University Center 302: Repeat request of wo 197856. The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and a bucket. | 2016-11-04 - 18010 - Dispatched to Steve Palombo. (FF) - Francesca Fernandez; 2016-11-08 - 18010 - Thomas Gibble-adjusted refrigerant level and got ems to drop temp - Thomas Gibble; 2016-11-08 - 18010 - Gail Jackson-adjusted refrigerant level and got ems to drop temp - Thomas Gibble | University Center 302: Repeat request of wo 197856. The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and a bucket. 2016-11-04 - 18010 - Dispatched to Steve Palombo. (FF) - Francesca Fernandez; 2016-11-08 - 18010 - Thomas Gibble-adjusted refrigerant level and got ems to drop temp - Thomas Gibble; 2016-11-08 - 18010 - Gail Jackson-adjusted refrigerant level and got ems to drop temp - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-04 | 174304 | RFMT-134027 | Repeat Request. My air vent smells really bad and it makes the air smell when I turn it on. 4NK5KL1 | 2016-11-10 - 18020 - Mike Guckian-cleared vent. - Mike Guckian | Repeat Request. My air vent smells really bad and it makes the air smell when I turn it on. 4NK5KL1 2016-11-10 - 18020 - Mike Guckian-cleared vent. - Mike Guckian | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-04 | 174310 | RFMT-134021 | Please replace HVAC condenser units contactor for Adelphi I K 114 | 2016-11-04 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Please replace HVAC condenser units contactor for Adelphi I K 114 2016-11-04 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-04 | 174311 | RFMT-134020 | Please replace HVAC condenser units contactor for Adelphi I K 110 | 2016-11-04 - 18010 - Simon Fernandez-replaced 35/5 cap. and 1 pole contactor - Simon Fernandez | Please replace HVAC condenser units contactor for Adelphi I K 110 2016-11-04 - 18010 - Simon Fernandez-replaced 35/5 cap. and 1 pole contactor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-04 | 174313 | RFMT-134018 | Please replace HVAC condenser units contactor for Adelphi I J luandry room | 2016-11-04 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Please replace HVAC condenser units contactor for Adelphi I J luandry room 2016-11-04 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-04 | 174317 | RFMT-134014 | Please replace HVAC condenser units contactor for Adelphi I H 106. | 2016-11-04 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor and contactor. - Thor Millsaps | Please replace HVAC condenser units contactor for Adelphi I H 106. 2016-11-04 - 18010 - Thor Millsaps-Replaced 35/5 dual capacitor and contactor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-04 | 214514 | RACC-114096 | !! The air conditioning is broken. Feels like an oven in here, its cooler outside than it is in here if that counts for something. My sliding glass door to my closet is also broken but the air conditioning unit is more of a pressing issue so if you are short on time, you could just focus on the airc. . . | NA | !! The air conditioning is broken. Feels like an oven in here, its cooler outside than it is in here if that counts for something. My sliding glass door to my closet is also broken but the air conditioning unit is more of a pressing issue so if you are short on time, you could just focus on the airc. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-04 | 214546 | RACC-114064 | Overdue maintenance of central A/C air filter. Dust has built up within vents. Request to clean or replace air filter. Attachment(s) 4NK3372 | NA | Overdue maintenance of central A/C air filter. Dust has built up within vents. Request to clean or replace air filter. Attachment(s) 4NK3372 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-05 | 214438 | RACC-114172 | AC broke again 4NOFGC3 | NA | AC broke again 4NOFGC3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-11-06 | 214491 | RACC-114119 | !! Air conditioner not working. Not hot water in room. Contact Name: Tanner Targowski Contact Phone Number: Contact Email: Ttargows@asu.edu 4NK5G0N | 2016-11-08 - 10010 - cleared condensate reset water sensor, hot water angle stop was shut off turned on and checked. Daniel - Jim Deal | !! Air conditioner not working. Not hot water in room. Contact Name: Tanner Targowski Contact Phone Number: Contact Email: Ttargows@asu.edu 4NK5G0N 2016-11-08 - 10010 - cleared condensate reset water sensor, hot water angle stop was shut off turned on and checked. Daniel - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-07 | 50591 | TMPE-199566 | MWO UNCTRB 108 BT TO HVAC - LEAK IS COMING FROM THE AIR HANDLER DRAIN ***ORIGINAL REQUEST***!! There is a leak in the ceiling of the conference room. One tile has fallen due to water. The room is 108 which is the conference room in suite 110. 4MNEFIG | 2016-11-09 - 18010 - Zhi Yu-Arrived @ room 108. We check the condensate drain plug-up. We vacuum and blow out the line. We clean out dust off coil and rescue return plenum. We also replaced 2 ceiling tiles. - Zhi Yu | MWO UNCTRB 108 BT TO HVAC - LEAK IS COMING FROM THE AIR HANDLER DRAIN ***ORIGINAL REQUEST***!! There is a leak in the ceiling of the conference room. One tile has fallen due to water. The room is 108 which is the conference room in suite 110. 4MNEFIG 2016-11-09 - 18010 - Zhi Yu-Arrived @ room 108. We check the condensate drain plug-up. We vacuum and blow out the line. We clean out dust off coil and rescue return plenum. We also replaced 2 ceiling tiles. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-07 | 50639 | TMPE-199518 | add AC belt guard is off and needs to be reinstalled, it is in the room on floor below belt Equipment Room Inspection-Monthly | 2016-11-29 - 18010 - Jennifer Moyer-Belt guard re-installed. - Jennifer Moyer | add AC belt guard is off and needs to be reinstalled, it is in the room on floor below belt Equipment Room Inspection-Monthly 2016-11-29 - 18010 - Jennifer Moyer-Belt guard re-installed. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-07 | 50701 | TMPE-199456 | MWO LSE E106 Help Desk - Diana R Life sciences E 106 Really loud air blowing sound lights flickering as well. Been going on for a week, and the noise is loud enough that the professor is having a hard time teaching. | 2016-11-16 - 18010 - Jennifer Moyer-Arrived at location to assess job. A class was in session, so I went to the shop and reviewed the class schedule to arrange repair. Also, there are very high ceilings in this room, so I will likely need a lift or assistance. I will look at the job when class is not in session. - Jennifer Moyer; 2016-12-22 - 18010 - Jennifer Moyer-thermostats are pneumatic and units are vav boxes. According to HVAC First Call List, this is for EMS. - Jennifer Moyer; 2016-12-22 - 18010 - Zhi Yu-thermostats are pneumatic and units are vav boxes. According to HVAC First Call List, this is for EMS. Transfer to EMS. - Jennifer Moyer; 2016-12-22 - 18010 - EMS work order # TMPE-2095789 - Jennifer Moyer | MWO LSE E106 Help Desk - Diana R Life sciences E 106 Really loud air blowing sound lights flickering as well. Been going on for a week, and the noise is loud enough that the professor is having a hard time teaching. 2016-11-16 - 18010 - Jennifer Moyer-Arrived at location to assess job. A class was in session, so I went to the shop and reviewed the class schedule to arrange repair. Also, there are very high ceilings in this room, so I will likely need a lift or assistance. I will look at the job when class is not in session. - Jennifer Moyer; 2016-12-22 - 18010 - Jennifer Moyer-thermostats are pneumatic and units are vav boxes. According to HVAC First Call List, this is for EMS. - Jennifer Moyer; 2016-12-22 - 18010 - Zhi Yu-thermostats are pneumatic and units are vav boxes. According to HVAC First Call List, this is for EMS. Transfer to EMS. - Jennifer Moyer; 2016-12-22 - 18010 - EMS work order # TMPE-2095789 - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-07 | 174199 | RFMT-134132 | Could you please fix my Air Conditioning unit? The fan still works, but the air isn't any cooler. The AC broke last Tuesday morning. I had the dorm room door open, and it was slightly hotter outside, so the AC was running. Very soon I noticed that the air coming out was not any cooler. Thanks for. . . | 2016-11-07 - 18290 - Simon Fernandez-checked a/c unit found bad 30/5 run capacitor. removed and replaced capacitor - Simon Fernandez | Could you please fix my Air Conditioning unit? The fan still works, but the air isn't any cooler. The AC broke last Tuesday morning. I had the dorm room door open, and it was slightly hotter outside, so the AC was running. Very soon I noticed that the air coming out was not any cooler. Thanks for. . . 2016-11-07 - 18290 - Simon Fernandez-checked a/c unit found bad 30/5 run capacitor. removed and replaced capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-11-07 | 174201 | RFMT-134130 | !! HVAC Air conditioning in need of maintenence. The condensate is fucked up and it's leaking water out of the main grate. Possible drywall water damage. Contact Name: Anthony Carrillo Contact Phone Number: 8582122293 Contact Email: Carrillo.t.anthony@gmail.com 4O2ADGF | 2016-11-08 - 18010 - Thomas Zambrano-fix ac. - Thomas Zambrano | !! HVAC Air conditioning in need of maintenence. The condensate is fucked up and it's leaking water out of the main grate. Possible drywall water damage. Contact Name: Anthony Carrillo Contact Phone Number: 8582122293 Contact Email: Carrillo.t.anthony@gmail.com 4O2ADGF 2016-11-08 - 18010 - Thomas Zambrano-fix ac. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-07 | 174227 | RFMT-134104 | Could you please fix my Air Conditioning unit? The fan still works, but the air isn't any cooler. The AC broke last Tuesday morning. I had the dorm room door open, and it was slightly hotter outside, so the AC was running. Very soon I noticed that the air coming out was not any cooler. Thanks for. . . | 2016-11-07 - 18290 - David Cates-Simon replaced unit's capacitor. Please create a TMA for him to account for his time and parts used. - David Cates; 2016-11-07 - 18290 - Simon copied - Gregory Stetka | Could you please fix my Air Conditioning unit? The fan still works, but the air isn't any cooler. The AC broke last Tuesday morning. I had the dorm room door open, and it was slightly hotter outside, so the AC was running. Very soon I noticed that the air coming out was not any cooler. Thanks for. . . 2016-11-07 - 18290 - David Cates-Simon replaced unit's capacitor. Please create a TMA for him to account for his time and parts used. - David Cates; 2016-11-07 - 18290 - Simon copied - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-11-07 | 233493 | POLY-114706 | !! Air conditioner does not work, it is not blowing cold air. Contact Name: raaqim wright Contact Phone Number: 5714199802 Contact Email: raaqimw27@gmail.com 4NG86IJ | NA | !! Air conditioner does not work, it is not blowing cold air. Contact Name: raaqim wright Contact Phone Number: 5714199802 Contact Email: raaqimw27@gmail.com 4NG86IJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-07 | 233509 | POLY-114690 | REPLACE WONEM'S BATHROOM EXHAUST FAN MOTOR 4O216EO | NA | REPLACE WONEM'S BATHROOM EXHAUST FAN MOTOR 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-07 | 254574 | DTPC-113964 | !! The two evaporative air coolers over the kiln room #167 need to be serviced so that they do not leak water over the gas kilns. The pads on both units also need to be replaced. Thank You, George Harris School of Art 42AMFKL | 2016-11-15 - 18150 - Ralph Lemons-Removed panels and need to be completely redone. no water or power to them. also need new pads. - Ralph Lemons; 2016-11-23 - 18150 - Ralph Lemons-Dave Downing showed and winterized the two coolers over the Kiln's. - Ralph Lemons | !! The two evaporative air coolers over the kiln room #167 need to be serviced so that they do not leak water over the gas kilns. The pads on both units also need to be replaced. Thank You, George Harris School of Art 42AMFKL 2016-11-15 - 18150 - Ralph Lemons-Removed panels and need to be completely redone. no water or power to them. also need new pads. - Ralph Lemons; 2016-11-23 - 18150 - Ralph Lemons-Dave Downing showed and winterized the two coolers over the Kiln's. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 50505 | TMPE-199652 | SWO MU 87 Replace controller and load program to controller, rewire/install and commission. May need to run a little wire from J-box on AH 12 to cabinet where controller is located plus labor. Jeffrey Green is aware of the work to be done on AH 12. Submitted by 4O33E90 | 2016-12-30 - 18050 - Jeffrey Green-Replaced defective AHU controller with DX checked sensors and program needs modifications but controlling better than before ready for start stop and vfd speed control when starter or vfd are replaced or repaired will monitor and improve programming as needed - Jeffrey Green | SWO MU 87 Replace controller and load program to controller, rewire/install and commission. May need to run a little wire from J-box on AH 12 to cabinet where controller is located plus labor. Jeffrey Green is aware of the work to be done on AH 12. Submitted by 4O33E90 2016-12-30 - 18050 - Jeffrey Green-Replaced defective AHU controller with DX checked sensors and program needs modifications but controlling better than before ready for start stop and vfd speed control when starter or vfd are replaced or repaired will monitor and improve programming as needed - Jeffrey Green | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-08 | 50521 | TMPE-199636 | SWO LSE 438 !! It is reported, "LSE 438 Details: Unfortunately it seems as if our 4C incubator is not working again \\u2013 it tends to stop holding low temps every couple of weeks following a repair." Please schedule service as quickly as possible. Charges up to $250.00 for this request may be bille. . . | 2016-11-09 - 18140 - Robert Ecabert-Found unit with bad starting components and I will replace the bad starting components tomorrow. - Robert Ecabert; 2016-11-09 - 18140 - Robert Ecabert-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert; 2016-11-09 - 18140 - Oner Munoz-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert; 2016-11-09 - 18140 - Oner Munoz-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert | SWO LSE 438 !! It is reported, "LSE 438 Details: Unfortunately it seems as if our 4C incubator is not working again \\u2013 it tends to stop holding low temps every couple of weeks following a repair." Please schedule service as quickly as possible. Charges up to $250.00 for this request may be bille. . . 2016-11-09 - 18140 - Robert Ecabert-Found unit with bad starting components and I will replace the bad starting components tomorrow. - Robert Ecabert; 2016-11-09 - 18140 - Robert Ecabert-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert; 2016-11-09 - 18140 - Oner Munoz-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert; 2016-11-09 - 18140 - Oner Munoz-Installed a new 3in1 starting component and the compressor came on and the unit pulled down to the 3.9 celcius setpoint and the unit is working fine. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 50848 | TMPE-199309 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 50849 | TMPE-199308 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 50869 | TMPE-199288 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51042 | TMPE-199115 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51202 | TMPE-198955 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51203 | TMPE-198954 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51204 | TMPE-198953 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51205 | TMPE-198952 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51206 | TMPE-198951 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51207 | TMPE-198950 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51208 | TMPE-198949 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51209 | TMPE-198948 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51210 | TMPE-198947 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 51211 | TMPE-198946 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-08 | 174114 | RFMT-134217 | RES LIFE / scott: Please perform D2D floors 1-7 | 2016-11-10 - 10010 - Scott Berndt-door to door ...replaced a/c filters - Scott Berndt | RES LIFE / scott: Please perform D2D floors 1-7 2016-11-10 - 10010 - Scott Berndt-door to door ...replaced a/c filters - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-08 | 208617 | RAMA-100647 | !! Our air conditioner has stopped working again and will not go any lower than 77. 4NJJLD7 | NA | !! Our air conditioner has stopped working again and will not go any lower than 77. 4NJJLD7 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-08 | 233457 | POLY-114742 | !! AC unit broken!!!! Temp set in required range but house temp still rising. Pipes appear to be frozen over. 4NK4LFJ | NA | !! AC unit broken!!!! Temp set in required range but house temp still rising. Pipes appear to be frozen over. 4NK4LFJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-08 | 254562 | DTPC-113976 | Replace Air Filters - 6C | 2016-11-08 - 18170 - Ross Hossack-Abel and I took new filters up to penthouse then removed old dirty filters and replaced them with new ones.Discarded old filters in dumpster. - Ross Hossack; 2016-11-08 - 18170 - Abel Esacreno-Valencia-Abel and I took new filters up to penthouse then removed old dirty filters and replaced them with new ones.Discarded old filters in dumpster. - Ross Hossack | Replace Air Filters - 6C 2016-11-08 - 18170 - Ross Hossack-Abel and I took new filters up to penthouse then removed old dirty filters and replaced them with new ones.Discarded old filters in dumpster. - Ross Hossack; 2016-11-08 - 18170 - Abel Esacreno-Valencia-Abel and I took new filters up to penthouse then removed old dirty filters and replaced them with new ones.Discarded old filters in dumpster. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 50248 | TMPE-199909 | MWO: CSB RM 48 The a/c in the room isn't working. The fan is moving but the air is warm. Please send someone to check on this asap. | 2016-11-26 - 18290 - Roque Garcia-Replaced the disconnect and rewired the cap. Checked and tested ok and left a note with faculty member who called in the request for service. - Roque Garcia | MWO: CSB RM 48 The a/c in the room isn't working. The fan is moving but the air is warm. Please send someone to check on this asap. 2016-11-26 - 18290 - Roque Garcia-Replaced the disconnect and rewired the cap. Checked and tested ok and left a note with faculty member who called in the request for service. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 50319 | TMPE-199838 | cooling tower pump not working - repair or replace | NA | cooling tower pump not working - repair or replace NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 50332 | TMPE-199825 | The sheave on the motor is worn. its a 5 groove sheave. Replace both Drive & Driven Sheaves so they are matched and new at the same time. (JH) | NA | The sheave on the motor is worn. its a 5 groove sheave. Replace both Drive & Driven Sheaves so they are matched and new at the same time. (JH) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 50360 | TMPE-199797 | MWO: EL Shop connected the existing condensate return pump in lower level service pit. AC Shop needs to check the floats. | 2016-11-10 - 23100 - Jose Lopez-lock &amp; tag 2 units,impeller in both units were'd stock to housing,remove pumps from housing free impeller,reinstall units but found floats not working fix and adjust floats.Unit working @ this time. - Jose Lopez | MWO: EL Shop connected the existing condensate return pump in lower level service pit. AC Shop needs to check the floats. 2016-11-10 - 23100 - Jose Lopez-lock &amp; tag 2 units,impeller in both units were'd stock to housing,remove pumps from housing free impeller,reinstall units but found floats not working fix and adjust floats.Unit working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-11-09 | 50397 | TMPE-199760 | MWO: We've received a faculty complaint about the AC unit in Discovery 113. They say that when the AC is running, it's terribly loud and disruptive, and when it's not running, it gets uncomfortably hot in the room. They have asked to move their class to another room because of the problem. C. . . | 2016-11-26 - 18010 - Roque Garcia-The room 113 in question is cooled by the AHU unit and is working ok. I contacted Nick from BMS and explained the complaint so I checked the AHU and the cold deck was 45 degrees and the dampers were operating correctly. The air compressor was running and providing the building with control air. I found out the issue was noise and i found a register that was vibrating so I realigned it and it stopped. - Roque Garcia | MWO: We've received a faculty complaint about the AC unit in Discovery 113. They say that when the AC is running, it's terribly loud and disruptive, and when it's not running, it gets uncomfortably hot in the room. They have asked to move their class to another room because of the problem. C. . . 2016-11-26 - 18010 - Roque Garcia-The room 113 in question is cooled by the AHU unit and is working ok. I contacted Nick from BMS and explained the complaint so I checked the AHU and the cold deck was 45 degrees and the dampers were operating correctly. The air compressor was running and providing the building with control air. I found out the issue was noise and i found a register that was vibrating so I realigned it and it stopped. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 50411 | TMPE-199746 | MWO CSAC: !! The pump in the lower level mechanical room in the CSAC is vibrating and making so much noise you can hear it in the Lobby at the Security Desk. This needs to be taken care of ASAP with a football game tomorrow. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-071. . . | 2016-11-09 - 23100 - Emailed shops information (FF) - Francesca Fernandez; 2016-11-09 - 23100 - Derek Gittings-replaced coupling, broken stud and rewired. Completed - Melanie Lamm | MWO CSAC: !! The pump in the lower level mechanical room in the CSAC is vibrating and making so much noise you can hear it in the Lobby at the Security Desk. This needs to be taken care of ASAP with a football game tomorrow. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-071. . . 2016-11-09 - 23100 - Emailed shops information (FF) - Francesca Fernandez; 2016-11-09 - 23100 - Derek Gittings-replaced coupling, broken stud and rewired. Completed - Melanie Lamm | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-11-09 | 174034 | RFMT-134297 | !! The fan in the bathroom is not working and a clear warm liquid is dripping from the vent. earlier on today it smelled like smoke in the bathroom but no one took much notice until the fan stopped working and the vent started dripping. Contact Name: Contact Phone Number: 4357303443 Contact Emai. . . | 2016-11-15 - 18010 - Thomas Zambrano-mike romero was called out for this w.o. - Thomas Zambrano | !! The fan in the bathroom is not working and a clear warm liquid is dripping from the vent. earlier on today it smelled like smoke in the bathroom but no one took much notice until the fan stopped working and the vent started dripping. Contact Name: Contact Phone Number: 4357303443 Contact Emai. . . 2016-11-15 - 18010 - Thomas Zambrano-mike romero was called out for this w.o. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174064 | RFMT-134267 | Please check a/c unit in Hayden E 223 for proper operation. | 2016-11-10 - 18010 - Salvatore Marasco Jr-This unit needs to be serviced by the A.C. techs. due to the reason that the valves ARE NOT functioning properly when called for at the thermostat. - Salvatore Marasco Jr | Please check a/c unit in Hayden E 223 for proper operation. 2016-11-10 - 18010 - Salvatore Marasco Jr-This unit needs to be serviced by the A.C. techs. due to the reason that the valves ARE NOT functioning properly when called for at the thermostat. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-11-09 | 174067 | RFMT-134264 | Please check Best C 315 for mold and a/c unit leak. | 2016-11-09 - 10010 - Eric Miller-Checked AC and room everything is OK. - Eric Miller | Please check Best C 315 for mold and a/c unit leak. 2016-11-09 - 10010 - Eric Miller-Checked AC and room everything is OK. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174073 | RFMT-134258 | Replaced G 100 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 45/5 mfd capacitor. - Thor Millsaps | Replaced G 100 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 45/5 mfd capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174074 | RFMT-134257 | Replaced G 102 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor - Thor Millsaps | Replaced G 102 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174075 | RFMT-134256 | Replaced F 206 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor. - Thor Millsaps | Replaced F 206 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174076 | RFMT-134255 | Replaced F 110 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor - Thor Millsaps | Replaced F 110 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 35/5 mfd capacitor and contactor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174077 | RFMT-134254 | Replaced F 100 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor. - Thor Millsaps | Replaced F 100 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174078 | RFMT-134253 | Replaced F laundry rm. HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and contactor - Thor Millsaps | Replaced F laundry rm. HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor and contactor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174079 | RFMT-134252 | Replaced F kitchen HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor - Thor Millsaps | Replaced F kitchen HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174080 | RFMT-134251 | Replaced F elevator HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor. - Thor Millsaps | Replaced F elevator HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 30/5 mfd capacitor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174083 | RFMT-134248 | Replaced E 214 HVAC condensing units capacitor | 2016-11-09 - 18010 - Thor Millsaps-Replaced 45/5 mfd capacitor - Thor Millsaps | Replaced E 214 HVAC condensing units capacitor 2016-11-09 - 18010 - Thor Millsaps-Replaced 45/5 mfd capacitor - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174085 | RFMT-134246 | Replaced E 210 HVAC condensing units capacitor | 2016-11-09 - 18010 - Simon Fernandez-replaced contactor and 35/5 capacitor - Simon Fernandez | Replaced E 210 HVAC condensing units capacitor 2016-11-09 - 18010 - Simon Fernandez-replaced contactor and 35/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-09 | 174086 | RFMT-134245 | Replaced E 200 HVAC condensing units capacitor | 2016-11-09 - 18010 - Simon Fernandez-replaced35/5 capacitor - Simon Fernandez | Replaced E 200 HVAC condensing units capacitor 2016-11-09 - 18010 - Simon Fernandez-replaced35/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 174087 | RFMT-134244 | Replaced E 100 HVAC condensing units capacitor | 2016-11-09 - 18010 - Simon Fernandez-replaced 45/5 cap. - Simon Fernandez | Replaced E 100 HVAC condensing units capacitor 2016-11-09 - 18010 - Simon Fernandez-replaced 45/5 cap. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 214371 | RACC-114239 | !! Our air conditioning is broken. There is nothing showing on the screen- the unit looks like it's dead. 4NO7G8H | NA | !! Our air conditioning is broken. There is nothing showing on the screen- the unit looks like it's dead. 4NO7G8H NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-11-09 | 233442 | POLY-114757 | boiler startup/service /maintenance 4O216EO | 2017-05-01 - 23020 - Esli Arvizo-performed unit start-up - Steve Clark; 2017-05-01 - 23020 - Allan Blair-performed unit start-up - Steve Clark; 2017-05-01 - 23020 - Suresh Nair-performed unit start-up - Steve Clark | boiler startup/service /maintenance 4O216EO 2017-05-01 - 23020 - Esli Arvizo-performed unit start-up - Steve Clark; 2017-05-01 - 23020 - Allan Blair-performed unit start-up - Steve Clark; 2017-05-01 - 23020 - Suresh Nair-performed unit start-up - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-09 | 233445 | POLY-114754 | A/C is not working and building got up to 84 yesterday. 42CDCJA | 2016-12-16 - 18290 - Allan Blair-found cond fan motor bad - replaced - Steve Clark; 2016-12-16 - 18290 - Allan Blair-found cond fan motor bad - replaced - Steve Clark | A/C is not working and building got up to 84 yesterday. 42CDCJA 2016-12-16 - 18290 - Allan Blair-found cond fan motor bad - replaced - Steve Clark; 2016-12-16 - 18290 - Allan Blair-found cond fan motor bad - replaced - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-10 | 50087 | TMPE-200070 | University Center 302: HVAC REPAIRED A LEAK A FEW DAYS AND THE A/C UNIT IS LEAKING AGAIN. ***ORIGINAL REQUEST***The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and a bucket. | 2016-11-10 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-16 - 18010 - Jennifer Moyer-Installed portable AC in room 302B to cool occupant and computers.Extra time was taken to match Y#, HP location, and thermostat. Unit is in process for replacement approval. - Jennifer Moyer; 2016-11-16 - 18010 - Robert Dauscher-Installed 2 portable A/C units. All of 302 hot. No AC working and fire damper was closed - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Installed 2 portable A/C units. All of 302 hot. No AC working and fire damper was closed - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Checked with ASU Fire Team. A company/person conducted testing that shut the AC off yesterday. Fire Team reset system to normal operation. - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Removed one of two portable A/C units. Other units in the room cooled the space after the fire alarm system was reset. - Jennifer Moyer; 2016-12-18 - 18010 - Robert Dauscher-Closing call - Robert Dauscher | University Center 302: HVAC REPAIRED A LEAK A FEW DAYS AND THE A/C UNIT IS LEAKING AGAIN. ***ORIGINAL REQUEST***The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and a bucket. 2016-11-10 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2016-11-16 - 18010 - Jennifer Moyer-Installed portable AC in room 302B to cool occupant and computers.Extra time was taken to match Y#, HP location, and thermostat. Unit is in process for replacement approval. - Jennifer Moyer; 2016-11-16 - 18010 - Robert Dauscher-Installed 2 portable A/C units. All of 302 hot. No AC working and fire damper was closed - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Installed 2 portable A/C units. All of 302 hot. No AC working and fire damper was closed - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Checked with ASU Fire Team. A company/person conducted testing that shut the AC off yesterday. Fire Team reset system to normal operation. - Jennifer Moyer; 2016-11-16 - 18010 - Jennifer Moyer-Removed one of two portable A/C units. Other units in the room cooled the space after the fire alarm system was reset. - Jennifer Moyer; 2016-12-18 - 18010 - Robert Dauscher-Closing call - Robert Dauscher | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2016-11-10 | 50113 | TMPE-200044 | MWO WGHL 202 from AC shop: please check a leak in sink by projector 3rd floor leaking down. There is a smell coming from this room, please inspect. Thank you. | 2016-11-17 - 18010 - John Crocker-TABLET IN SHOP FOR REPAIRS Transfer To HVAC SHOP BY RADIO. Leak From DuctOnto Ceiling Tile - John Crocker | MWO WGHL 202 from AC shop: please check a leak in sink by projector 3rd floor leaking down. There is a smell coming from this room, please inspect. Thank you. 2016-11-17 - 18010 - John Crocker-TABLET IN SHOP FOR REPAIRS Transfer To HVAC SHOP BY RADIO. Leak From DuctOnto Ceiling Tile - John Crocker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2016-11-10 | 50206 | TMPE-199951 | Fan not running, bad motor bearing. Found on lower roof above N.East entrance doors. | 2016-12-15 - 18230 - Roque Garcia-Checked the 3 exhaust fans on the roof of Wells Fargo Arena that belong to the kitchen. Tested all 3 and didnt find an issue with any of them. - Roque Garcia | Fan not running, bad motor bearing. Found on lower roof above N.East entrance doors. 2016-12-15 - 18230 - Roque Garcia-Checked the 3 exhaust fans on the roof of Wells Fargo Arena that belong to the kitchen. Tested all 3 and didnt find an issue with any of them. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-10 | 173997 | RFMT-134334 | !! My AC unit isn't working. When I tried to adjust the fan this morning it proceeded to make a sound but it wasn't working. Contact Name: Contact Phone Number: 4697770424 Contact Email: 4NOBBME | 2016-11-10 - 18010 - Joe Swan-Blower motor is bad. Occupant ok until Monday for repairs - Joe Swan; 2016-11-14 - 18010 - Salvatore Marasco Jr-Replaced one D1144 motor HC/00010. Room is cooling down. - Salvatore Marasco Jr | !! My AC unit isn't working. When I tried to adjust the fan this morning it proceeded to make a sound but it wasn't working. Contact Name: Contact Phone Number: 4697770424 Contact Email: 4NOBBME 2016-11-10 - 18010 - Joe Swan-Blower motor is bad. Occupant ok until Monday for repairs - Joe Swan; 2016-11-14 - 18010 - Salvatore Marasco Jr-Replaced one D1144 motor HC/00010. Room is cooling down. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-10 | 174026 | RFMT-134305 | Replaced U 205 rooftop condensing units capacitor. | 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Replaced U 205 rooftop condensing units capacitor. 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-10 | 174027 | RFMT-134304 | Replaced D 206 rooftop HVAC condensing units capacitor. | 2016-11-10 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Replaced D 206 rooftop HVAC condensing units capacitor. 2016-11-10 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-10 | 174029 | RFMT-134302 | Replaced C 106 rooftop HVAC condensing units capacitor & contactor | 2016-11-10 - 18010 - Simon Fernandez-replaced 35/5 capacitor - Simon Fernandez | Replaced C 106 rooftop HVAC condensing units capacitor & contactor 2016-11-10 - 18010 - Simon Fernandez-replaced 35/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-10 | 214340 | RACC-114270 | My name is Cassandra Rehwalt and I live in Vista, Building I, Room 2107. Our air conditioning unit stopped working on the side with rooms C and D, and currently it is 80 degrees in my room. I tried to fill out a TMA request online, but it seemed as though the site was down. | 2016-11-12 - 10010 - changed out capacitor and blown fuse. Richard - Jim Deal | My name is Cassandra Rehwalt and I live in Vista, Building I, Room 2107. Our air conditioning unit stopped working on the side with rooms C and D, and currently it is 80 degrees in my room. I tried to fill out a TMA request online, but it seemed as though the site was down. 2016-11-12 - 10010 - changed out capacitor and blown fuse. Richard - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-11 | 214336 | RACC-114274 | !! Room AC (air conditioning) is not working in my room only. Broken drawers (furniture) 4NM70KL | 2016-11-12 - 10010 - A/C was working fine adjusted vents to try and balance airflow. Richard - Jim Deal | !! Room AC (air conditioning) is not working in my room only. Broken drawers (furniture) 4NM70KL 2016-11-12 - 10010 - A/C was working fine adjusted vents to try and balance airflow. Richard - Jim Deal | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-13 | 214312 | RACC-114298 | !! Air conditioning not working. It has been set to cool but temperature remains constant or increase. Also my shower rod is bent and loosely screwed into the wall. Will need a new shower rod. Contact Name: Contact Phone Number: 6232971639 Contact Email: 4NH8O4C | 2016-11-17 - 10010 - replaced run capacitor , replaced curtain rod. Aaron - Jim Deal | !! Air conditioning not working. It has been set to cool but temperature remains constant or increase. Also my shower rod is bent and loosely screwed into the wall. Will need a new shower rod. Contact Name: Contact Phone Number: 6232971639 Contact Email: 4NH8O4C 2016-11-17 - 10010 - replaced run capacitor , replaced curtain rod. Aaron - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-13 | 3676 | WEST-107573 | Air Compressor - Monthly Maintenance | 2016-11-15 - xPM-0100-M - Robert Gailey-Ran compressor, aired up tires. - Robert Gailey | Air Compressor - Monthly Maintenance 2016-11-15 - xPM-0100-M - Robert Gailey-Ran compressor, aired up tires. - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-14 | 49329 | TMPE-200828 | SWO: !! It is reported, "LSA L1-73 (basement); back left corner after you walk through the door Details: The ice machine in this room is not producing ice. The machine is running, but it's not at the correct temperature and it doesn't seem like there's any water being pumped to the system. Please. . . | 2016-11-22 - 18210 - Thomas Gibble-cleaned and re-set ice machine - Thomas Gibble; 2016-11-22 - 18210 - Gail Jackson-cleaned and re-set ice machine - Thomas Gibble | SWO: !! It is reported, "LSA L1-73 (basement); back left corner after you walk through the door Details: The ice machine in this room is not producing ice. The machine is running, but it's not at the correct temperature and it doesn't seem like there's any water being pumped to the system. Please. . . 2016-11-22 - 18210 - Thomas Gibble-cleaned and re-set ice machine - Thomas Gibble; 2016-11-22 - 18210 - Gail Jackson-cleaned and re-set ice machine - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 49338 | TMPE-200819 | MWO SDFC 124: *TRANSFER* PL to HVAC to clean coils on the Drinking Fountain. We have a clogged coil vent. ORIG REQUEST !! Repeat Request. The water fountain to the left when you walk in is not working. This is a repeat request. 4NOCE5L | 2016-11-29 - 18090 - Jennifer Moyer- Unit not cooling, making huge racket, coil clogged solid. Bad compressor vlvs. Parts request in process. - Jennifer Moyer; 2016-11-29 - 18090 - Jennifer Moyer-Locate water fountain and assess repair/schedule repair around students. - Jennifer Moyer; 2016-12-30 - 18090 - Schedule AC shop to remove water fountain and bring into shop per Steve Palombo. - Jennifer Moyer; 2017-02-07 - 18090 - Jennifer Moyer-Removed water fountain and brought back to shop for repair. - Jennifer Moyer; 2017-02-09 - 18090 - Jennifer Moyer-Installed a quick-start on the compressor to improve function.Did not work, submitted parts request. - Jennifer Moyer; 2017-02-09 - 18090 - Jennifer Moyer-3:15-4:45pm Looked for caps, then installed water line and drain line caps. Red tagged lines in addition to previously installed caution tape. Entered info into TMA. (traffic from SDF to USB at this time is heavy) Process review of current and future water fountain repair vs. replacement underway. - Jennifer Moyer; 2017-05-04 - 18090 - Jennifer Moyer-Called to check on warranty. - Jennifer Moyer; 2017-05-10 - 18090 - Jennifer Moyer-Called Sean Hagerty 602-388-2222. He gave me the Elkay Rep. number 1-800-260-6640 to call for warranty work. The compressor is under warranty. - Jennifer Moyer; 2017-05-11 - 18090 - Elkay will be sending a tech. to 1551 South Rural Road.Parts and labor covered. - Jennifer Moyer; 2017-05-17 - 18090 - Jennifer Moyer-Called Elkay again for warranty work. Left message with tech. - Jennifer Moyer | MWO SDFC 124: *TRANSFER* PL to HVAC to clean coils on the Drinking Fountain. We have a clogged coil vent. ORIG REQUEST !! Repeat Request. The water fountain to the left when you walk in is not working. This is a repeat request. 4NOCE5L 2016-11-29 - 18090 - Jennifer Moyer- Unit not cooling, making huge racket, coil clogged solid. Bad compressor vlvs. Parts request in process. - Jennifer Moyer; 2016-11-29 - 18090 - Jennifer Moyer-Locate water fountain and assess repair/schedule repair around students. - Jennifer Moyer; 2016-12-30 - 18090 - Schedule AC shop to remove water fountain and bring into shop per Steve Palombo. - Jennifer Moyer; 2017-02-07 - 18090 - Jennifer Moyer-Removed water fountain and brought back to shop for repair. - Jennifer Moyer; 2017-02-09 - 18090 - Jennifer Moyer-Installed a quick-start on the compressor to improve function.Did not work, submitted parts request. - Jennifer Moyer; 2017-02-09 - 18090 - Jennifer Moyer-3:15-4:45pm Looked for caps, then installed water line and drain line caps. Red tagged lines in addition to previously installed caution tape. Entered info into TMA. (traffic from SDF to USB at this time is heavy) Process review of current and future water fountain repair vs. replacement underway. - Jennifer Moyer; 2017-05-04 - 18090 - Jennifer Moyer-Called to check on warranty. - Jennifer Moyer; 2017-05-10 - 18090 - Jennifer Moyer-Called Sean Hagerty 602-388-2222. He gave me the Elkay Rep. number 1-800-260-6640 to call for warranty work. The compressor is under warranty. - Jennifer Moyer; 2017-05-11 - 18090 - Elkay will be sending a tech. to 1551 South Rural Road.Parts and labor covered. - Jennifer Moyer; 2017-05-17 - 18090 - Jennifer Moyer-Called Elkay again for warranty work. Left message with tech. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-14 | 49372 | TMPE-200785 | MWO: ASU PD 107U1 THE UNIT ON THE WEST WALL IS STILL LEAKING. PLEASE SEND HVAC ASAP. ***ORIGINAL REQUEST***There's 2 wall units that are leaking. One is on the south wall and the other is on the west wall; it's the unit that is closest to the south wall. | 2016-11-17 - 18010 - Gail Jackson-Found no water on walls at this time, maybe doubled up on work order. - Gail Jackson | MWO: ASU PD 107U1 THE UNIT ON THE WEST WALL IS STILL LEAKING. PLEASE SEND HVAC ASAP. ***ORIGINAL REQUEST***There's 2 wall units that are leaking. One is on the south wall and the other is on the west wall; it's the unit that is closest to the south wall. 2016-11-17 - 18010 - Gail Jackson-Found no water on walls at this time, maybe doubled up on work order. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 49403 | TMPE-200754 | SPECIAL FUNDING: Diagnosed this unit with a \\u201cgrounded\\u201d compressor and system contamination. This unit is over 20 years old. Quote from Pueblo Mechanical to replace this unit. There is some additional roof top duct work included in this cost for supply and return air ductwork reconfiguration. We ha. . . | 2016-12-05 - 23100 - Jennifer Moyer-Picked up portable A/C unit. Trane unit workin' fine. - Jennifer Moyer; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. in-order to measure duct work - Oner Munoz; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. To check on progress of job. afterwards I accompanied Pueblo over to Tempe CTR. to address the A/C unit which was installed last month, then over to Ceramics which needed attention as well. - Oner Munoz; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. To check on progress of job. afterwards I accompanied Pueblo over to Tempe CTR. to address the A/C unit which was installed last month, then over to Ceramics which needed attention as well. - Oner Munoz | SPECIAL FUNDING: Diagnosed this unit with a \\u201cgrounded\\u201d compressor and system contamination. This unit is over 20 years old. Quote from Pueblo Mechanical to replace this unit. There is some additional roof top duct work included in this cost for supply and return air ductwork reconfiguration. We ha. . . 2016-12-05 - 23100 - Jennifer Moyer-Picked up portable A/C unit. Trane unit workin' fine. - Jennifer Moyer; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. in-order to measure duct work - Oner Munoz; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. To check on progress of job. afterwards I accompanied Pueblo over to Tempe CTR. to address the A/C unit which was installed last month, then over to Ceramics which needed attention as well. - Oner Munoz; 2016-12-05 - 23100 - Oner Munoz-met with Pueblo Mech. To check on progress of job. afterwards I accompanied Pueblo over to Tempe CTR. to address the A/C unit which was installed last month, then over to Ceramics which needed attention as well. - Oner Munoz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2016-11-14 | 49672 | TMPE-200485 | MWO: !! The A/C vent above cubicle 104BC has been blowing air 24/7 since last Monday. It is making it difficult for the occupant of that cubicle to work. Can someone please address this issue. Thank you! 4MO5454 | NA | MWO: !! The A/C vent above cubicle 104BC has been blowing air 24/7 since last Monday. It is making it difficult for the occupant of that cubicle to work. Can someone please address this issue. Thank you! 4MO5454 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 49704 | TMPE-200453 | MWO CP 1st Flr !! Please create a WO for HVAC shop to investigate flashing light on bldg. as reported by UTO dept to us. He said it normally means something has failed. This is an HVAC issue not EMS Thanks Jeffrey 4N00ABB | 2016-12-06 - 15000 - Zhi Yu-Arrived the alarm light was reset and off. No error code were found.. - Zhi Yu; 2016-12-06 - 15000 - Robert Dauscher-Arrived the alarm light was reset and off. No error code were found.. - Zhi Yu | MWO CP 1st Flr !! Please create a WO for HVAC shop to investigate flashing light on bldg. as reported by UTO dept to us. He said it normally means something has failed. This is an HVAC issue not EMS Thanks Jeffrey 4N00ABB 2016-12-06 - 15000 - Zhi Yu-Arrived the alarm light was reset and off. No error code were found.. - Zhi Yu; 2016-12-06 - 15000 - Robert Dauscher-Arrived the alarm light was reset and off. No error code were found.. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 173610 | RFMT-134721 | Replaced rooftop HVAC condensing units capacitor for R204 | 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Replaced rooftop HVAC condensing units capacitor for R204 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 173611 | RFMT-134720 | Replaced rooftop HVAC condensing units capacitor for Q303 | 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | Replaced rooftop HVAC condensing units capacitor for Q303 2016-11-14 - 18010 - Simon Fernandez-replaced 30/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 173612 | RFMT-134719 | Replaced rooftop HVAC condensing units capacitor for Q208 | 2016-11-14 - 18010 - Simon Fernandez-replaced 35/5 capacitor - Simon Fernandez | Replaced rooftop HVAC condensing units capacitor for Q208 2016-11-14 - 18010 - Simon Fernandez-replaced 35/5 capacitor - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 173669 | RFMT-134662 | HVAC Semi-Annual | 2016-11-17 - 50016 - Simon Fernandez- PM equipment; found bad spider bearings front and rear. bad belt AX-62 dual run cap.460 volt,10/10 mfd ,oval ( need parts on order ) - Simon Fernandez; 2016-11-17 - 50016 - Carrier HVAC Unit - Santino Aguilar; 2016-11-28 - 50016 - Costs manually added to RFMT-134662. Tino A. 11/28/2016 - Santino Aguilar; 2016-12-08 - 50016 - Simon Fernandez-replaced rear bearing ops checked okay - Simon Fernandez; 2016-12-08 - 50016 - Thor Millsaps-replaced front bearing ops checked okay - Simon Fernandez | HVAC Semi-Annual 2016-11-17 - 50016 - Simon Fernandez- PM equipment; found bad spider bearings front and rear. bad belt AX-62 dual run cap.460 volt,10/10 mfd ,oval ( need parts on order ) - Simon Fernandez; 2016-11-17 - 50016 - Carrier HVAC Unit - Santino Aguilar; 2016-11-28 - 50016 - Costs manually added to RFMT-134662. Tino A. 11/28/2016 - Santino Aguilar; 2016-12-08 - 50016 - Simon Fernandez-replaced rear bearing ops checked okay - Simon Fernandez; 2016-12-08 - 50016 - Thor Millsaps-replaced front bearing ops checked okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-14 | 28178 | TMPE-221979 | Naumann Hobbs located unit, inspected and found that unit has no brakes, torn seat and locked up seat belt. Notified customer and ordered parts. Removed/ reupholstered installed seat and replaced seat belt. total: 2771.47 | NA | Naumann Hobbs located unit, inspected and found that unit has no brakes, torn seat and locked up seat belt. Notified customer and ordered parts. Removed/ reupholstered installed seat and replaced seat belt. total: 2771.47 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-11-14 | 3605 | WEST-107644 | Replace motor.AHU-004 | 2017-01-17 - 18230 - Alfred Rohe-Assisted Run Em Again Motors With repair to new motor wiring and start-up procedures. Gave access to them to other needed areas. - Alfred Rohe | Replace motor.AHU-004 2017-01-17 - 18230 - Alfred Rohe-Assisted Run Em Again Motors With repair to new motor wiring and start-up procedures. Gave access to them to other needed areas. - Alfred Rohe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-15 | 48422 | TMPE-201735 | 1" Air Filter Replacement-Monthly Filter Order | 2016-11-28 - xPM-2200.01-FO - Jennifer Moyer-Order filters and coordinate with PM supervisor future filter ordering. Met with customer to see where filters were going. - Jennifer Moyer; 2016-12-22 - xPM-2200.01-FO - Jennifer Moyer-Email from Michael Comroe sent 12/14/16 to PM and A/C management. Filters to be delivered to: Arizona State University DACT 550 E. Orange ISTB 1 122 Tempe, Arizona 85287 340E-4x10x10, 1x18x10 340F-1x18x10 340D-1x18x10 340H-1x18x10 340J-1x18x10 340B-1x18x10 340A-1x18x10 340G-1x18x10 348L-1x10x12 Filters Delivered. - Jennifer Moyer | 1" Air Filter Replacement-Monthly Filter Order 2016-11-28 - xPM-2200.01-FO - Jennifer Moyer-Order filters and coordinate with PM supervisor future filter ordering. Met with customer to see where filters were going. - Jennifer Moyer; 2016-12-22 - xPM-2200.01-FO - Jennifer Moyer-Email from Michael Comroe sent 12/14/16 to PM and A/C management. Filters to be delivered to: Arizona State University DACT 550 E. Orange ISTB 1 122 Tempe, Arizona 85287 340E-4x10x10, 1x18x10 340F-1x18x10 340D-1x18x10 340H-1x18x10 340J-1x18x10 340B-1x18x10 340A-1x18x10 340G-1x18x10 348L-1x10x12 Filters Delivered. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49251 | TMPE-200906 | MWO: !! Replace blown fuse on the elevator disconnect switch located in the elevator machine room in the mechanical space. Spoke to John Scudalari regarding request Elevator Unit# 0885 Call when completed 516-903-1381 4O1D9GN | 2016-11-29 - 15000 - Chet Harvey-fuses replaced - Chet Harvey | MWO: !! Replace blown fuse on the elevator disconnect switch located in the elevator machine room in the mechanical space. Spoke to John Scudalari regarding request Elevator Unit# 0885 Call when completed 516-903-1381 4O1D9GN 2016-11-29 - 15000 - Chet Harvey-fuses replaced - Chet Harvey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49803 | TMPE-200354 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49804 | TMPE-200353 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49805 | TMPE-200352 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49806 | TMPE-200351 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49807 | TMPE-200350 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49808 | TMPE-200349 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49809 | TMPE-200348 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49810 | TMPE-200347 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49811 | TMPE-200346 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49812 | TMPE-200345 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49813 | TMPE-200344 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49814 | TMPE-200343 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 49815 | TMPE-200342 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 173538 | RFMT-134793 | Please check the A/C unit in room 131 the maintenance Shop. Simon | 2016-11-17 - 18010 - Simon Fernandez-trouble shoot a/c unit found bad motor control board, on order - Simon Fernandez; 2016-11-22 - 18010 - Simon Fernandez-removed and replaced motor control board (non stock item) - Simon Fernandez | Please check the A/C unit in room 131 the maintenance Shop. Simon 2016-11-17 - 18010 - Simon Fernandez-trouble shoot a/c unit found bad motor control board, on order - Simon Fernandez; 2016-11-22 - 18010 - Simon Fernandez-removed and replaced motor control board (non stock item) - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-15 | 173555 | RFMT-134776 | Fan coil malfunction rm. 110. | 2016-11-15 - 18010 - Thor Millsaps-Checked fan coil in room. Tightened blower wheel to reduce noise. - Thor Millsaps | Fan coil malfunction rm. 110. 2016-11-15 - 18010 - Thor Millsaps-Checked fan coil in room. Tightened blower wheel to reduce noise. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-15 | 233319 | POLY-114880 | REPAIR BAD DUCT WORK TO VAV3 4O216EO | 2016-11-28 - 18010 - Darusman Amin-11/4 - Darusman and Allan repaired the broken ductwork in two locations. - Gayle Swenson | REPAIR BAD DUCT WORK TO VAV3 4O216EO 2016-11-28 - 18010 - Darusman Amin-11/4 - Darusman and Allan repaired the broken ductwork in two locations. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 2
2016-11-15 | 233322 | POLY-114877 | AIR FLOW DAMPER STUCK 4O216EO | 2016-11-28 - 18010 - Darusman Amin-11/3 - Darusman and Allan found bad damper actuator, and replaced it. - Gayle Swenson | AIR FLOW DAMPER STUCK 4O216EO 2016-11-28 - 18010 - Darusman Amin-11/3 - Darusman and Allan found bad damper actuator, and replaced it. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-16 | 48940 | TMPE-201217 | MWO CSAC 303 Water leak under the sink in room 303. 4NM9B6B | 2016-11-17 - 23000 - Jesus Colon-I was not sure if the water was coming from the sink plumbing or from the reverse osmosis system. I turned off the ro system. We cleaned all the water up from under the sink. I returned about two hours later and turned the R.O. system back on. At this time I found that the water was coming form a manifold on the R.O. unit. This unit is serviced by an outside company. I turned the water off to the R.O. system and informed Bonnie Kopp. She will contact Sparkle water. Materials: 0 Hrs 1.0 JColo\\xf1 - Jesus Colon [Modified: 2016-11-22 Stephen Chisler] | MWO CSAC 303 Water leak under the sink in room 303. 4NM9B6B 2016-11-17 - 23000 - Jesus Colon-I was not sure if the water was coming from the sink plumbing or from the reverse osmosis system. I turned off the ro system. We cleaned all the water up from under the sink. I returned about two hours later and turned the R.O. system back on. At this time I found that the water was coming form a manifold on the R.O. unit. This unit is serviced by an outside company. I turned the water off to the R.O. system and informed Bonnie Kopp. She will contact Sparkle water. Materials: 0 Hrs 1.0 JColo\\xf1 - Jesus Colon [Modified: 2016-11-22 Stephen Chisler] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-16 | 49045 | TMPE-201112 | MWO UNCTRC 300L1 Service HP-3-18 , Y# 08427 Schedule Jennifer action was done, work order is needed for time and unit record. | 2016-11-16 - 18010 - Jennifer Moyer-Submit work order to repair/replace breaker. Installed new filter. Unit is cooling. - Jennifer Moyer; 2016-11-16 - 18010 - Extra time was taken to match the Y#, HP location, thermostat, and breaker. - Jennifer Moyer | MWO UNCTRC 300L1 Service HP-3-18 , Y# 08427 Schedule Jennifer action was done, work order is needed for time and unit record. 2016-11-16 - 18010 - Jennifer Moyer-Submit work order to repair/replace breaker. Installed new filter. Unit is cooling. - Jennifer Moyer; 2016-11-16 - 18010 - Extra time was taken to match the Y#, HP location, thermostat, and breaker. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-16 | 49046 | TMPE-201111 | SWO: Please extend the existing exhaust pip above the adjacent AC unit in the third base concession stand at Phx Muni. Contact James for access. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF | 2016-11-18 - 18010 - Carl Karr-Checked job out. Pipe in question is a plumbing vent. Job sent to plumbing shop. - Carl Karr; 2016-11-18 - 18010 - Robert Dauscher-Checked job out. Pipe in question is a plumbing vent. Job sent to plumbing shop. - Carl Karr | SWO: Please extend the existing exhaust pip above the adjacent AC unit in the third base concession stand at Phx Muni. Contact James for access. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF 2016-11-18 - 18010 - Carl Karr-Checked job out. Pipe in question is a plumbing vent. Job sent to plumbing shop. - Carl Karr; 2016-11-18 - 18010 - Robert Dauscher-Checked job out. Pipe in question is a plumbing vent. Job sent to plumbing shop. - Carl Karr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-16 | 49051 | TMPE-201106 | MWO: Service HP-3-15, Y# 08429 Schedule to Jennifer, service was done, work order is needed to record time and unit repair. | 2016-11-16 - 18010 - Jennifer Moyer-Reset unit after fire alarm test.Adjusted set point for customer to 75 cooling.Extra time was taken to match the Y#, HP location, and the room supplied. - Jennifer Moyer | MWO: Service HP-3-15, Y# 08429 Schedule to Jennifer, service was done, work order is needed to record time and unit repair. 2016-11-16 - 18010 - Jennifer Moyer-Reset unit after fire alarm test.Adjusted set point for customer to 75 cooling.Extra time was taken to match the Y#, HP location, and the room supplied. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-16 | 49080 | TMPE-201077 | University Center 302: new work order made for AC08428 HVAC REPAIRED A LEAK A FEW DAYS AND THE A/C UNIT IS LEAKING AGAIN. ***ORIGINAL REQUEST***The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and. . . | 2016-11-16 - 18010 - Jennifer Moyer-This unit had set points that were too close together. The cooling was set at 73 degrees. Extra time was taken to match the Y#, HP location, and thermostat to the unit. This unit was iced up. Disconnect turned off to defrost. - Jennifer Moyer [Modified: 2016-11-16 Jennifer Moyer]; 2016-11-16 - 18010 - Jennifer Moyer-Turned on disconnect and monitored unit for cooling. Seems to be operating normally. Will consult the customer later today. - Jennifer Moyer; 2016-11-16 - 18010 - Called customer 8/16/16 4:10pm. Unit is cooling properly and I will pick up the portable tomorrow morning. - Jennifer Moyer; 2016-11-22 - 18010 - Jennifer Moyer-pick up portable. - Jennifer Moyer | University Center 302: new work order made for AC08428 HVAC REPAIRED A LEAK A FEW DAYS AND THE A/C UNIT IS LEAKING AGAIN. ***ORIGINAL REQUEST***The ceiling tile is bowing again and about to fall. There is another leak. Please send someone to make repairs, ASAP. I have put down plastic and. . . 2016-11-16 - 18010 - Jennifer Moyer-This unit had set points that were too close together. The cooling was set at 73 degrees. Extra time was taken to match the Y#, HP location, and thermostat to the unit. This unit was iced up. Disconnect turned off to defrost. - Jennifer Moyer [Modified: 2016-11-16 Jennifer Moyer]; 2016-11-16 - 18010 - Jennifer Moyer-Turned on disconnect and monitored unit for cooling. Seems to be operating normally. Will consult the customer later today. - Jennifer Moyer; 2016-11-16 - 18010 - Called customer 8/16/16 4:10pm. Unit is cooling properly and I will pick up the portable tomorrow morning. - Jennifer Moyer; 2016-11-22 - 18010 - Jennifer Moyer-pick up portable. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-16 | 214191 | RACC-114419 | !! The air conditioner is leaking and has made a puddle. 4NGKMGD | 2016-11-21 - 10010 - cleared trap under sink. Richard - Jim Deal | !! The air conditioner is leaking and has made a puddle. 4NGKMGD 2016-11-21 - 10010 - cleared trap under sink. Richard - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-17 | 48760 | TMPE-201397 | SWO MU Qdoba Hello, Today we had an ecolab personnel out to look at this cooler. He replaced the hot loop and now stating that the compressor is failing. I assume that this compressor came with a warranty. Can we please look into this and have it repaired ASAP? Thank you, | 2016-11-28 - 18100 - Gail Jackson-Trip to ARS Phx to swap out warranty compressor and pickup parts - Gail Jackson; 2016-11-30 - 18100 - Zhi Yu-We bring prep cooler back to shop and diagnose the system contaminated with water. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We bring prep cooler back to shop and diagnose the system contaminated with water. - Zhi Yu; 2016-11-30 - 18100 - Zhi Yu-We Replaced New compressor, liquid drier, and TXV. We removed evap coil and flush the system with R-11, also blow out with nitrogen. We vacuum to 450 micron and charge 19oz R134a. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We Replaced New compressor, liquid drier, and TXV. We removed evap coil and flush the system with R-11, also blow out with nitrogen. We vacuum to 450 micron and charge 19oz R134a. - Zhi Yu; 2016-11-30 - 18100 - Zhi Yu-We test unit overnight. Temp @ 32-38 We delivery back to Qdoba. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We test unit overnight. Temp @ 32-38 We delivery back to Qdoba. - Zhi Yu | SWO MU Qdoba Hello, Today we had an ecolab personnel out to look at this cooler. He replaced the hot loop and now stating that the compressor is failing. I assume that this compressor came with a warranty. Can we please look into this and have it repaired ASAP? Thank you, 2016-11-28 - 18100 - Gail Jackson-Trip to ARS Phx to swap out warranty compressor and pickup parts - Gail Jackson; 2016-11-30 - 18100 - Zhi Yu-We bring prep cooler back to shop and diagnose the system contaminated with water. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We bring prep cooler back to shop and diagnose the system contaminated with water. - Zhi Yu; 2016-11-30 - 18100 - Zhi Yu-We Replaced New compressor, liquid drier, and TXV. We removed evap coil and flush the system with R-11, also blow out with nitrogen. We vacuum to 450 micron and charge 19oz R134a. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We Replaced New compressor, liquid drier, and TXV. We removed evap coil and flush the system with R-11, also blow out with nitrogen. We vacuum to 450 micron and charge 19oz R134a. - Zhi Yu; 2016-11-30 - 18100 - Zhi Yu-We test unit overnight. Temp @ 32-38 We delivery back to Qdoba. - Zhi Yu; 2016-11-30 - 18100 - Gail Jackson-We test unit overnight. Temp @ 32-38 We delivery back to Qdoba. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-17 | 48782 | TMPE-201375 | MWO ISTB2 185 CR TO MECHANICAL SHOP - SOUNDS LIKE IT MAY BE A BELT OR SOMETHING FROM THE A/C UNIT. ***ORIGINAL REQUEST***Can you please investigate and address the high pitched chirping sounds on the East side of the room near the ovens? It sounds like something is rubbing, something needs l. . . | 2016-12-02 - 18010 - Thomas Gibble-changed belt and cleaned coil. belt size a-52 - Thomas Gibble | MWO ISTB2 185 CR TO MECHANICAL SHOP - SOUNDS LIKE IT MAY BE A BELT OR SOMETHING FROM THE A/C UNIT. ***ORIGINAL REQUEST***Can you please investigate and address the high pitched chirping sounds on the East side of the room near the ovens? It sounds like something is rubbing, something needs l. . . 2016-12-02 - 18010 - Thomas Gibble-changed belt and cleaned coil. belt size a-52 - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-17 | 48822 | TMPE-201335 | SWO: FSST: Rooftop A/C unit 160A-EXF-01017, Fire alarm activation has shut of rooftop unit, has removed 24V to unit. Please reset system so we can turn on A/C unit. Please work with Simon @ 602-769-1457 to ensure unit is back up and running Submitted by 4N0JHK6 | 2016-12-13 - 17000 - Danilo Benitez-Found that the safety module for the unit is open. Tried to locate the module but could not find it. The print does not show the exact location of the module so as the program. Traced the conduit but it did not lead us to the module. - Danilo Benitez; 2016-12-15 - 17000 - Danilo Benitez-Replaced two Control Relay for roof AHU shutdown. - Danilo Benitez | SWO: FSST: Rooftop A/C unit 160A-EXF-01017, Fire alarm activation has shut of rooftop unit, has removed 24V to unit. Please reset system so we can turn on A/C unit. Please work with Simon @ 602-769-1457 to ensure unit is back up and running Submitted by 4N0JHK6 2016-12-13 - 17000 - Danilo Benitez-Found that the safety module for the unit is open. Tried to locate the module but could not find it. The print does not show the exact location of the module so as the program. Traced the conduit but it did not lead us to the module. - Danilo Benitez; 2016-12-15 - 17000 - Danilo Benitez-Replaced two Control Relay for roof AHU shutdown. - Danilo Benitez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-17 | 48837 | TMPE-201320 | Low duct pressure alarm y362 / belts are broken. Located in the basement area. Please contact Mike for direction location and issue. 480-330-3235 | 2016-11-22 - 18010 - Jennifer Moyer-Installed new belts, however the blower wheel was broken and the unit could not be started. - Jennifer Moyer | Low duct pressure alarm y362 / belts are broken. Located in the basement area. Please contact Mike for direction location and issue. 480-330-3235 2016-11-22 - 18010 - Jennifer Moyer-Installed new belts, however the blower wheel was broken and the unit could not be started. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3
2016-11-17 | 48894 | TMPE-201263 | SWO: !! The pump at the lift station is not working. The pump is located on the west side of Starbucks, outside. The lift station was pumped this morning at 7 am. It will quickly fill up again. I called John Howell with HVAC Mechanical. Brian was sent over and he has pictures of the station. . . . | 2016-11-22 - 23100 - Thomas Gibble-helped electrician replace GFI - Thomas Gibble; 2016-11-22 - 23100 - Thomas Gibble-put pump upright and undid the hose - Thomas Gibble; 2016-11-23 - 23100 - Robert Dauscher-helped electrician put in GFI - Thomas Gibble; 2016-12-01 - 23100 - 11/21/2016 1OT 5pm-6pm Thomas Gibble - PV East GFI needs to be replaced for pump. - Kerri Perkins; 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-07 - 23100 - Michael Kelley-put in temp. sump pump to pump down pit. Roped off area - Michael Kelley; 2016-12-07 - 23100 - Michael Kelley-Found bad float and broken discharge line. GFI bad in pit - Michael Kelley; 2016-12-07 - 23100 - Michael Kelley-Went back and added band to Discharge line. Could not find elec. to GFI. - Michael Kelley; 2016-12-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-21 - 23100 - Michael Kelley-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Robert Dauscher-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Roque Garcia-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Midhat Mukanovic-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley | SWO: !! The pump at the lift station is not working. The pump is located on the west side of Starbucks, outside. The lift station was pumped this morning at 7 am. It will quickly fill up again. I called John Howell with HVAC Mechanical. Brian was sent over and he has pictures of the station. . . . 2016-11-22 - 23100 - Thomas Gibble-helped electrician replace GFI - Thomas Gibble; 2016-11-22 - 23100 - Thomas Gibble-put pump upright and undid the hose - Thomas Gibble; 2016-11-23 - 23100 - Robert Dauscher-helped electrician put in GFI - Thomas Gibble; 2016-12-01 - 23100 - 11/21/2016 1OT 5pm-6pm Thomas Gibble - PV East GFI needs to be replaced for pump. - Kerri Perkins; 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-07 - 23100 - Michael Kelley-put in temp. sump pump to pump down pit. Roped off area - Michael Kelley; 2016-12-07 - 23100 - Michael Kelley-Found bad float and broken discharge line. GFI bad in pit - Michael Kelley; 2016-12-07 - 23100 - Michael Kelley-Went back and added band to Discharge line. Could not find elec. to GFI. - Michael Kelley; 2016-12-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-21 - 23100 - Michael Kelley-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Robert Dauscher-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Roque Garcia-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley; 2016-12-21 - 23100 - Midhat Mukanovic-replaced pipe on pump. drained pit. found electrical problem with GFI. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2016-11-17 | 233258 | POLY-114941 | boiler start-up/service/maintenance 4O216EO | 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - ORDERED PARTS - Steve Clark; 2017-01-13 - 23020 - Esli Arvizo-SERVICED UNIT - ORDERED PARTS - Steve Clark; 2017-01-13 - 23020 - Esli Arvizo-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Darusman Amin-SERVICED UNIT - Steve Clark | boiler start-up/service/maintenance 4O216EO 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - ORDERED PARTS - Steve Clark; 2017-01-13 - 23020 - Esli Arvizo-SERVICED UNIT - ORDERED PARTS - Steve Clark; 2017-01-13 - 23020 - Esli Arvizo-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Suresh Nair-SERVICED UNIT - Steve Clark; 2017-01-13 - 23020 - Darusman Amin-SERVICED UNIT - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-17 | 233271 | POLY-114928 | Housing has told me that I need to ask you for a new filter for the HVAC unit. The filter size written on the HVAC reads 16 x 28 x 1. But the filter itself reads 16 X 27 5/8 x 1. 4NJC292 | NA | Housing has told me that I need to ask you for a new filter for the HVAC unit. The filter size written on the HVAC reads 16 x 28 x 1. But the filter itself reads 16 X 27 5/8 x 1. 4NJC292 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-18 | 48693 | TMPE-201464 | MWO PSY L1-12U1 AH 3 Vivarium humidifier is not able to maintain needed humidification to zone. Shows a time to clean tank warning. Send to HVAC for humidifier checkout and cleaning. 42B213C | 2017-03-07 - 18010 - Michael Kelley-Checked out unit. All was perfect. job complete. no alarms or cleaning needed at this time - Michael Kelley; 2017-03-07 - 18010 - Zhi Yu-Checked out unit. All was perfect. job complete. no alarms or cleaning needed at this time - Michael Kelley | MWO PSY L1-12U1 AH 3 Vivarium humidifier is not able to maintain needed humidification to zone. Shows a time to clean tank warning. Send to HVAC for humidifier checkout and cleaning. 42B213C 2017-03-07 - 18010 - Michael Kelley-Checked out unit. All was perfect. job complete. no alarms or cleaning needed at this time - Michael Kelley; 2017-03-07 - 18010 - Zhi Yu-Checked out unit. All was perfect. job complete. no alarms or cleaning needed at this time - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-18 | 254284 | DTPC-114254 | Fan Coil Unit 10-7 NR Not Responding. | 2016-11-18 - 18090 - Ross Hossack-Found unit with blown fuse. Checked for short(no short)Replaced fuse.Unit running. - Ross Hossack | Fan Coil Unit 10-7 NR Not Responding. 2016-11-18 - 18090 - Ross Hossack-Found unit with blown fuse. Checked for short(no short)Replaced fuse.Unit running. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-20 | 3528 | WEST-107721 | ADA Door Weekly Inspection | 2016-11-22 - xPM-WC-ADADOOR - Tim Jowers-checked all of the units, need to check 301 door lock. 221 door lock. changed the battery in the 310w1 outside button it is still not working, ran out of time will work on it on monday. - Tim Jowers; 2016-11-28 - xPM-WC-ADADOOR - Tim Jowers-found that the door button on the 310w1 outer door had a bad battery/battery connector,replaced the battery but ran out of time to fix the button. the 301 door has a bad striker,I will talk with Pete about replacement. the 221 door is not set up to unlock the door so the a.d.a. opener cannot be used. - Tim Jowers | ADA Door Weekly Inspection 2016-11-22 - xPM-WC-ADADOOR - Tim Jowers-checked all of the units, need to check 301 door lock. 221 door lock. changed the battery in the 310w1 outside button it is still not working, ran out of time will work on it on monday. - Tim Jowers; 2016-11-28 - xPM-WC-ADADOOR - Tim Jowers-found that the door button on the 310w1 outer door had a bad battery/battery connector,replaced the battery but ran out of time to fix the button. the 301 door has a bad striker,I will talk with Pete about replacement. the 221 door is not set up to unlock the door so the a.d.a. opener cannot be used. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-11-21 | 48406 | TMPE-201751 | MWO: Unit not cooling well and making noise. Please repair Director Pat Smith's Office. | 2016-12-28 - 18010 - Jennifer Moyer-Installed new motor and discovered the power head was missing from the water valve. I am ordering a new water valve, as the old one was mostly plugged. - Jennifer Moyer; 2016-12-30 - 18010 - Jennifer Moyer-Remove old water valve and order new one. - Jennifer Moyer; 2017-01-04 - 18010 - Jennifer Moyer-Schedule repair. - Jennifer Moyer; 2017-01-10 - 18010 - Jennifer Moyer-Acid flush the coil.Unfortunately there is a pin hole leak in the coil. - Jennifer Moyer; 2017-01-25 - 18010 - Jennifer Moyer-Attempt repair of leak in fan coil unit. Unit is too corroded. Request new unit. - Jennifer Moyer; 2017-01-25 - 18010 - Zhi Yu-Attempt repair of leak in fan coil unit. Unit is too corroded. Request new unit. - Jennifer Moyer; 2017-02-09 - 18010 - Carl Karr-Fabricate pan. - Carl Karr; 2017-02-10 - 18010 - Carl Karr-Fabricate pan. - Carl Karr; 2017-02-13 - 18010 - Carl Karr-Fabricate condensate pan. - Carl Karr | MWO: Unit not cooling well and making noise. Please repair Director Pat Smith's Office. 2016-12-28 - 18010 - Jennifer Moyer-Installed new motor and discovered the power head was missing from the water valve. I am ordering a new water valve, as the old one was mostly plugged. - Jennifer Moyer; 2016-12-30 - 18010 - Jennifer Moyer-Remove old water valve and order new one. - Jennifer Moyer; 2017-01-04 - 18010 - Jennifer Moyer-Schedule repair. - Jennifer Moyer; 2017-01-10 - 18010 - Jennifer Moyer-Acid flush the coil.Unfortunately there is a pin hole leak in the coil. - Jennifer Moyer; 2017-01-25 - 18010 - Jennifer Moyer-Attempt repair of leak in fan coil unit. Unit is too corroded. Request new unit. - Jennifer Moyer; 2017-01-25 - 18010 - Zhi Yu-Attempt repair of leak in fan coil unit. Unit is too corroded. Request new unit. - Jennifer Moyer; 2017-02-09 - 18010 - Carl Karr-Fabricate pan. - Carl Karr; 2017-02-10 - 18010 - Carl Karr-Fabricate pan. - Carl Karr; 2017-02-13 - 18010 - Carl Karr-Fabricate condensate pan. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2016-11-21 | 173119 | RFMT-135212 | ASUHC-Agent: Ahmed Khalil Description: Lounge air conditioning panel vent cover has been taken off. Who was dispatched: Joe Swan Time of dispatch: 5:51PM | 2016-11-22 - 18010 - Joe Swan-Reinstalled A/C panel - Joe Swan | ASUHC-Agent: Ahmed Khalil Description: Lounge air conditioning panel vent cover has been taken off. Who was dispatched: Joe Swan Time of dispatch: 5:51PM 2016-11-22 - 18010 - Joe Swan-Reinstalled A/C panel - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-21 | 173153 | RFMT-135178 | !! AC unit will not cool off just throws warm air 4NH8NJ2 | 2016-11-22 - 18010 - Casey Faultner-Replaced broken Thermostat. Room cool down now. - Casey Faultner | !! AC unit will not cool off just throws warm air 4NH8NJ2 2016-11-22 - 18010 - Casey Faultner-Replaced broken Thermostat. Room cool down now. - Casey Faultner | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-21 | 214051 | RACC-114559 | Our air-conditioning unit has been leaking and running constantly. In the hall on the left side. 4NJCH59 | 2016-11-28 - 10010 - charged system Aaron - Jim Deal | Our air-conditioning unit has been leaking and running constantly. In the hall on the left side. 4NJCH59 2016-11-28 - 10010 - charged system Aaron - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-21 | 233193 | POLY-115006 | !! Please note: This was called in by George Vasquez at approximately 10:12 a.m November 21, 2016. Shelly Took the Call. I do know that OZZIE maintenance technician responded. Issue home owner 5804 S, Terripin stated that the light switch, is catching fire, then corrected and stated it was sp. . . | NA | !! Please note: This was called in by George Vasquez at approximately 10:12 a.m November 21, 2016. Shelly Took the Call. I do know that OZZIE maintenance technician responded. Issue home owner 5804 S, Terripin stated that the light switch, is catching fire, then corrected and stated it was sp. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-21 | 254202 | DTPC-114336 | !! Three offices in a row, 533, 517 & 515 are freezing. It feels like the air conditioning is on full blast. Would someone be able to check these office out and see if it can be corrected? Thank you for all your help! 42CHG1D | 2016-11-21 - 18300 - Steve Skibbe-switch blower to cycle there is no heat as of now will investigate further tomorrow - Steve Skibbe; 2016-11-22 - 18300 - Steve Skibbe-checked out unit cannot access fully the heater section due to furniture placement. think it might be a bad transformer have to order will consult brian from climatec - Steve Skibbe; 2016-11-23 - 18300 - Steve Skibbe-climatec Brian and me rechecked unit and eventually found a programing error keeping the heat locked out this has been revised and is in working order now - Steve Skibbe | !! Three offices in a row, 533, 517 & 515 are freezing. It feels like the air conditioning is on full blast. Would someone be able to check these office out and see if it can be corrected? Thank you for all your help! 42CHG1D 2016-11-21 - 18300 - Steve Skibbe-switch blower to cycle there is no heat as of now will investigate further tomorrow - Steve Skibbe; 2016-11-22 - 18300 - Steve Skibbe-checked out unit cannot access fully the heater section due to furniture placement. think it might be a bad transformer have to order will consult brian from climatec - Steve Skibbe; 2016-11-23 - 18300 - Steve Skibbe-climatec Brian and me rechecked unit and eventually found a programing error keeping the heat locked out this has been revised and is in working order now - Steve Skibbe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-11-21 | 254214 | DTPC-114324 | !! We have no A/C in the control room, B4-113. Ralph is aware of it, and we immediate assistance in getting this fixed. We have the motor, but we need Roof Access. If any problems, please call Julee at 452-3002. Thank you, Chris | 2016-11-21 - 18010 - Ralph Lemons-Spoke to Julee in office and they are to install the outdoor fan motor today. - Ralph Lemons; 2016-11-21 - 18010 - Ross Hossack-Spoke to Julee in office and they are to install the outdoor fan motor today. - Ralph Lemons | !! We have no A/C in the control room, B4-113. Ralph is aware of it, and we immediate assistance in getting this fixed. We have the motor, but we need Roof Access. If any problems, please call Julee at 452-3002. Thank you, Chris 2016-11-21 - 18010 - Ralph Lemons-Spoke to Julee in office and they are to install the outdoor fan motor today. - Ralph Lemons; 2016-11-21 - 18010 - Ross Hossack-Spoke to Julee in office and they are to install the outdoor fan motor today. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 48195 | TMPE-201962 | !! Please create a WO for HVAC shop to work on condensing unit that serves AH5 located in Rm 114U1. CU is on the roof. Compressor will not turn on has voltage to board, contactor will not pull in did not see any reset button. Tried powering down unit to see if that would clear....did not! Thanks. . . | 2016-12-04 - 18010 - Robert Dauscher-Unit in need of replacement. Unit has had several leaks over the past couple of years. Twice this year alone in the last two(2) months which has needed 13lbs 9oz of r410a EACH Time!!!! On this last failure unit lost all refrigerant, on a non repairable leak on the reversing valve. Since the room will never need heating(data room) we removed the reversing valve and straight piped the unit for cooling only. While re-filling the unit with refrigerant we discovered that the control board is also bad, as it wouldn't call for compressor or fan to turn on. At this time the only viable part in the condenser is the compressor. And with all of the oil loss it is only a matter od time until that fails as well. UNIT NEEDS REPLACEMENT!! Sending info to Brian and Steve for replacement. - Robert Dauscher; 2016-12-04 - 18010 - Zhi Yu-Unit in need of replacement. Unit has had several leaks over the past couple of years. Twice this year alone in the last two(2) months which has needed 13lbs 9oz of r410a EACH Time!!!! On this last failure unit lost all refrigerant, on a non repairable leak on the reversing valve. Since the room will never need heating(data room) we removed the reversing valve and straight piped the unit for cooling only. While re-filling the unit with refrigerant we discovered that the control board is also bad, as it wouldn't call for compressor or fan to turn on. At this time the only viable part in the condenser is the compressor. And with all of the oil loss it is only a matter od time until that fails as well. UNIT NEEDS REPLACEMENT!! Sending info to Brian and Steve for replacement. - Robert Dauscher | !! Please create a WO for HVAC shop to work on condensing unit that serves AH5 located in Rm 114U1. CU is on the roof. Compressor will not turn on has voltage to board, contactor will not pull in did not see any reset button. Tried powering down unit to see if that would clear....did not! Thanks. . . 2016-12-04 - 18010 - Robert Dauscher-Unit in need of replacement. Unit has had several leaks over the past couple of years. Twice this year alone in the last two(2) months which has needed 13lbs 9oz of r410a EACH Time!!!! On this last failure unit lost all refrigerant, on a non repairable leak on the reversing valve. Since the room will never need heating(data room) we removed the reversing valve and straight piped the unit for cooling only. While re-filling the unit with refrigerant we discovered that the control board is also bad, as it wouldn't call for compressor or fan to turn on. At this time the only viable part in the condenser is the compressor. And with all of the oil loss it is only a matter od time until that fails as well. UNIT NEEDS REPLACEMENT!! Sending info to Brian and Steve for replacement. - Robert Dauscher; 2016-12-04 - 18010 - Zhi Yu-Unit in need of replacement. Unit has had several leaks over the past couple of years. Twice this year alone in the last two(2) months which has needed 13lbs 9oz of r410a EACH Time!!!! On this last failure unit lost all refrigerant, on a non repairable leak on the reversing valve. Since the room will never need heating(data room) we removed the reversing valve and straight piped the unit for cooling only. While re-filling the unit with refrigerant we discovered that the control board is also bad, as it wouldn't call for compressor or fan to turn on. At this time the only viable part in the condenser is the compressor. And with all of the oil loss it is only a matter od time until that fails as well. UNIT NEEDS REPLACEMENT!! Sending info to Brian and Steve for replacement. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 10
2016-11-22 | 48274 | TMPE-201883 | MWO: PSD 57 The chiller compressor is not cooling . Please have someone make repairs asap. Have the technician call me first. I want to be there for the repairs and I also have questions to ask him. | 2016-12-02 - 18080 - Thomas Gibble-adjusted water pressure on the chiller pump - Thomas Gibble | MWO: PSD 57 The chiller compressor is not cooling . Please have someone make repairs asap. Have the technician call me first. I want to be there for the repairs and I also have questions to ask him. 2016-12-02 - 18080 - Thomas Gibble-adjusted water pressure on the chiller pump - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-22 | 48305 | TMPE-201852 | SWO ACACI FACMAN HVAC- Requesting for 1 bottle of 410-A | 2016-11-29 - 18010 - 1 Drum R-410A Refrigerant delivered to Simon Fernandez (Will Call Johnstone Mesa) Shop Request AC-1513644 $169.37. - John Howell | SWO ACACI FACMAN HVAC- Requesting for 1 bottle of 410-A 2016-11-29 - 18010 - 1 Drum R-410A Refrigerant delivered to Simon Fernandez (Will Call Johnstone Mesa) Shop Request AC-1513644 $169.37. - John Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-22 | 49411 | TMPE-200746 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 49462 | TMPE-200695 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 49463 | TMPE-200694 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 49464 | TMPE-200693 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 49465 | TMPE-200692 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 49466 | TMPE-200691 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-22 | 173075 | RFMT-135256 | Please lock out tag out HVAC unit tomorrow morning at 8:30 a.m. in K 106 prior to bed bug treatment. | 2016-11-23 - 19080 - Simon Fernandez-locked out and tagged disconnect for a/c unit - Simon Fernandez | Please lock out tag out HVAC unit tomorrow morning at 8:30 a.m. in K 106 prior to bed bug treatment. 2016-11-23 - 19080 - Simon Fernandez-locked out and tagged disconnect for a/c unit - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2016-11-22 | 173102 | RFMT-135229 | ASUHC-Agent: Ahmed Khalil Description: Lounge air conditioning panel vent cover has been taken off. Who was dispatched: Joe Swan Time of dispatch: 5:51PM | 2016-11-23 - 18010 - Simon Fernandez-checked a/c unit for proper operation, and reinstalled panel - Simon Fernandez | ASUHC-Agent: Ahmed Khalil Description: Lounge air conditioning panel vent cover has been taken off. Who was dispatched: Joe Swan Time of dispatch: 5:51PM 2016-11-23 - 18010 - Simon Fernandez-checked a/c unit for proper operation, and reinstalled panel - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-22 | 214015 | RACC-114595 | Both air filters for heating/cooling system NEED to be changed. 4NKBNNJ | NA | Both air filters for heating/cooling system NEED to be changed. 4NKBNNJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-22 | 233168 | POLY-115031 | There is a leakage of water at the hallway and the tiles at the hallway are broken. 4NDBINI | NA | There is a leakage of water at the hallway and the tiles at the hallway are broken. 4NDBINI NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-23 | 46733 | TMPE-203424 | SWO: repair 154-EXF-06713, which has a bad bearing and is not operational. This was found during a preventive maintenance visit. Please sen this estimate to Bonny Kopp: bonita.kopp@asu.edu EST-154899 | 2016-12-02 - 18160 - Gail Jackson-Found bearings and motor burned out, removed. A 10 ft step ladder is required. Trip to warehouse for belt, motor and sheave. Ehx Fan in men restrooms sounds like it about ready to call it quits also, units run 24/7, no need for this, waist of energy and equipment. - Gail Jackson; 2016-12-05 - 18160 - Gail Jackson-Trip to Brg, Belt and Chain to pickup bearings. Assemble unit at shop. Soccer field install parts. - Gail Jackson; 2016-12-05 - 18160 - Carl Karr-Trip to Brg, Belt and Chain to pickup bearings. Assemble unit at shop. Soccer field install parts. - Gail Jackson; 2016-12-05 - 18160 - Gail Jackson-finished INSTALLING BLOWER ASSEMBLY, belt, motor and pulleys. RUN TEST, COMPLETE. - Gail Jackson; 2016-12-05 - 18160 - Carl Karr-finished INSTALLING BLOWER ASSEMBLY, belt, motor, RE WIRE and pulleys. RUN TEST, COMPLETE. - Gail Jackson | SWO: repair 154-EXF-06713, which has a bad bearing and is not operational. This was found during a preventive maintenance visit. Please sen this estimate to Bonny Kopp: bonita.kopp@asu.edu EST-154899 2016-12-02 - 18160 - Gail Jackson-Found bearings and motor burned out, removed. A 10 ft step ladder is required. Trip to warehouse for belt, motor and sheave. Ehx Fan in men restrooms sounds like it about ready to call it quits also, units run 24/7, no need for this, waist of energy and equipment. - Gail Jackson; 2016-12-05 - 18160 - Gail Jackson-Trip to Brg, Belt and Chain to pickup bearings. Assemble unit at shop. Soccer field install parts. - Gail Jackson; 2016-12-05 - 18160 - Carl Karr-Trip to Brg, Belt and Chain to pickup bearings. Assemble unit at shop. Soccer field install parts. - Gail Jackson; 2016-12-05 - 18160 - Gail Jackson-finished INSTALLING BLOWER ASSEMBLY, belt, motor and pulleys. RUN TEST, COMPLETE. - Gail Jackson; 2016-12-05 - 18160 - Carl Karr-finished INSTALLING BLOWER ASSEMBLY, belt, motor, RE WIRE and pulleys. RUN TEST, COMPLETE. - Gail Jackson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2016-11-23 | 48103 | TMPE-202054 | chemical feed system for cooling tower needs repair | 2017-02-06 - 18110 - Kenneth Kamptner-met with a john h. vendor.. control unit doesn't need repair...needs total replacement .. don't think any decision is soon..close tick. for now.. - Kenneth Kamptner | chemical feed system for cooling tower needs repair 2017-02-06 - 18110 - Kenneth Kamptner-met with a john h. vendor.. control unit doesn't need repair...needs total replacement .. don't think any decision is soon..close tick. for now.. - Kenneth Kamptner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
2016-11-23 | 48123 | TMPE-202034 | MWO ECF F103 2 out of the 3 exhaust fans are out. Number 2 and 3. Please respond urgently, thank you. | 2016-11-30 - 18160 - Thomas Gibble-changed one fuss in ex-fan #2 and #3. re-set both ex-fans - Thomas Gibble; 2016-11-30 - 18160 - Robert Dauscher-changed one fuss in ex-fan #2 and #3. re-set both ex-fans - Thomas Gibble | MWO ECF F103 2 out of the 3 exhaust fans are out. Number 2 and 3. Please respond urgently, thank you. 2016-11-30 - 18160 - Thomas Gibble-changed one fuss in ex-fan #2 and #3. re-set both ex-fans - Thomas Gibble; 2016-11-30 - 18160 - Robert Dauscher-changed one fuss in ex-fan #2 and #3. re-set both ex-fans - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-23 | 48172 | TMPE-201985 | MWO SCOB EQ room 327U3 upon inspection found: AH 6 leaking all over floor for AC shop | 2016-12-09 - 18050 - Roque Garcia-AHU 6 has been patched and needs to be replaced. I sent Steve pics and he was going to have contractor replace the cooling coil. - Roque Garcia | MWO SCOB EQ room 327U3 upon inspection found: AH 6 leaking all over floor for AC shop 2016-12-09 - 18050 - Roque Garcia-AHU 6 has been patched and needs to be replaced. I sent Steve pics and he was going to have contractor replace the cooling coil. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-23 | 173020 | RFMT-135311 | Shelby Prockish 11/23/2016 12:24 - Water is leaking from the air vent, causing the floor to be very wet and smells like mildew. This is the second time this has happened, last time they took too long to clean up and all her clothes smelled like mildew. *please put fan in the room to dry the. . . | 2016-11-23 - 23000 - Rick checked the fan coil unit and room - he did not detect a leak. - Gregory Stetka | Shelby Prockish 11/23/2016 12:24 - Water is leaking from the air vent, causing the floor to be very wet and smells like mildew. This is the second time this has happened, last time they took too long to clean up and all her clothes smelled like mildew. *please put fan in the room to dry the. . . 2016-11-23 - 23000 - Rick checked the fan coil unit and room - he did not detect a leak. - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-23 | 214013 | RACC-114597 | !! There is a smell possibly coming the locked, unoccupied room A in our apartment. Or, it is coming from the apartment next to ours, 4102, and filling our apartment. Or, somehow in the vents in general. We are almost certain it is not the sink, trash, fridge or any other source withing our own . . . | 2016-11-28 - 10010 - empty unit ran water in traps aired room out Frank - Jim Deal | !! There is a smell possibly coming the locked, unoccupied room A in our apartment. Or, it is coming from the apartment next to ours, 4102, and filling our apartment. Or, somehow in the vents in general. We are almost certain it is not the sink, trash, fridge or any other source withing our own . . . 2016-11-28 - 10010 - empty unit ran water in traps aired room out Frank - Jim Deal | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-11-25 | 173001 | RFMT-135330 | !! Need the garbage disposal to be fixed for the sink in the kitchen, as well as one of the bathroom sinks which does not drain completely(left side) Contact Name: Daya Contact Phone Number: 5105855405 Contact Email: 4NOIOL7 | 2016-11-29 - 23000 - Chester Duncan-Cleared vanity sink Inspected disposal. Was able to reset and get lugs turning but unit would not rotate. will need to be replaced. No parts at shop. !!!!!Send this to Tommy's bucket!!!!! - Chester Duncan | !! Need the garbage disposal to be fixed for the sink in the kitchen, as well as one of the bathroom sinks which does not drain completely(left side) Contact Name: Daya Contact Phone Number: 5105855405 Contact Email: 4NOIOL7 2016-11-29 - 23000 - Chester Duncan-Cleared vanity sink Inspected disposal. Was able to reset and get lugs turning but unit would not rotate. will need to be replaced. No parts at shop. !!!!!Send this to Tommy's bucket!!!!! - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-25 | 233116 | POLY-115083 | !! I have an emergency issue with my heating unit as I turned it on today to air it out and now the FAN will not shut off. The heat is continuously running whether the unit is on the ON or OFF position. I don't believe it will be healthy for the heating mechanism to be running non-stop until Monda. . . | NA | !! I have an emergency issue with my heating unit as I turned it on today to air it out and now the FAN will not shut off. The heat is continuously running whether the unit is on the ON or OFF position. I don't believe it will be healthy for the heating mechanism to be running non-stop until Monda. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-26 | 233098 | POLY-115101 | Please call before coming over for maintenance. We have a dog and we'd like to make sure we are home before anyone comes in. We need to replace our fridge. We thought we could make it until we move out in December but it is on it's last leg. It is still keeping things cold, but the condenser o. . . | NA | Please call before coming over for maintenance. We have a dog and we'd like to make sure we are home before anyone comes in. We need to replace our fridge. We thought we could make it until we move out in December but it is on it's last leg. It is still keeping things cold, but the condenser o. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-28 | 46767 | TMPE-203390 | MWO ISTB1 454 !! It is reported, "ISTB1 454 cold room Details: The cold room is typically at 4 Celsius but is currently 14 Celsius. I've been monitoring it throughout the day but it does not seem to be cooling down to its normal temperature." Please inspect and service at the earliest opportunit. . . | 2016-12-05 - 18290 - Duane Rider-Troubleshooting unit - Duane Rider; 2016-12-05 - 18290 - Bruce Feldhusen-recovered refrigerant replaced TXV leaked check unit. recharge refrigerant. - Duane Rider | MWO ISTB1 454 !! It is reported, "ISTB1 454 cold room Details: The cold room is typically at 4 Celsius but is currently 14 Celsius. I've been monitoring it throughout the day but it does not seem to be cooling down to its normal temperature." Please inspect and service at the earliest opportunit. . . 2016-12-05 - 18290 - Duane Rider-Troubleshooting unit - Duane Rider; 2016-12-05 - 18290 - Bruce Feldhusen-recovered refrigerant replaced TXV leaked check unit. recharge refrigerant. - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-28 | 46786 | TMPE-203371 | ERC406: !! Air system is making a loud noise in the room 4O1GM1B | 2017-01-04 - 18010 - Thomas Gibble-changed v-belt on fan coil - Thomas Gibble | ERC406: !! Air system is making a loud noise in the room 4O1GM1B 2017-01-04 - 18010 - Thomas Gibble-changed v-belt on fan coil - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-28 | 46798 | TMPE-203359 | MWO ISTB5 Roof AH #3, Y#3153, has dirty pre-filters and a dirty cooling coil that is causing airflow alarms and not enough airflow to labs. Need pre-filters changed and cooling coil externally cleaned ASAP. Send to HVAC services 42B213C | 2016-12-05 - 18010 - Jennifer Moyer-Replace pre-filters and assess job for coil cleaning. No water available and only small hand held Goodman portable coil cleaner can be used. There is a ladder from one roof to another. Elevator was acting up. No light when you get off elevator before roof access. - Jennifer Moyer; 2016-12-05 - 18010 - Jennifer Moyer-Clean coil. Very dirty, plugged solid in parts. - Jennifer Moyer | MWO ISTB5 Roof AH #3, Y#3153, has dirty pre-filters and a dirty cooling coil that is causing airflow alarms and not enough airflow to labs. Need pre-filters changed and cooling coil externally cleaned ASAP. Send to HVAC services 42B213C 2016-12-05 - 18010 - Jennifer Moyer-Replace pre-filters and assess job for coil cleaning. No water available and only small hand held Goodman portable coil cleaner can be used. There is a ladder from one roof to another. Elevator was acting up. No light when you get off elevator before roof access. - Jennifer Moyer; 2016-12-05 - 18010 - Jennifer Moyer-Clean coil. Very dirty, plugged solid in parts. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-28 | 46897 | TMPE-203260 | !! We need to have the warm air started up in A210C2, A210B1 and A210A. These three rooms within A210 are all connected to the same thermostat, which is physically in A210C2. The thermostat is currently set at 73 degrees with the air handler blowing cold air. All other areas within A210 are fine . . . | 2016-12-09 - 18300 - Roque Garcia-Heaters were not working and the building controls were offline. Also the air compressor for building controls was offline. Found circuit 1 was offline due to grounded motor. Circuit 2 replaced fuse and found the valve for the drain open causing the air compressor not to produce enuff pressure. Derek, Michael, MIT, Oner, Robert and Nick worked to resolve the problems. - Roque Garcia | !! We need to have the warm air started up in A210C2, A210B1 and A210A. These three rooms within A210 are all connected to the same thermostat, which is physically in A210C2. The thermostat is currently set at 73 degrees with the air handler blowing cold air. All other areas within A210 are fine . . . 2016-12-09 - 18300 - Roque Garcia-Heaters were not working and the building controls were offline. Also the air compressor for building controls was offline. Found circuit 1 was offline due to grounded motor. Circuit 2 replaced fuse and found the valve for the drain open causing the air compressor not to produce enuff pressure. Derek, Michael, MIT, Oner, Robert and Nick worked to resolve the problems. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7
2016-11-28 | 46909 | TMPE-203248 | MWO: transfer to HVAC for repair on condensation pump switch. I jumped switch, motor works fine. PSYCHOLOGY NORTH Room Number 103 west door on wall any ? Please call.815-901-6919. This is leaking water on shop floor . Thank you Jeff Armstrong Waterline is dripping water about 8ft from the. . . | 2017-03-06 - 18010 - Jennifer Moyer-Re-submitted hot work permit for approval and purchased supplies for the job. - Jennifer Moyer; 2017-03-22 - 18010 - Jennifer Moyer-Brazed in a copper tee. The A/C unit operates on a negative pressure and requires a tee vent after the drain trap to ensure the condensate drains out of the unit. The negative pressure was pulling up the condensate float and making the pump run all the time without water, which burned up the wire on the pump. With proper drainage now, the pump should run and the water should drain correctly. - Jennifer Moyer | MWO: transfer to HVAC for repair on condensation pump switch. I jumped switch, motor works fine. PSYCHOLOGY NORTH Room Number 103 west door on wall any ? Please call.815-901-6919. This is leaking water on shop floor . Thank you Jeff Armstrong Waterline is dripping water about 8ft from the. . . 2017-03-06 - 18010 - Jennifer Moyer-Re-submitted hot work permit for approval and purchased supplies for the job. - Jennifer Moyer; 2017-03-22 - 18010 - Jennifer Moyer-Brazed in a copper tee. The A/C unit operates on a negative pressure and requires a tee vent after the drain trap to ensure the condensate drains out of the unit. The negative pressure was pulling up the condensate float and making the pump run all the time without water, which burned up the wire on the pump. With proper drainage now, the pump should run and the water should drain correctly. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2016-11-28 | 172843 | RFMT-135488 | The heater in our room isn't working, it just keeps blowing cold air 4O0IMK7 | 2016-11-29 - 18010 - Casey Faultner-Found bad actuator valve and and the heating valve on the first floor was shut by someone else. Fixing those two issues corrected the problem. - Casey Faultner | The heater in our room isn't working, it just keeps blowing cold air 4O0IMK7 2016-11-29 - 18010 - Casey Faultner-Found bad actuator valve and and the heating valve on the first floor was shut by someone else. Fixing those two issues corrected the problem. - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-11-28 | 172845 | RFMT-135486 | Our heater doesn't work, it blows out cold air. Contact Name: Contact Phone Number: 4803345139 Contact Email: 4NOKFBL | 2016-11-29 - 18010 - Gabriel Figueroa-Switched unit to on position and ran for awhile. Temp at vent was 88 degrees and climbing. Unit working good. - Gabriel Figueroa | Our heater doesn't work, it blows out cold air. Contact Name: Contact Phone Number: 4803345139 Contact Email: 4NOKFBL 2016-11-29 - 18010 - Gabriel Figueroa-Switched unit to on position and ran for awhile. Temp at vent was 88 degrees and climbing. Unit working good. - Gabriel Figueroa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-28 | 172848 | RFMT-135483 | The heat from the air conditioner doesn't work in my room. 4NO4J1H | 2016-11-29 - 18010 - Salvatore Marasco Jr-Checked T-stat making sure it is controlling the A/C unit's valves and blower motor, and checked temperature at the A/C unit (66 degrees). Explained to student that calls were made to the Central Plant to change over system from cooling to heating. - Salvatore Marasco Jr | The heat from the air conditioner doesn't work in my room. 4NO4J1H 2016-11-29 - 18010 - Salvatore Marasco Jr-Checked T-stat making sure it is controlling the A/C unit's valves and blower motor, and checked temperature at the A/C unit (66 degrees). Explained to student that calls were made to the Central Plant to change over system from cooling to heating. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-11-28 | 172860 | RFMT-135471 | Install 1 portable heater in Best C 405 | 2016-11-28 - 18010 - Rene Arrieta-install portable heater in room - Rene Arrieta | Install 1 portable heater in Best C 405 2016-11-28 - 18010 - Rene Arrieta-install portable heater in room - Rene Arrieta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-28 | 172862 | RFMT-135469 | Fan coil leak Sonora 205 | 2016-11-29 - 18010 - Simon Fernandez-checked a/c fan coil s.s. braided hose line leaking and at coil,heating side.need part. - Simon Fernandez; 2016-12-15 - 18010 - Simon Fernandez-removed,repaired, and reinstalled fan coil - Simon Fernandez; 2016-12-15 - 18010 - David Cates-assisted HVAC tech. - Simon Fernandez | Fan coil leak Sonora 205 2016-11-29 - 18010 - Simon Fernandez-checked a/c fan coil s.s. braided hose line leaking and at coil,heating side.need part. - Simon Fernandez; 2016-12-15 - 18010 - Simon Fernandez-removed,repaired, and reinstalled fan coil - Simon Fernandez; 2016-12-15 - 18010 - David Cates-assisted HVAC tech. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-28 | 172863 | RFMT-135468 | Fan coil leak Sonora 205 | 2016-11-29 - 18010 - Gabriel Figueroa-Isolated leak, called Stetka and informed him to get Olympus out to room to extract water in room 205 and 105. Also told Stetka the cause of the leak and to have A/C tech repair. Informed Stetka that A/C unit will be out of service for the night and that portable heaters would be needed in room for the night. - Gabriel Figueroa | Fan coil leak Sonora 205 2016-11-29 - 18010 - Gabriel Figueroa-Isolated leak, called Stetka and informed him to get Olympus out to room to extract water in room 205 and 105. Also told Stetka the cause of the leak and to have A/C tech repair. Informed Stetka that A/C unit will be out of service for the night and that portable heaters would be needed in room for the night. - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-11-28 | 213942 | RACC-114668 | Repeat Request. When air conditioner between C and D is put on heat, smell of smoke comes from the air vent and the fire alarm goes off. 4NIL65H | 2016-11-30 - 10010 - cleared both heaters. Johnny - Jim Deal | Repeat Request. When air conditioner between C and D is put on heat, smell of smoke comes from the air vent and the fire alarm goes off. 4NIL65H 2016-11-30 - 10010 - cleared both heaters. Johnny - Jim Deal | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-28 | 213958 | RACC-114652 | Our air conditioner is broken. Every time we turn the heat on to high the air only goes lower. For example, we turned the air conditioner to 85 but instead of it being 85 it is at 68 and is going lower. 4NOFF8D | NA | Our air conditioner is broken. Every time we turn the heat on to high the air only goes lower. For example, we turned the air conditioner to 85 but instead of it being 85 it is at 68 and is going lower. 4NOFF8D NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-11-28 | 3323 | WEST-107926 | Track skylight replacement in the Fletcher library. I spoke with Carl on 11/28/2016 about a schedule. Carl aggreed to get me a schedule as soon as possible. I also spoke with Margaret and informed her of the targeted dates for the work on 11/28. She has no problems with closing the appropriate ar. . . | 2016-12-30 - 10010 - Daniel Tanner-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2016-12-30 - 10010 - Darrel Counts-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2016-12-30 - 10010 - Tim Jowers-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2017-01-03 - 10010 - Daniel Tanner-Replaced all water damaged ceiling tiles, vacuumed the area that was affected, and put new cove base along the wall. - Daniel Tanner | Track skylight replacement in the Fletcher library. I spoke with Carl on 11/28/2016 about a schedule. Carl aggreed to get me a schedule as soon as possible. I also spoke with Margaret and informed her of the targeted dates for the work on 11/28. She has no problems with closing the appropriate ar. . . 2016-12-30 - 10010 - Daniel Tanner-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2016-12-30 - 10010 - Darrel Counts-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2016-12-30 - 10010 - Tim Jowers-Cleaning up from a water leak. Extracting carpets, opening floating floors to air out, drilling holes in the Drywall to get air behind it to dry quicker, removing saturated ceiling tiles, and set up fans and blowers to assist with drying. - Daniel Tanner; 2017-01-03 - 10010 - Daniel Tanner-Replaced all water damaged ceiling tiles, vacuumed the area that was affected, and put new cove base along the wall. - Daniel Tanner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-29 | 46694 | TMPE-203463 | MWO MUSIC WB52U1 The Fan Coil Unit #1, vin #7527 is leaking rapidly. Please come quickly, it is near a transformer. Thank you. | 2016-11-29 - 18090 - Called out to Steve P. - Amanda Thomas; 2016-12-09 - 18090 - Roque Garcia-Found the condensate drain disconnected and causing all the water to develop in the room. Repaired and checked it was working and stop leaking - Roque Garcia | MWO MUSIC WB52U1 The Fan Coil Unit #1, vin #7527 is leaking rapidly. Please come quickly, it is near a transformer. Thank you. 2016-11-29 - 18090 - Called out to Steve P. - Amanda Thomas; 2016-12-09 - 18090 - Roque Garcia-Found the condensate drain disconnected and causing all the water to develop in the room. Repaired and checked it was working and stop leaking - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-29 | 46719 | TMPE-203438 | MWO MUSIC W260 *TRANSFER* ADD EL: Assist HVAC Tech Jennifer Moyer to find and isolate power for unit repair/demo. BT to HVAC The condenser fan was running constantly and the compressor was short cycling. It is now tuned off ORIG REQUEST In the hallway near W260, a plume of smoke came out of the. . . | 2016-11-30 - 15010 - Gary Conover-Traced circuit and labeled unit. - Gary Conover; 2016-11-30 - 15010 - Semeon Haile-Traced circuit and labeled same. - Gary Conover | MWO MUSIC W260 *TRANSFER* ADD EL: Assist HVAC Tech Jennifer Moyer to find and isolate power for unit repair/demo. BT to HVAC The condenser fan was running constantly and the compressor was short cycling. It is now tuned off ORIG REQUEST In the hallway near W260, a plume of smoke came out of the. . . 2016-11-30 - 15010 - Gary Conover-Traced circuit and labeled unit. - Gary Conover; 2016-11-30 - 15010 - Semeon Haile-Traced circuit and labeled same. - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-29 | 172783 | RFMT-135548 | The air filter in A/C unit in the classroom 105 on the roof needs to be replaced. | 2016-12-02 - 18170 - John Romero-Replaced air filter on the roof.. 16 x 25 x 2 - John Romero | The air filter in A/C unit in the classroom 105 on the roof needs to be replaced. 2016-12-02 - 18170 - John Romero-Replaced air filter on the roof.. 16 x 25 x 2 - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-29 | 172784 | RFMT-135547 | !! I either don't know how to work the heat or its broken. I flipped the switch to heat and raised to temperature yet it still blows cool air. 4NHGM38 | 2016-11-29 - 18010 - David Cates-Checked tstat and it wouldn't turn on while set to Auto and no heat was coming out of the vents. Thor checked it out as well, and we replaced the tstat and he had to run a jumper wire from the white to the yellow wires to get the heat to engage. Air was coming out of vents at 86 degrees. Please create a TMA for him to account for his time. - David Cates | !! I either don't know how to work the heat or its broken. I flipped the switch to heat and raised to temperature yet it still blows cool air. 4NHGM38 2016-11-29 - 18010 - David Cates-Checked tstat and it wouldn't turn on while set to Auto and no heat was coming out of the vents. Thor checked it out as well, and we replaced the tstat and he had to run a jumper wire from the white to the yellow wires to get the heat to engage. Air was coming out of vents at 86 degrees. Please create a TMA for him to account for his time. - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-11-29 | 172835 | RFMT-135496 | Air conditioner is bowing out heat 4O018LI | 2016-11-29 - 18010 - Gabriel Figueroa-Switched unit to cool and let it run for 30 minutes. Checked temp and it was at 70 degrees and going down. A/C is working good. - Gabriel Figueroa | Air conditioner is bowing out heat 4O018LI 2016-11-29 - 18010 - Gabriel Figueroa-Switched unit to cool and let it run for 30 minutes. Checked temp and it was at 70 degrees and going down. A/C is working good. - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-29 | 208584 | RAMA-100680 | !! I believe the heater is not working properly I went to turn the a/c on and nothing but cold air comes out of the vents. Also, there is very unpleasant smell that seems to be coming from inside the sink. Can someone come and take a look? Thank you! 4NFA5B3 | NA | !! I believe the heater is not working properly I went to turn the a/c on and nothing but cold air comes out of the vents. Also, there is very unpleasant smell that seems to be coming from inside the sink. Can someone come and take a look? Thank you! 4NFA5B3 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-11-30 | 46401 | TMPE-203756 | MWO PSD Roof !! Please create a WO for Electric shop to determine issue with electric heat on AH#5 on roof. Signal exists to controller but appears every time panel is put together the system shuts down. Door disconnect switch appears to not function properly. Please advise Mike as researchers. . . | 2016-12-01 - 15000 - Gary Conover-Troubleshot AH#5 heating controls. Was unable to locate specific problem. Greg, Building Technical Manager said he would take it from here. - Gary Conover; 2016-12-06 - 15000 - Semeon Haile-Further research done on unit unable to locate exact problem. - Gary Conover; 2016-12-06 - 15000 - Gary Conover-Still attempting to locate exact cause of problem - Gary Conover; 2016-12-20 - 15000 - Gary Conover-Replaced auto cutout switch. - Gary Conover; 2017-01-17 - 15000 - Semeon Haile-troubleshoot and repaired AHU unit heater control system - Semeon Haile | MWO PSD Roof !! Please create a WO for Electric shop to determine issue with electric heat on AH#5 on roof. Signal exists to controller but appears every time panel is put together the system shuts down. Door disconnect switch appears to not function properly. Please advise Mike as researchers. . . 2016-12-01 - 15000 - Gary Conover-Troubleshot AH#5 heating controls. Was unable to locate specific problem. Greg, Building Technical Manager said he would take it from here. - Gary Conover; 2016-12-06 - 15000 - Semeon Haile-Further research done on unit unable to locate exact problem. - Gary Conover; 2016-12-06 - 15000 - Gary Conover-Still attempting to locate exact cause of problem - Gary Conover; 2016-12-20 - 15000 - Gary Conover-Replaced auto cutout switch. - Gary Conover; 2017-01-17 - 15000 - Semeon Haile-troubleshoot and repaired AHU unit heater control system - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-11-30 | 46467 | TMPE-203690 | MWO TOWER Auditorium for Robert Ecabert: This auditorium has no heat | 2016-12-05 - 18300 - Jennifer Moyer-Assist Robert in installing condenser fan. - Jennifer Moyer; 2016-12-13 - 18300 - Robert Ecabert-Installed first new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Oner Munoz-Installed first new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Oner Munoz-Installed second new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Robert Ecabert- Installed second new condenser fan motor. Repaired two leaks in the condenser coil and charged the second stage with 6Lbs 11oz of refrigerant r-22 from refrigerant drum js160216-22. - Robert Ecabert; 2016-12-13 - 18300 - Robert Ecabert-Installed a new v-belt. - Robert Ecabert | MWO TOWER Auditorium for Robert Ecabert: This auditorium has no heat 2016-12-05 - 18300 - Jennifer Moyer-Assist Robert in installing condenser fan. - Jennifer Moyer; 2016-12-13 - 18300 - Robert Ecabert-Installed first new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Oner Munoz-Installed first new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Oner Munoz-Installed second new condenser fan motor. - Robert Ecabert; 2016-12-13 - 18300 - Robert Ecabert- Installed second new condenser fan motor. Repaired two leaks in the condenser coil and charged the second stage with 6Lbs 11oz of refrigerant r-22 from refrigerant drum js160216-22. - Robert Ecabert; 2016-12-13 - 18300 - Robert Ecabert-Installed a new v-belt. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-11-30 | 46472 | TMPE-203685 | MWO INDSA A210A A201, A204, A207, A210, A211 and A212? !! Repeat Request. Please reference Work order number #203260. On Monday, FacMan staff from HVAC turned the thermostat up to 78 degrees to alleviate the cold air. It is no longer helping. The air conditioning is coming out too cold. Plus, t. . . | 2016-12-16 - 18300 - Nicholas Sizow-Found air compressor down. AC shop repaired compressor. - Nicholas Sizow | MWO INDSA A210A A201, A204, A207, A210, A211 and A212? !! Repeat Request. Please reference Work order number #203260. On Monday, FacMan staff from HVAC turned the thermostat up to 78 degrees to alleviate the cold air. It is no longer helping. The air conditioning is coming out too cold. Plus, t. . . 2016-12-16 - 18300 - Nicholas Sizow-Found air compressor down. AC shop repaired compressor. - Nicholas Sizow | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-30 | 172682 | RFMT-135649 | Please repair leaking AC coil house. | 2016-12-16 - 18010 - Thor Millsaps-Repaired leak on heating side of coil. System up and running. No leaks. Used 1 vibration eliminator purchased from United Refrigeration. - Thor Millsaps | Please repair leaking AC coil house. 2016-12-16 - 18010 - Thor Millsaps-Repaired leak on heating side of coil. System up and running. No leaks. Used 1 vibration eliminator purchased from United Refrigeration. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-11-30 | 172713 | RFMT-135618 | HVAC equipment check. | 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | HVAC equipment check. 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-11-30 | 172714 | RFMT-135617 | HVAC equipment check. | 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | HVAC equipment check. 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-11-30 | 172715 | RFMT-135616 | HVAC equipment check. | 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | HVAC equipment check. 2016-12-02 - 18010 - Thor Millsaps-Checked temp split at air handler between return and supply air. System is putting out 100 degree air. Recommend installing air temp sensors in supply ducts at air handler for easier monitoring. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 46207 | TMPE-203950 | SWO: Hayden Library - 4th floor - Room #434 - Refrigerator Refrigerator is leaking again. Margaret T. Schmidt 5-5889 4MNA207 | 2016-12-06 - 18240 - Thomas Gibble-removed ice from freezer section. water was from ice trays. - Thomas Gibble | SWO: Hayden Library - 4th floor - Room #434 - Refrigerator Refrigerator is leaking again. Margaret T. Schmidt 5-5889 4MNA207 2016-12-06 - 18240 - Thomas Gibble-removed ice from freezer section. water was from ice trays. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 46227 | TMPE-203930 | MWO SCOB 327U1 A/H #6 coil leak inside Please see Mark Smith for any additional details. | 2016-12-06 - 18090 - Zhi Yu-Water leak is handle by other AC Tech. this is a duplicate work order. - Zhi Yu; 2016-12-06 - 18090 - Robert Dauscher-Water leak is handle by other AC Tech. this is a duplicate work order. - Zhi Yu | MWO SCOB 327U1 A/H #6 coil leak inside Please see Mark Smith for any additional details. 2016-12-06 - 18090 - Zhi Yu-Water leak is handle by other AC Tech. this is a duplicate work order. - Zhi Yu; 2016-12-06 - 18090 - Robert Dauscher-Water leak is handle by other AC Tech. this is a duplicate work order. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 46240 | TMPE-203917 | Bearings are bad, need replaced | 2016-12-30 - 18050 - Duane Rider-assisted vendor on replacement of bearing - Duane Rider | Bearings are bad, need replaced 2016-12-30 - 18050 - Duane Rider-assisted vendor on replacement of bearing - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 46353 | TMPE-203804 | MWO: WHALL 48 FOR JOSE LOPEZ: Condensate pump not working. | 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-05 - 23100 - Jose Lopez-remove float switches inspect them,adjust float switches,test unit.working normal. - Jose Lopez | MWO: WHALL 48 FOR JOSE LOPEZ: Condensate pump not working. 2016-12-05 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-05 - 23100 - Jose Lopez-remove float switches inspect them,adjust float switches,test unit.working normal. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 46363 | TMPE-203794 | MWO Dixie Gammage 212: The wall thermostat on the NW corner of the room does not have a way to be turned on. The occupants of this shared office would like to be able to turn on the heat. Can someone please be sent out to fix this? Thank you 4O25GF6 | 2016-12-08 - 18300 - Gail Jackson-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Carl Karr-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Zhi Yu-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Gail Jackson-Assembled unit in shop, found motor in cage 1/8 hp 1550 rpm that would work and 7.5 mfd run cap. Bench test unit and take amp draw, OK. Installed in office area, run test. - Gail Jackson; 2016-12-08 - 18300 - Zhi Yu-Assembled unit in shop, found motor in cage 1/8 hp 1550 rpm that would work and 7.5 mfd run cap. Bench test unit and take amp draw, OK. Installed in office area, run test. - Gail Jackson | MWO Dixie Gammage 212: The wall thermostat on the NW corner of the room does not have a way to be turned on. The occupants of this shared office would like to be able to turn on the heat. Can someone please be sent out to fix this? Thank you 4O25GF6 2016-12-08 - 18300 - Gail Jackson-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Carl Karr-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Zhi Yu-Found fan blade cracked, 1975 motor burned out, thermostat off, and no steam in lines. The plumbers worked on steam, trip to ARS Tempe for fan blade, and Carl made adapter plate to mount new motor on obsolete base. - Gail Jackson; 2016-12-08 - 18300 - Gail Jackson-Assembled unit in shop, found motor in cage 1/8 hp 1550 rpm that would work and 7.5 mfd run cap. Bench test unit and take amp draw, OK. Installed in office area, run test. - Gail Jackson; 2016-12-08 - 18300 - Zhi Yu-Assembled unit in shop, found motor in cage 1/8 hp 1550 rpm that would work and 7.5 mfd run cap. Bench test unit and take amp draw, OK. Installed in office area, run test. - Gail Jackson | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-01 | 47213 | TMPE-202944 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47214 | TMPE-202943 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47215 | TMPE-202942 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47216 | TMPE-202941 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47217 | TMPE-202940 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47218 | TMPE-202939 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47219 | TMPE-202938 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47220 | TMPE-202937 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47221 | TMPE-202936 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47222 | TMPE-202935 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47223 | TMPE-202934 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-01 | 47519 | TMPE-202638 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-01 | 172630 | RFMT-135701 | RTU 163C-EXF-01029 serial- 0406G30020, AX62 belt | 2016-12-02 - 18010 - Thor Millsaps-Replaced AX62 indoor blower motor belt. System up and running. - Thor Millsaps | RTU 163C-EXF-01029 serial- 0406G30020, AX62 belt 2016-12-02 - 18010 - Thor Millsaps-Replaced AX62 indoor blower motor belt. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 172637 | RFMT-135694 | RTU 160A-EXF-01017 serial- 3905G30007, diagnose fire damper low volt | 2016-12-02 - 18010 - Thor Millsaps-Found unit not turning on due to open smoke detector relay. Contacted fire techs to fix problem. - Thor Millsaps | RTU 160A-EXF-01017 serial- 3905G30007, diagnose fire damper low volt 2016-12-02 - 18010 - Thor Millsaps-Found unit not turning on due to open smoke detector relay. Contacted fire techs to fix problem. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 172638 | RFMT-135693 | RTU 160A-EXF-01016 serial- 3905G30004, 10/10 mfd dual capacitor, need condenser fan motor | 2016-12-02 - 18010 - Thor Millsaps-Replaced 10/10 mfd dual capacitor for condenser fan motors with 2 single 10 mfd capacitors. - Thor Millsaps | RTU 160A-EXF-01016 serial- 3905G30004, 10/10 mfd dual capacitor, need condenser fan motor 2016-12-02 - 18010 - Thor Millsaps-Replaced 10/10 mfd dual capacitor for condenser fan motors with 2 single 10 mfd capacitors. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-01 | 172639 | RFMT-135692 | RTU 163A-EXF-01016 serial- 0406G30017, AX62 belt, refrigerant leak, need service port | 2016-12-06 - 18010 - Thor Millsaps-Repaired refrigerant leaks on evap coil. Replaced service port on circuit 2 that was leaking refrigerant. Vacuumed system and charged to factory specs with 410A - Thor Millsaps | RTU 163A-EXF-01016 serial- 0406G30017, AX62 belt, refrigerant leak, need service port 2016-12-06 - 18010 - Thor Millsaps-Repaired refrigerant leaks on evap coil. Replaced service port on circuit 2 that was leaking refrigerant. Vacuumed system and charged to factory specs with 410A - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-01 | 172640 | RFMT-135691 | RTU serial- 3905G30003, wire repair on condenser fan motor | 2016-12-02 - 18010 - Thor Millsaps-Repaired wires on condenser fan motor that had been cut by fan blade. System up and running. - Thor Millsaps | RTU serial- 3905G30003, wire repair on condenser fan motor 2016-12-02 - 18010 - Thor Millsaps-Repaired wires on condenser fan motor that had been cut by fan blade. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-01 | 253747 | DTPC-114791 | Air Compressor | 2016-12-23 - 18030 - Keith Griffin-PM air compressor, volt and amp draw, belts, oil, air filter, blow tank - Keith Griffin | Air Compressor 2016-12-23 - 18030 - Keith Griffin-PM air compressor, volt and amp draw, belts, oil, air filter, blow tank - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-01 | 253857 | DTPC-114681 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 253858 | DTPC-114680 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 253859 | DTPC-114679 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 253860 | DTPC-114678 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 253861 | DTPC-114677 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 253862 | DTPC-114676 | Roof | 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | Roof 2016-12-13 - 13120 - Ralph Lemons-Roof has been walked and all vents and storm drains are clean. - Ralph Lemons | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-01 | 3481 | WEST-107768 | Chiller-CH-004 | 2017-02-22 - 18080 - David Valentine-ordered brushes in preparation of punching evap tubes next week. - David Valentine; 2017-03-01 - 18080 - David Valentine-place CH4 out of service, isolated evap, drained. removed end bell. set up good way and commenced punching tubes. - David Valentine; 2017-03-01 - 18080 - Joseph McCormick-Isolated, drained, tagged out, and opened evaporator. Setup goodway machine and started brushing tubes. - Joseph McCormick; 2017-03-02 - 18080 - David Valentine-cleaned up bolts from CH4 evap - David Valentine; 2017-03-02 - 18080 - David Valentine-assist with tube punching on CH4 - David Valentine; 2017-03-02 - 18080 - Joseph McCormick-Continued brushing of tubes in evap. - Joseph McCormick; 2017-03-02 - 18080 - Ronald Chaffee-Brushing evaporator tubes. - Ronald Chaffee; 2017-03-03 - 18080 - David Valentine-assist with ch4 evap tube punching, cable on machine broke, got new one from stock to replace it. mopping floor, - David Valentine; 2017-03-03 - 18080 - Joseph McCormick-Continued to punch tubes.... - Joseph McCormick; 2017-03-03 - 18080 - Donald Miller-Punched evaporator tubes - Donald Miller; 2017-03-04 - 18080 - Randy Randell-brush chiller tubes and clean up mess - Randy Randell; 2017-03-06 - 18080 - Joseph McCormick-Continued to brush tubes in evap. Down to the bottom 3 rows, where the silt / sludge is worst. - Joseph McCormick; 2017-03-06 - 18080 - David Valentine-continue with tube punching, repaired Goodway machine due to cable mishap. (no injuries except someones pride) - David Valentine; 2017-03-07 - 18080 - Kevin Brenden-Punched evap. tubes. CH: 4. - Kevin Brenden; 2017-03-07 - 18080 - Joseph McCormick-Brushed, hosed down and shop-vacced bottom rows of evap. then put away all the equipment and cleaned the area for tube camera tomorrow. - Joseph McCormick; 2017-03-07 - 18080 - Donald Miller-Punched evaporator tubes and cleaned up area afterwards - Donald Miller; 2017-03-08 - 18080 - David Valentine-assist with tube punching, set up WEST for scoping on 3-7-17 - David Valentine; 2017-03-08 - 18080 - Donald Miller-Scrubbed evap tube sheet with clr and started removing loose epoxy coating - Donald Miller; 2017-03-09 - 18080 - Donald Miller-Finished wire brushing evap tube sheet, sanded and prepped sheet for epoxy and added first coat of epoxy - Donald Miller; 2017-03-10 - 18080 - Donald Miller-Applied 2nd coat of epoxy to evap tube sheet. Cleaned evap endbell and cut new gasket for endbell. Used silicone and attached gasket to endbell. - Donald Miller; 2017-03-11 - 18080 - Randy Randell-calen chiller head and make gasket - Randy Randell; 2017-03-13 - 18080 - David Valentine-assist with end bell install, tightened bolts on end bell after springing a leak. trip to Lowes for 3/4"x4.5" nipples for end bell drains and vents. - David Valentine; 2017-03-13 - 18080 - Joseph McCormick-Re-installed evap end bell with new drain and vent nipples. Pressure tested shell with city pressure. Disconnected fill and vent hoses. Re-tightened end bell bolts. Put away tools. Mopped and swept area. - Joseph McCormick; 2017-03-17 - 18080 - Randy Randell-put chiller evap end bell on - Randy Randell; 2017-03-17 - 18080 - David Valentine-start cleanup of cond tube sheet, arranged for WEST to scope tubes next week. - David Valentine; 2017-03-17 - 18080 - David Valentine-cleaned sump, checked pump, placed in operation. - David Valentine; 2017-03-20 - 18080 - David Valentine-after WEST scoped the tubes, started wire wheeling bad epoxy/rust spots. - David Valentine; 2017-03-21 - 18080 - Donald Miller-Used wire grinder, sanded, cleaned with alcohol and applied first coat of epoxy on condenser tube sheet - Donald Miller; 2017-03-22 - 18080 - Donald Miller-Applied 2nd coat of epoxy to condenser tube sheet. Cut new gasket for condenser, Used wire wheel on endbell. Attached new gasket to endbell. - Donald Miller; 2017-03-23 - 18080 - David Valentine-chiller ops. - David Valentine; 2017-03-23 - 18080 - David Valentine-inspect epoxy job on ch4 cond tube sheet, looks good. - David Valentine; 2017-03-23 - 18080 - Donald Miller-Finished prepping chiller 4 for condenser endbell install for friday - Donald Miller; 2017-03-24 - 18080 - Donald Miller-Installed condenser endbell and prepped for filling - Donald Miller; 2017-03-25 - 18080 - Randy Randell-clean chiller condenser head bolts and put head on - Randy Randell; 2017-03-27 - 18080 - Thomas Wienand-REVIEW WORK COMPLETE - Thomas Wienand | Chiller-CH-004 2017-02-22 - 18080 - David Valentine-ordered brushes in preparation of punching evap tubes next week. - David Valentine; 2017-03-01 - 18080 - David Valentine-place CH4 out of service, isolated evap, drained. removed end bell. set up good way and commenced punching tubes. - David Valentine; 2017-03-01 - 18080 - Joseph McCormick-Isolated, drained, tagged out, and opened evaporator. Setup goodway machine and started brushing tubes. - Joseph McCormick; 2017-03-02 - 18080 - David Valentine-cleaned up bolts from CH4 evap - David Valentine; 2017-03-02 - 18080 - David Valentine-assist with tube punching on CH4 - David Valentine; 2017-03-02 - 18080 - Joseph McCormick-Continued brushing of tubes in evap. - Joseph McCormick; 2017-03-02 - 18080 - Ronald Chaffee-Brushing evaporator tubes. - Ronald Chaffee; 2017-03-03 - 18080 - David Valentine-assist with ch4 evap tube punching, cable on machine broke, got new one from stock to replace it. mopping floor, - David Valentine; 2017-03-03 - 18080 - Joseph McCormick-Continued to punch tubes.... - Joseph McCormick; 2017-03-03 - 18080 - Donald Miller-Punched evaporator tubes - Donald Miller; 2017-03-04 - 18080 - Randy Randell-brush chiller tubes and clean up mess - Randy Randell; 2017-03-06 - 18080 - Joseph McCormick-Continued to brush tubes in evap. Down to the bottom 3 rows, where the silt / sludge is worst. - Joseph McCormick; 2017-03-06 - 18080 - David Valentine-continue with tube punching, repaired Goodway machine due to cable mishap. (no injuries except someones pride) - David Valentine; 2017-03-07 - 18080 - Kevin Brenden-Punched evap. tubes. CH: 4. - Kevin Brenden; 2017-03-07 - 18080 - Joseph McCormick-Brushed, hosed down and shop-vacced bottom rows of evap. then put away all the equipment and cleaned the area for tube camera tomorrow. - Joseph McCormick; 2017-03-07 - 18080 - Donald Miller-Punched evaporator tubes and cleaned up area afterwards - Donald Miller; 2017-03-08 - 18080 - David Valentine-assist with tube punching, set up WEST for scoping on 3-7-17 - David Valentine; 2017-03-08 - 18080 - Donald Miller-Scrubbed evap tube sheet with clr and started removing loose epoxy coating - Donald Miller; 2017-03-09 - 18080 - Donald Miller-Finished wire brushing evap tube sheet, sanded and prepped sheet for epoxy and added first coat of epoxy - Donald Miller; 2017-03-10 - 18080 - Donald Miller-Applied 2nd coat of epoxy to evap tube sheet. Cleaned evap endbell and cut new gasket for endbell. Used silicone and attached gasket to endbell. - Donald Miller; 2017-03-11 - 18080 - Randy Randell-calen chiller head and make gasket - Randy Randell; 2017-03-13 - 18080 - David Valentine-assist with end bell install, tightened bolts on end bell after springing a leak. trip to Lowes for 3/4"x4.5" nipples for end bell drains and vents. - David Valentine; 2017-03-13 - 18080 - Joseph McCormick-Re-installed evap end bell with new drain and vent nipples. Pressure tested shell with city pressure. Disconnected fill and vent hoses. Re-tightened end bell bolts. Put away tools. Mopped and swept area. - Joseph McCormick; 2017-03-17 - 18080 - Randy Randell-put chiller evap end bell on - Randy Randell; 2017-03-17 - 18080 - David Valentine-start cleanup of cond tube sheet, arranged for WEST to scope tubes next week. - David Valentine; 2017-03-17 - 18080 - David Valentine-cleaned sump, checked pump, placed in operation. - David Valentine; 2017-03-20 - 18080 - David Valentine-after WEST scoped the tubes, started wire wheeling bad epoxy/rust spots. - David Valentine; 2017-03-21 - 18080 - Donald Miller-Used wire grinder, sanded, cleaned with alcohol and applied first coat of epoxy on condenser tube sheet - Donald Miller; 2017-03-22 - 18080 - Donald Miller-Applied 2nd coat of epoxy to condenser tube sheet. Cut new gasket for condenser, Used wire wheel on endbell. Attached new gasket to endbell. - Donald Miller; 2017-03-23 - 18080 - David Valentine-chiller ops. - David Valentine; 2017-03-23 - 18080 - David Valentine-inspect epoxy job on ch4 cond tube sheet, looks good. - David Valentine; 2017-03-23 - 18080 - Donald Miller-Finished prepping chiller 4 for condenser endbell install for friday - Donald Miller; 2017-03-24 - 18080 - Donald Miller-Installed condenser endbell and prepped for filling - Donald Miller; 2017-03-25 - 18080 - Randy Randell-clean chiller condenser head bolts and put head on - Randy Randell; 2017-03-27 - 18080 - Thomas Wienand-REVIEW WORK COMPLETE - Thomas Wienand | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 6
2016-12-01 | 3482 | WEST-107767 | Chiller-CH-003 | 2017-01-09 - 18080 - Joseph McCormick-There is an orphaned 1-1/2" pipe 10 feet above #14 cond. water pump that is corroded between weld-o-let nipple and brass ball valve. Needs to be removed and plugged. - Joseph McCormick; 2017-01-24 - 18080 - David Valentine-drained condenser and evaporator, removed end bells, started punching condenser tubes. - David Valentine; 2017-01-24 - 18080 - David Valentine-drained condenser and evaporator, removed end bells, started punching condenser tubes. - David Valentine; 2017-01-24 - 18080 - Donald Miller-Assisted in removal of condenser and evaporator endbells. Prepped for brushing chiller tubes. Brushed top half of condenser tubes. Cleaned up area and prepped for tomorrow work - Donald Miller; 2017-01-25 - 18080 - David Valentine-punching tube on evap and cond - David Valentine; 2017-01-25 - 18080 - Joseph McCormick-Brushing evap tubes. - Joseph McCormick; 2017-01-25 - 18080 - Donald Miller-Punched tubes on condenser and evaporator. Cleaned condenser tube sheet and work area - Donald Miller; 2017-01-26 - 18080 - Joseph McCormick-Continued to punch evap tubes. - Joseph McCormick; 2017-01-26 - 18080 - Donald Miller-Punched evap tubes, having to do 4 to 5 passes to get clean. Cleaned work area and prepped for Friday - Donald Miller; 2017-01-27 - 18080 - David Valentine-assist with evap tube punching - David Valentine; 2017-01-27 - 18080 - David Valentine-assist with punching of ch3 evap tubes,clean up, set up WEST for Monday scoping - David Valentine; 2017-01-27 - 18080 - Donald Miller-finished cleaning evap tubes and cleaned up work area - Donald Miller; 2017-01-27 - 18080 - Randy Randell-CLEAN CHILLER TUBES - Randy Randell; 2017-01-31 - 18080 - Kevin Brenden-Cleaned and inspected CHW supply and return. - Kevin Brenden; 2017-01-31 - 18080 - David Valentine-removed reducers on inlet side of evap to clean residue from brushing. - David Valentine; 2017-01-31 - 18080 - Joseph McCormick-Helped to remove piping and open south end bell to clear out black muck. Cleaned black muck. Re-installed piping. Cleaning old silicone off evap endbell. - Joseph McCormick; 2017-02-01 - 18080 - Joseph McCormick-Completed the removal/re-application of old silicone sealant and new silicone sealant on evap end bell. - Joseph McCormick; 2017-02-01 - 18080 - Donald Miller-Used grinder on tube sheet in preparation for epoxy - Donald Miller; 2017-02-02 - 18080 - Donald Miller-Cleaned condenser tube sheet with angle grinder - Donald Miller; 2017-02-07 - 18080 - David Valentine-1st coat of epoxy on cond tube sheet - David Valentine; 2017-02-07 - 18080 - David Valentine-2nd coat of epoxy on cond tube sheet. - David Valentine; 2017-02-08 - 18080 - David Valentine-installed evap end bell, flooded. had a leak on the inlet reducer, managed to get it stopped. evap is ready for chemical flush tomorrow. - David Valentine; 2017-02-09 - 18080 - Joseph McCormick-Closed up #3 condenser. Flowed water. Valves and pumps back in auto. - Joseph McCormick; 2017-02-10 - 18080 - David Valentine-assist WEST with cemical rinse on ch3 evap - David Valentine; 2017-02-10 - 18080 - David Valentine-installed ch3 cond end bell - David Valentine; 2017-02-10 - 18080 - Joseph McCormick-Cleaned up/mopped around recent tube brushing job. - Joseph McCormick | Chiller-CH-003 2017-01-09 - 18080 - Joseph McCormick-There is an orphaned 1-1/2" pipe 10 feet above #14 cond. water pump that is corroded between weld-o-let nipple and brass ball valve. Needs to be removed and plugged. - Joseph McCormick; 2017-01-24 - 18080 - David Valentine-drained condenser and evaporator, removed end bells, started punching condenser tubes. - David Valentine; 2017-01-24 - 18080 - David Valentine-drained condenser and evaporator, removed end bells, started punching condenser tubes. - David Valentine; 2017-01-24 - 18080 - Donald Miller-Assisted in removal of condenser and evaporator endbells. Prepped for brushing chiller tubes. Brushed top half of condenser tubes. Cleaned up area and prepped for tomorrow work - Donald Miller; 2017-01-25 - 18080 - David Valentine-punching tube on evap and cond - David Valentine; 2017-01-25 - 18080 - Joseph McCormick-Brushing evap tubes. - Joseph McCormick; 2017-01-25 - 18080 - Donald Miller-Punched tubes on condenser and evaporator. Cleaned condenser tube sheet and work area - Donald Miller; 2017-01-26 - 18080 - Joseph McCormick-Continued to punch evap tubes. - Joseph McCormick; 2017-01-26 - 18080 - Donald Miller-Punched evap tubes, having to do 4 to 5 passes to get clean. Cleaned work area and prepped for Friday - Donald Miller; 2017-01-27 - 18080 - David Valentine-assist with evap tube punching - David Valentine; 2017-01-27 - 18080 - David Valentine-assist with punching of ch3 evap tubes,clean up, set up WEST for Monday scoping - David Valentine; 2017-01-27 - 18080 - Donald Miller-finished cleaning evap tubes and cleaned up work area - Donald Miller; 2017-01-27 - 18080 - Randy Randell-CLEAN CHILLER TUBES - Randy Randell; 2017-01-31 - 18080 - Kevin Brenden-Cleaned and inspected CHW supply and return. - Kevin Brenden; 2017-01-31 - 18080 - David Valentine-removed reducers on inlet side of evap to clean residue from brushing. - David Valentine; 2017-01-31 - 18080 - Joseph McCormick-Helped to remove piping and open south end bell to clear out black muck. Cleaned black muck. Re-installed piping. Cleaning old silicone off evap endbell. - Joseph McCormick; 2017-02-01 - 18080 - Joseph McCormick-Completed the removal/re-application of old silicone sealant and new silicone sealant on evap end bell. - Joseph McCormick; 2017-02-01 - 18080 - Donald Miller-Used grinder on tube sheet in preparation for epoxy - Donald Miller; 2017-02-02 - 18080 - Donald Miller-Cleaned condenser tube sheet with angle grinder - Donald Miller; 2017-02-07 - 18080 - David Valentine-1st coat of epoxy on cond tube sheet - David Valentine; 2017-02-07 - 18080 - David Valentine-2nd coat of epoxy on cond tube sheet. - David Valentine; 2017-02-08 - 18080 - David Valentine-installed evap end bell, flooded. had a leak on the inlet reducer, managed to get it stopped. evap is ready for chemical flush tomorrow. - David Valentine; 2017-02-09 - 18080 - Joseph McCormick-Closed up #3 condenser. Flowed water. Valves and pumps back in auto. - Joseph McCormick; 2017-02-10 - 18080 - David Valentine-assist WEST with cemical rinse on ch3 evap - David Valentine; 2017-02-10 - 18080 - David Valentine-installed ch3 cond end bell - David Valentine; 2017-02-10 - 18080 - Joseph McCormick-Cleaned up/mopped around recent tube brushing job. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 6
2016-12-01 | 3483 | WEST-107766 | Chiller-CH-002 | 2016-12-02 - 50010 - David Valentine-removed end bells from evaporator and condenser, gathered up tube cleaning equipment. - David Valentine; 2016-12-02 - 50010 - David Valentine-drained condenser and evaporator - David Valentine; 2016-12-05 - 50010 - Donald Miller-Punched condenser tubes and wiped down tube sheet - Donald Miller; 2016-12-07 - 50010 - David Valentine-called WEST to inspect tubes, all look good. cleaned evap and cond tube sheets in preparation of epoxy repairs. - David Valentine; 2016-12-12 - 50010 - David Valentine-vacuumed evap tubes, wire wheeled cond and evap tube sheet(first pass)in prep of epoxy coating. - David Valentine; 2016-12-13 - 50010 - David Valentine-sanded wire brushed areas and feathered out remaining epoxy, laid down first coat of new epoxoy. - David Valentine; 2016-12-14 - 50010 - David Valentine-applied 2nd coat of epoxy on cond and evap tube sheets - David Valentine; 2016-12-30 - 50010 - Donald Miller-Installed evap and cond endbells. Filled evap with water and checked for leaks. - Donald Miller; 2016-12-31 - 50010 - Donald Miller-Flowed water through evap and checked for leaks - none observed. - Donald Miller; 2017-01-03 - 50010 - Joseph McCormick-Helped re-fill tower and test run chiller - Joseph McCormick; 2017-01-03 - 50010 - David Valentine-filled ct2 and flooded condenser. checked for leaks. turned on b&amp;g circ pump and sand filter. also aqua heater. - David Valentine; 2017-01-20 - 50010 - Randy Randell-put on evapator end bell - Randy Randell; 2017-01-23 - 50010 - Randy Randell-MAKE CONDSER GASKET - Randy Randell; 2017-01-30 - 50010 - Joseph McCormick-Helped to prep #2 evap for acid wash first thing in morning. - Joseph McCormick; 2017-01-31 - 50010 - David Valentine-prep ch2 evap for chemical rinse - David Valentine; 2017-01-31 - 50010 - David Valentine-assist WEST with chemical cleaning on evap - David Valentine; 2017-02-02 - 50010 - David Valentine-isolated and drained evap ,removed evap end bell, set up tube punching gear, assist with punching tubes. - David Valentine; 2017-02-02 - 50010 - Joseph McCormick-Set-up and actual mechanical brushing of evap tubes. Nasty black silt has turned to nasty brown stuff after acid wash/rinse by West Chemicals. 10-12 passes per tube with oversize diameter brushes. - Joseph McCormick; 2017-02-02 - 50010 - Donald Miller-Assisted in removal of evap endbell - Donald Miller; 2017-02-03 - 50010 - David Valentine-tube punching ch2 evap support - David Valentine; 2017-02-03 - 50010 - Joseph McCormick-Continued brushing tubes of evap. Brown crud. - Joseph McCormick; 2017-02-03 - 50010 - Randy Randell-work on evapator tubes - Randy Randell; 2017-02-06 - 50010 - Randy Randell-brush evaporator tubes - Randy Randell; 2017-02-06 - 50010 - Joseph McCormick-Continued brushing evap tubes. Avg. 10-12 passes due to brown silt. - Joseph McCormick; 2017-02-07 - 50010 - Kevin Brenden-Punched evap. tubes. - Kevin Brenden; 2017-02-07 - 50010 - David Valentine-evap tube punching support - David Valentine; 2017-02-07 - 50010 - Joseph McCormick-Continued to punch evap tubes. Brown silt makes it take 10-12 passes per tube on average. - Joseph McCormick; 2017-02-07 - 50010 - Donald Miller-Assisted in punching evap tubes - Donald Miller; 2017-02-08 - 50010 - Joseph McCormick-Completed the brushing of evap. Brown silt is out of evap. - Joseph McCormick; 2017-02-08 - 50010 - Donald Miller-Finished punching Evap tubes and cleaned area - Donald Miller; 2017-02-09 - 50010 - Joseph McCormick-Helped to close up evap and cleanup. - Joseph McCormick; 2017-02-09 - 50010 - Donald Miller-Installed Evap Endbell, filled evap and flowed water through evap. Cleaned work area. - Donald Miller; 2017-02-10 - 50010 - Joseph McCormick-Cleaned / mopped around completed tube brushing job. - Joseph McCormick | Chiller-CH-002 2016-12-02 - 50010 - David Valentine-removed end bells from evaporator and condenser, gathered up tube cleaning equipment. - David Valentine; 2016-12-02 - 50010 - David Valentine-drained condenser and evaporator - David Valentine; 2016-12-05 - 50010 - Donald Miller-Punched condenser tubes and wiped down tube sheet - Donald Miller; 2016-12-07 - 50010 - David Valentine-called WEST to inspect tubes, all look good. cleaned evap and cond tube sheets in preparation of epoxy repairs. - David Valentine; 2016-12-12 - 50010 - David Valentine-vacuumed evap tubes, wire wheeled cond and evap tube sheet(first pass)in prep of epoxy coating. - David Valentine; 2016-12-13 - 50010 - David Valentine-sanded wire brushed areas and feathered out remaining epoxy, laid down first coat of new epoxoy. - David Valentine; 2016-12-14 - 50010 - David Valentine-applied 2nd coat of epoxy on cond and evap tube sheets - David Valentine; 2016-12-30 - 50010 - Donald Miller-Installed evap and cond endbells. Filled evap with water and checked for leaks. - Donald Miller; 2016-12-31 - 50010 - Donald Miller-Flowed water through evap and checked for leaks - none observed. - Donald Miller; 2017-01-03 - 50010 - Joseph McCormick-Helped re-fill tower and test run chiller - Joseph McCormick; 2017-01-03 - 50010 - David Valentine-filled ct2 and flooded condenser. checked for leaks. turned on b&amp;g circ pump and sand filter. also aqua heater. - David Valentine; 2017-01-20 - 50010 - Randy Randell-put on evapator end bell - Randy Randell; 2017-01-23 - 50010 - Randy Randell-MAKE CONDSER GASKET - Randy Randell; 2017-01-30 - 50010 - Joseph McCormick-Helped to prep #2 evap for acid wash first thing in morning. - Joseph McCormick; 2017-01-31 - 50010 - David Valentine-prep ch2 evap for chemical rinse - David Valentine; 2017-01-31 - 50010 - David Valentine-assist WEST with chemical cleaning on evap - David Valentine; 2017-02-02 - 50010 - David Valentine-isolated and drained evap ,removed evap end bell, set up tube punching gear, assist with punching tubes. - David Valentine; 2017-02-02 - 50010 - Joseph McCormick-Set-up and actual mechanical brushing of evap tubes. Nasty black silt has turned to nasty brown stuff after acid wash/rinse by West Chemicals. 10-12 passes per tube with oversize diameter brushes. - Joseph McCormick; 2017-02-02 - 50010 - Donald Miller-Assisted in removal of evap endbell - Donald Miller; 2017-02-03 - 50010 - David Valentine-tube punching ch2 evap support - David Valentine; 2017-02-03 - 50010 - Joseph McCormick-Continued brushing tubes of evap. Brown crud. - Joseph McCormick; 2017-02-03 - 50010 - Randy Randell-work on evapator tubes - Randy Randell; 2017-02-06 - 50010 - Randy Randell-brush evaporator tubes - Randy Randell; 2017-02-06 - 50010 - Joseph McCormick-Continued brushing evap tubes. Avg. 10-12 passes due to brown silt. - Joseph McCormick; 2017-02-07 - 50010 - Kevin Brenden-Punched evap. tubes. - Kevin Brenden; 2017-02-07 - 50010 - David Valentine-evap tube punching support - David Valentine; 2017-02-07 - 50010 - Joseph McCormick-Continued to punch evap tubes. Brown silt makes it take 10-12 passes per tube on average. - Joseph McCormick; 2017-02-07 - 50010 - Donald Miller-Assisted in punching evap tubes - Donald Miller; 2017-02-08 - 50010 - Joseph McCormick-Completed the brushing of evap. Brown silt is out of evap. - Joseph McCormick; 2017-02-08 - 50010 - Donald Miller-Finished punching Evap tubes and cleaned area - Donald Miller; 2017-02-09 - 50010 - Joseph McCormick-Helped to close up evap and cleanup. - Joseph McCormick; 2017-02-09 - 50010 - Donald Miller-Installed Evap Endbell, filled evap and flowed water through evap. Cleaned work area. - Donald Miller; 2017-02-10 - 50010 - Joseph McCormick-Cleaned / mopped around completed tube brushing job. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 6
2016-12-02 | 46012 | TMPE-204145 | SWO: MU STARBUCKS The memorial union loading dock walk in freezer for Starbucks! One of the fans in our dock freezer is not working Can we please have someone out to look | 2016-12-18 - 18180 - Robert Dauscher-defrosted unit to free fan blade. approx. 8 inches thick ice buildup. AC-Complete - Robert Dauscher; 2016-12-18 - 18180 - Zhi Yu-defrosted unit to free fan blade. approx. 8 inches thick ice buildup. AC-Complete - Robert Dauscher | SWO: MU STARBUCKS The memorial union loading dock walk in freezer for Starbucks! One of the fans in our dock freezer is not working Can we please have someone out to look 2016-12-18 - 18180 - Robert Dauscher-defrosted unit to free fan blade. approx. 8 inches thick ice buildup. AC-Complete - Robert Dauscher; 2016-12-18 - 18180 - Zhi Yu-defrosted unit to free fan blade. approx. 8 inches thick ice buildup. AC-Complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-02 | 46036 | TMPE-204121 | SWO: !! Replace faulty contact for Photo-cell lighting system, system has been rigged to stay on. Eddie Howell has diagnosed the problem and will make repairs once materials have arrived URGENT: Contact Ron Romo when repairs have been made 480.206.5213 Ronald.Romo@asu.edu 42B9D6L | 2016-12-02 - 15040 - Edward Howell-Traced the issue and removed contactor and sent info to Terry to order the contactor - Edward Howell; 2017-01-23 - 15040 - Robert Kirk-Finished install and connected override. - Edward Howell | SWO: !! Replace faulty contact for Photo-cell lighting system, system has been rigged to stay on. Eddie Howell has diagnosed the problem and will make repairs once materials have arrived URGENT: Contact Ron Romo when repairs have been made 480.206.5213 Ronald.Romo@asu.edu 42B9D6L 2016-12-02 - 15040 - Edward Howell-Traced the issue and removed contactor and sent info to Terry to order the contactor - Edward Howell; 2017-01-23 - 15040 - Robert Kirk-Finished install and connected override. - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-02 | 46089 | TMPE-204068 | MWO LSC 210A Av transfer to EMS-noise appears to be from the mixing box. Contact Carl in sheet metal with any questions. BT transfer to AC: The sound is by the door in the duct. There is a buzzing sound coming from the ceiling in LSC 210A. It seems as though it's coming from the light fixture. . . | 2017-02-16 - 18010 - John Holloway-The noise has not returned - John Holloway | MWO LSC 210A Av transfer to EMS-noise appears to be from the mixing box. Contact Carl in sheet metal with any questions. BT transfer to AC: The sound is by the door in the duct. There is a buzzing sound coming from the ceiling in LSC 210A. It seems as though it's coming from the light fixture. . . 2017-02-16 - 18010 - John Holloway-The noise has not returned - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2016-12-02 | 213760 | RACC-114850 | !! Fridge is leaking everywhere. The issue only appeared once every few weeks but it has become frequent in the past few days. Water has flooded the bottom of the fridge (and freezer? it's a frozen lake up top even though we have no water up there and the ice machine is off) and leaks out onto the f. . . | 2016-12-05 - 10010 - cleared condensate drain thawed evaporator coil. Richard - Jim Deal | !! Fridge is leaking everywhere. The issue only appeared once every few weeks but it has become frequent in the past few days. Water has flooded the bottom of the fridge (and freezer? it's a frozen lake up top even though we have no water up there and the ice machine is off) and leaks out onto the f. . . 2016-12-05 - 10010 - cleared condensate drain thawed evaporator coil. Richard - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-03 | 172449 | RFMT-135882 | !! The condition is not work for a long time, if it for a long time, we will get a bad cold, can you help us to repair it? Thanks Contact Name: Xinyi Yan Contact Phone Number: 5207197987 Contact Email: xyan36@asu.edu 4O1F7B9 | 2016-12-05 - 18300 - John Romero-Checked out unit and everything is working like it should. Had to show student how to work thermostat. - John Romero | !! The condition is not work for a long time, if it for a long time, we will get a bad cold, can you help us to repair it? Thanks Contact Name: Xinyi Yan Contact Phone Number: 5207197987 Contact Email: xyan36@asu.edu 4O1F7B9 2016-12-05 - 18300 - John Romero-Checked out unit and everything is working like it should. Had to show student how to work thermostat. - John Romero | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-04 | 3272 | WEST-107977 | Operable Air Wall Maintenance-Annual | 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-cleared out storage areas and brought lifts into ballroom. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Daniel Tanner-started service on east wall - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-Completed service on east wall. Lubed carriers and tightened hinges. Replaced 6 guide blocks and end pieces of guide track. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Tim Jowers-Serviced west wall. Lubed carrier wheels and tightened hinges. Replaced worn guide blocks. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-Completed service and removed equipment from ballroom. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Robert Gailey-Operated wall, annual service just completed. - Robert Gailey | Operable Air Wall Maintenance-Annual 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-cleared out storage areas and brought lifts into ballroom. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Daniel Tanner-started service on east wall - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-Completed service on east wall. Lubed carriers and tightened hinges. Replaced 6 guide blocks and end pieces of guide track. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Tim Jowers-Serviced west wall. Lubed carrier wheels and tightened hinges. Replaced worn guide blocks. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Darrel Counts-Completed service and removed equipment from ballroom. - Robert Gailey; 2017-01-06 - xPM-AIRWALL-A - Robert Gailey-Operated wall, annual service just completed. - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-12-05 | 45409 | TMPE-204748 | SWO MANZY Dining Hall The exhaust fan is not working, making a weird noise causing smoke to fill the floor. Please come urgently. Thank you! | 2016-12-05 - 18160 - Called out to John Howell - Amanda Thomas; 2016-12-06 - 18160 - customer emailed back on 12/6 that it is still an issue. Contacted John Howell again. - Francesca Fernandez; 2016-12-06 - 18160 - 12/5/2016 1 OT 5pm-6pm Jennifer Moyer - Manzanita Manzanita/replaced belt on exhaust fan - Kerri Perkins [Modified: 2016-12-14 Melanie Lamm]; 2016-12-14 - 18160 - Jennifer Moyer-Installed new belt on correct unit. Many of the equipment (exhaust fans, evaporator cooler, a/c equipment) are in dire need of maintenance, cleaning, and repair. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Installed new belt on correct unit. Many of the equipment (exhaust fans, evaporator cooler, a/c equipment) are in dire need of maintenance, cleaning, and repair. - Jennifer Moyer; 2016-12-14 - 18160 - Jennifer Moyer-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer | SWO MANZY Dining Hall The exhaust fan is not working, making a weird noise causing smoke to fill the floor. Please come urgently. Thank you! 2016-12-05 - 18160 - Called out to John Howell - Amanda Thomas; 2016-12-06 - 18160 - customer emailed back on 12/6 that it is still an issue. Contacted John Howell again. - Francesca Fernandez; 2016-12-06 - 18160 - 12/5/2016 1 OT 5pm-6pm Jennifer Moyer - Manzanita Manzanita/replaced belt on exhaust fan - Kerri Perkins [Modified: 2016-12-14 Melanie Lamm]; 2016-12-14 - 18160 - Jennifer Moyer-Installed new belt on correct unit. Many of the equipment (exhaust fans, evaporator cooler, a/c equipment) are in dire need of maintenance, cleaning, and repair. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Installed new belt on correct unit. Many of the equipment (exhaust fans, evaporator cooler, a/c equipment) are in dire need of maintenance, cleaning, and repair. - Jennifer Moyer; 2016-12-14 - 18160 - Jennifer Moyer-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer; 2016-12-14 - 18160 - Thomas Gibble-Exhaust fan shaft damaged and not turning exhaust fan blower wheel. Suggested replacement. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-05 | 45419 | TMPE-204738 | MWO: USE roof repairs CA shop assign to Crhis also coat over graffiti of roof | 2016-12-06 - 13120 - Christopher Dovales-Applying gray premium coat and made repairs on roof membrane - Christopher Dovales; 2016-12-07 - 13120 - Christopher Dovales-Applied second coat of primer and made more repairs on roof membrane - Christopher Dovales; 2016-12-08 - 13120 - Christopher Dovales-Applied top coat on graffiti and made repairs on roof membrane - Christopher Dovales; 2016-12-09 - 13120 - Christopher Dovales-Applied final coat on graffiti,made repairs on roof membrane and had to make repairs on roof leaks in RM170D caused by PM crew when cleaning out A/C units - Christopher Dovales; 2016-12-12 - 13120 - Christopher Dovales-Made repairs on roof,replaced four stained ceiling tile caused by leak in RM170D leak is repaired - Christopher Dovales; 2016-12-14 - 13120 - Christopher Dovales-Patching cracks on roof membrane,sealing roof jack and pitch pans - Christopher Dovales; 2016-12-15 - 13120 - Christopher Dovales-making repairs on lower roof on south side - Christopher Dovales; 2016-12-16 - 13120 - Christopher Dovales-making repairs on south side roof - Christopher Dovales; 2016-12-21 - 13120 - Christopher Dovales-Repairing cracks and pitch pan on lower roof - Christopher Dovales; 2016-12-22 - 13120 - Christopher Dovales-checked for leaks and cleaned off roof - Christopher Dovales; 2017-02-03 - 13120 - Christopher Dovales-Making repairs on drain,pipe jacks and curb flashing - Christopher Dovales; 2017-02-06 - 13120 - Christopher Dovales-making repairs roof - Christopher Dovales; 2017-02-07 - 13120 - Christopher Dovales-Cleaning off crack sealant on metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-09 - 13120 - Christopher Dovales-Repairs are completed on west side roofs - Christopher Dovales | MWO: USE roof repairs CA shop assign to Crhis also coat over graffiti of roof 2016-12-06 - 13120 - Christopher Dovales-Applying gray premium coat and made repairs on roof membrane - Christopher Dovales; 2016-12-07 - 13120 - Christopher Dovales-Applied second coat of primer and made more repairs on roof membrane - Christopher Dovales; 2016-12-08 - 13120 - Christopher Dovales-Applied top coat on graffiti and made repairs on roof membrane - Christopher Dovales; 2016-12-09 - 13120 - Christopher Dovales-Applied final coat on graffiti,made repairs on roof membrane and had to make repairs on roof leaks in RM170D caused by PM crew when cleaning out A/C units - Christopher Dovales; 2016-12-12 - 13120 - Christopher Dovales-Made repairs on roof,replaced four stained ceiling tile caused by leak in RM170D leak is repaired - Christopher Dovales; 2016-12-14 - 13120 - Christopher Dovales-Patching cracks on roof membrane,sealing roof jack and pitch pans - Christopher Dovales; 2016-12-15 - 13120 - Christopher Dovales-making repairs on lower roof on south side - Christopher Dovales; 2016-12-16 - 13120 - Christopher Dovales-making repairs on south side roof - Christopher Dovales; 2016-12-21 - 13120 - Christopher Dovales-Repairing cracks and pitch pan on lower roof - Christopher Dovales; 2016-12-22 - 13120 - Christopher Dovales-checked for leaks and cleaned off roof - Christopher Dovales; 2017-02-03 - 13120 - Christopher Dovales-Making repairs on drain,pipe jacks and curb flashing - Christopher Dovales; 2017-02-06 - 13120 - Christopher Dovales-making repairs roof - Christopher Dovales; 2017-02-07 - 13120 - Christopher Dovales-Cleaning off crack sealant on metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-08 - 13120 - Christopher Dovales-Cleaning and sealing metal drip edge - Christopher Dovales; 2017-02-09 - 13120 - Christopher Dovales-Repairs are completed on west side roofs - Christopher Dovales | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 45463 | TMPE-204694 | SWO: !! Requesting service from the appropriate FACMAN shop. Please adjust / repair the HVAC system for Irish B. The HVAC system is not properly heating the building. EMS has been out and have adjusted the HVAC controls and valves. We are only getting a 3-5 degree indoor temp. split inside t. . . | 2016-12-08 - 18010 - Zhi Yu-Arrived we check heatexchanger temp @110ded and return @105deg. We flush one room no temperature different. All we can do at mean time. - Zhi Yu; 2016-12-08 - 18010 - Zhi Yu-I Meet Plumbers and Mike Cozens. We flush Irish A,B. temperature increases by little. notice the heatexchanger clog. - Zhi Yu; 2016-12-15 - 18010 - 12/2/2016 2CE 3pm-5pm Oner Munoz -Irish B Worked past shift trying to repair building heat system. - Kerri Perkins | SWO: !! Requesting service from the appropriate FACMAN shop. Please adjust / repair the HVAC system for Irish B. The HVAC system is not properly heating the building. EMS has been out and have adjusted the HVAC controls and valves. We are only getting a 3-5 degree indoor temp. split inside t. . . 2016-12-08 - 18010 - Zhi Yu-Arrived we check heatexchanger temp @110ded and return @105deg. We flush one room no temperature different. All we can do at mean time. - Zhi Yu; 2016-12-08 - 18010 - Zhi Yu-I Meet Plumbers and Mike Cozens. We flush Irish A,B. temperature increases by little. notice the heatexchanger clog. - Zhi Yu; 2016-12-15 - 18010 - 12/2/2016 2CE 3pm-5pm Oner Munoz -Irish B Worked past shift trying to repair building heat system. - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-12-05 | 45478 | TMPE-204679 | MWO ERC 425 !! Repeat Request. I had previously called over the weekend regarding cold air blowing at high velocity from the air conditioning system in my office, and the lack of radiator heat. I received a visit on Saturday evening from Mike, and while the radiator issue was addressed, I was t. . . | 2016-12-05 - 18300 - 12-5-16 Control air compressor work completion delayed. Contractor hopes to have control air restored by tomorrow morning. - Mike Cozens | MWO ERC 425 !! Repeat Request. I had previously called over the weekend regarding cold air blowing at high velocity from the air conditioning system in my office, and the lack of radiator heat. I received a visit on Saturday evening from Mike, and while the radiator issue was addressed, I was t. . . 2016-12-05 - 18300 - 12-5-16 Control air compressor work completion delayed. Contractor hopes to have control air restored by tomorrow morning. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 45479 | TMPE-204678 | MWO ENGRC 485 AC is not working properly. It makes the office cooler than outside. Contact Name: Contact Phone Number: 4807472808 Contact Email: 4NC7GJD | 2016-12-07 - 18300 - Michael Cozens-Reduced cooling - Mike Cozens | MWO ENGRC 485 AC is not working properly. It makes the office cooler than outside. Contact Name: Contact Phone Number: 4807472808 Contact Email: 4NC7GJD 2016-12-07 - 18300 - Michael Cozens-Reduced cooling - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-05 | 45483 | TMPE-204674 | MWO GGMA 301 !! "Gammage 301 is FREEZING!!!! It's bad enough for the healthy among us, but Anne is sick, and it's really not helping her. Is there anybody that can be contacted over her to do something about it?" 42A9MCD | 2016-12-06 - 18300 - Brian Qualls-Pump #2 motor is grounded. Took motor from pump #1 and installed at #2. Aligned motor to pump, check amp draws, all OK. nut and bolted starter connections. 43 psi split across pump. - Brian Qualls | MWO GGMA 301 !! "Gammage 301 is FREEZING!!!! It's bad enough for the healthy among us, but Anne is sick, and it's really not helping her. Is there anybody that can be contacted over her to do something about it?" 42A9MCD 2016-12-06 - 18300 - Brian Qualls-Pump #2 motor is grounded. Took motor from pump #1 and installed at #2. Aligned motor to pump, check amp draws, all OK. nut and bolted starter connections. 43 psi split across pump. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 45510 | TMPE-204647 | MWO PSD D57- D62 There is a chiller malfunctioning due to a pressurized regulator going bad. Please replace asap, this has an impact on lab activity. If you need me, I am in office D13. Thank you! | 2016-12-12 - 18080 - Zhi Yu-We Stop by on the 12/08/16 parts not arrived. - Zhi Yu; 2016-12-12 - 18080 - Zhi Yu-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu; 2016-12-12 - 18080 - Robert Dauscher-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu; 2016-12-12 - 18080 - Zhi Yu-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu | MWO PSD D57- D62 There is a chiller malfunctioning due to a pressurized regulator going bad. Please replace asap, this has an impact on lab activity. If you need me, I am in office D13. Thank you! 2016-12-12 - 18080 - Zhi Yu-We Stop by on the 12/08/16 parts not arrived. - Zhi Yu; 2016-12-12 - 18080 - Zhi Yu-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu; 2016-12-12 - 18080 - Robert Dauscher-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu; 2016-12-12 - 18080 - Zhi Yu-We when back on 12/9/16 the pump was installed by their technician. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 45516 | TMPE-204641 | MWO: Thermostat cover is falling off, needs to be fixed. Contact Name: Emily Patterson Contact Phone Number: 480-965-8917 Contact Email: Emily.M.Patterson@asu.edu Attachment(s) 4NGM9CB | 2017-02-06 - 18010 - Roque Garcia-Remounted the tstat and checked good - Roque Garcia | MWO: Thermostat cover is falling off, needs to be fixed. Contact Name: Emily Patterson Contact Phone Number: 480-965-8917 Contact Email: Emily.M.Patterson@asu.edu Attachment(s) 4NGM9CB 2017-02-06 - 18010 - Roque Garcia-Remounted the tstat and checked good - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-05 | 45595 | TMPE-204562 | SPECIAL FUNDING: ASU Life Sciences Bld D AHU Repair. Pueblo Proposal #:16-11-048. Disconnect power to equipment. Lock out & tag out. Demo existing blower wheels, shaft & bearings as requested over the weekend; Schedule Sunbelt Rental to provide and install (8) fans to pressurize air handler in ord. . . | NA | SPECIAL FUNDING: ASU Life Sciences Bld D AHU Repair. Pueblo Proposal #:16-11-048. Disconnect power to equipment. Lock out & tag out. Demo existing blower wheels, shaft & bearings as requested over the weekend; Schedule Sunbelt Rental to provide and install (8) fans to pressurize air handler in ord. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-12-05 | 45599 | TMPE-204558 | MWO: LL 46U1 The pump in the Eq Rm is leaking. There's about 5 gallons of water on the floor. | 2016-12-05 - 23100 - CALLED TO STEVE P. - Monica Moraga; 2017-02-16 - 23100 - Derek Gittings-replacing bearings and seals. - Derek Gittings; 2017-02-22 - 23100 - Derek Gittings-replacing seals and bearings,bead blasting end bells. - Derek Gittings; 2017-02-23 - 23100 - Derek Gittings-had to replace seal,it had cracked.clean pump - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-replacing bearings ,seals gaskets - Derek Gittings; 2017-03-09 - 23100 - Michael Kelley-replacing bearings ,seals gaskets - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-replacing seals and bearings. - Derek Gittings; 2017-03-10 - 23100 - Derek Gittings-replacing bearings,seals and gasskits - Derek Gittings; 2017-03-28 - 23100 - Zhi Yu-alined motor. - Derek Gittings; 2017-03-28 - 23100 - Derek Gittings-alined motor. - Derek Gittings | MWO: LL 46U1 The pump in the Eq Rm is leaking. There's about 5 gallons of water on the floor. 2016-12-05 - 23100 - CALLED TO STEVE P. - Monica Moraga; 2017-02-16 - 23100 - Derek Gittings-replacing bearings and seals. - Derek Gittings; 2017-02-22 - 23100 - Derek Gittings-replacing seals and bearings,bead blasting end bells. - Derek Gittings; 2017-02-23 - 23100 - Derek Gittings-had to replace seal,it had cracked.clean pump - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-replacing bearings ,seals gaskets - Derek Gittings; 2017-03-09 - 23100 - Michael Kelley-replacing bearings ,seals gaskets - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-replacing seals and bearings. - Derek Gittings; 2017-03-10 - 23100 - Derek Gittings-replacing bearings,seals and gasskits - Derek Gittings; 2017-03-28 - 23100 - Zhi Yu-alined motor. - Derek Gittings; 2017-03-28 - 23100 - Derek Gittings-alined motor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-05 | 45600 | TMPE-204557 | MWO: ERC 123 The belt on the air handler seems to be slipping. There's a constant squealing noise. | 2016-12-15 - 18010 - Zhi Yu-We diagnose the belts is slipping and sheave worn out. Need to be replace - Zhi Yu; 2017-01-12 - 18010 - Zhi Yu-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu; 2017-01-12 - 18010 - Zhi Yu-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu; 2017-01-12 - 18010 - Jennifer Moyer-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu | MWO: ERC 123 The belt on the air handler seems to be slipping. There's a constant squealing noise. 2016-12-15 - 18010 - Zhi Yu-We diagnose the belts is slipping and sheave worn out. Need to be replace - Zhi Yu; 2017-01-12 - 18010 - Zhi Yu-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu; 2017-01-12 - 18010 - Zhi Yu-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu; 2017-01-12 - 18010 - Jennifer Moyer-Replaced new 2 sheave and belts. align sheave and belt tensioner. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-05 | 45619 | TMPE-204538 | High temperature alarm came in because DX cooling AC unit is not cooling. Send to HVAC services for checkout and repair ASAP. 42B213C | 2016-12-08 - 18010 - Zhi Yu-Arrived the t/sat setting on heating. we switch back to cooling and check pressure and adjust the set point. - Zhi Yu; 2016-12-08 - 18010 - Gail Jackson-Arrived the t/sat setting on heating. we switch back to cooling and check pressure and adjust the set point. - Zhi Yu | High temperature alarm came in because DX cooling AC unit is not cooling. Send to HVAC services for checkout and repair ASAP. 42B213C 2016-12-08 - 18010 - Zhi Yu-Arrived the t/sat setting on heating. we switch back to cooling and check pressure and adjust the set point. - Zhi Yu; 2016-12-08 - 18010 - Gail Jackson-Arrived the t/sat setting on heating. we switch back to cooling and check pressure and adjust the set point. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 45634 | TMPE-204523 | ASUHD-Agent: Connie Brown Description: bldg is very cold Who was dispatched: Mike Cozens Time of dispatch":9:07a Cindy Luna 12/03/2016 09:26 - Mike Cozens called to have HVAC dispatched to check why no heat is coming from the pumps. 9:25am - Dispatched Robert Dauscher @ 480-689-0362 ASUHD-A. . . | 2016-12-18 - 18300 - Robert Dauscher-Emergency call from Call center. Found both large units on East end of building locked out on a safety. UNABLE TO DETERMINE CAUSE OF FAILURE DUE TO SHOP NOT HAVING PROPER TOOL TO READ ERROR MESSAGE CONTAINED IN CONTROL BOARD. *SHOP NEEDS TO PURCHASE TOOL* Power cycled both units. Both units started working properly afterwards - Robert Dauscher | ASUHD-Agent: Connie Brown Description: bldg is very cold Who was dispatched: Mike Cozens Time of dispatch":9:07a Cindy Luna 12/03/2016 09:26 - Mike Cozens called to have HVAC dispatched to check why no heat is coming from the pumps. 9:25am - Dispatched Robert Dauscher @ 480-689-0362 ASUHD-A. . . 2016-12-18 - 18300 - Robert Dauscher-Emergency call from Call center. Found both large units on East end of building locked out on a safety. UNABLE TO DETERMINE CAUSE OF FAILURE DUE TO SHOP NOT HAVING PROPER TOOL TO READ ERROR MESSAGE CONTAINED IN CONTROL BOARD. *SHOP NEEDS TO PURCHASE TOOL* Power cycled both units. Both units started working properly afterwards - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-12-05 | 172323 | RFMT-136008 | !! The A/C unit has not been working like it used to. The thermostat stays at 60 but the entire dorm is very warm and muggy. Also our air filter is very old and dirty, it needs to be replaced. 4NJ75KI | 2016-12-06 - 18010 - Thomas Zambrano-AIR CONDITIONING IS OFF FOR THE WINTER, building only had heat. - Thomas Zambrano | !! The A/C unit has not been working like it used to. The thermostat stays at 60 but the entire dorm is very warm and muggy. Also our air filter is very old and dirty, it needs to be replaced. 4NJ75KI 2016-12-06 - 18010 - Thomas Zambrano-AIR CONDITIONING IS OFF FOR THE WINTER, building only had heat. - Thomas Zambrano | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 172341 | RFMT-135990 | HVAC air handler filter change: 18 @ 20 x 20 x 2 pleated type. | 2016-12-12 - 18010 - Eric Miller-Changed out filters in Best C. - Eric Miller | HVAC air handler filter change: 18 @ 20 x 20 x 2 pleated type. 2016-12-12 - 18010 - Eric Miller-Changed out filters in Best C. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 172471 | RFMT-135860 | Check room fan coil supply and return air temps in common room locations on the first and second levels. | 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 7 degrees and 15 degrees. - Salvatore Marasco Jr | Check room fan coil supply and return air temps in common room locations on the first and second levels. 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 7 degrees and 15 degrees. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 172472 | RFMT-135859 | Check room fan coil supply and return air temps in common room locations on the first and second levels. | 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 3 degrees and 5 degrees. - Salvatore Marasco Jr [Modified: 2016-12-05 Salvatore Marasco Jr]; 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 3 degrees and 5 degrees. - Salvatore Marasco Jr | Check room fan coil supply and return air temps in common room locations on the first and second levels. 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 3 degrees and 5 degrees. - Salvatore Marasco Jr [Modified: 2016-12-05 Salvatore Marasco Jr]; 2016-12-05 - 18010 - Salvatore Marasco Jr-Checked fan coil units in common areas (kitchen, laundry, and rest room) and one empty dorm room, finding split temps. between 3 degrees and 5 degrees. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 24177 | TMPE-225980 | Shop Reconfiguration: HVAC Shop | 2017-03-20 - 18010 - William Zimmer-Layout cut and weld together table top - Francesca Fernandez; 2017-03-20 - 18010 - William Zimmer-Install wall anchors to support table top and install top. - Francesca Fernandez; 2017-04-03 - 18010 - Carl Karr-Fabricate ductwork. - Carl Karr; 2017-04-03 - 18010 - Carl Karr-Fabricate and install ductwork. - Carl Karr; 2017-04-04 - 18010 - Carl Karr-Fabricate and install duct. - Carl Karr; 2017-04-05 - 18010 - Carl Karr-Fabricate and install duct. - Carl Karr; 2017-04-07 - 18010 - Carl Karr-install and seal duct. - Carl Karr; 2017-04-10 - 18010 - Carl Karr-Fabricate duct,pick up material. - Carl Karr; 2017-04-10 - 18010 - Gail Jackson-pick up material. - Carl Karr; 2017-04-12 - 18010 - Carl Karr-Install duct work. - Carl Karr; 2017-04-12 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-17 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-20 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-24 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-26 - 18010 - Carl Karr-Install exhaust duct. Pick up material. - Carl Karr; 2017-04-26 - 18010 - Robert Ecabert-Install exhaust duct. Pick up material. - Carl Karr; 2017-04-26 - 18010 - Carl Karr-Install duct and supply and return grills. - Carl Karr; 2017-04-27 - 18010 - Carl Karr-Install supply duct and exhaust duct. - Carl Karr; 2017-05-02 - 18010 - Carl Karr-Fabricate filter rack. - Carl Karr; 2017-05-03 - 18010 - Carl Karr-Fabricate return plenum. - Carl Karr; 2017-05-05 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-08 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-10 - 18010 - Carl Karr-Install unistruit. - Carl Karr; 2017-05-11 - 18010 - Gail Jackson-Fabricate and install four inch sleeves. - Carl Karr; 2017-05-16 - 18010 - Carl Karr-Fabricate duct work - Carl Karr; 2017-05-17 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-18 - 18010 - William Zimmer-Make bracket for hose. - William Zimmer | Shop Reconfiguration: HVAC Shop 2017-03-20 - 18010 - William Zimmer-Layout cut and weld together table top - Francesca Fernandez; 2017-03-20 - 18010 - William Zimmer-Install wall anchors to support table top and install top. - Francesca Fernandez; 2017-04-03 - 18010 - Carl Karr-Fabricate ductwork. - Carl Karr; 2017-04-03 - 18010 - Carl Karr-Fabricate and install ductwork. - Carl Karr; 2017-04-04 - 18010 - Carl Karr-Fabricate and install duct. - Carl Karr; 2017-04-05 - 18010 - Carl Karr-Fabricate and install duct. - Carl Karr; 2017-04-07 - 18010 - Carl Karr-install and seal duct. - Carl Karr; 2017-04-10 - 18010 - Carl Karr-Fabricate duct,pick up material. - Carl Karr; 2017-04-10 - 18010 - Gail Jackson-pick up material. - Carl Karr; 2017-04-12 - 18010 - Carl Karr-Install duct work. - Carl Karr; 2017-04-12 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-17 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-20 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-24 - 18010 - Carl Karr-Install exhaust duct. - Carl Karr; 2017-04-26 - 18010 - Carl Karr-Install exhaust duct. Pick up material. - Carl Karr; 2017-04-26 - 18010 - Robert Ecabert-Install exhaust duct. Pick up material. - Carl Karr; 2017-04-26 - 18010 - Carl Karr-Install duct and supply and return grills. - Carl Karr; 2017-04-27 - 18010 - Carl Karr-Install supply duct and exhaust duct. - Carl Karr; 2017-05-02 - 18010 - Carl Karr-Fabricate filter rack. - Carl Karr; 2017-05-03 - 18010 - Carl Karr-Fabricate return plenum. - Carl Karr; 2017-05-05 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-08 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-10 - 18010 - Carl Karr-Install unistruit. - Carl Karr; 2017-05-11 - 18010 - Gail Jackson-Fabricate and install four inch sleeves. - Carl Karr; 2017-05-16 - 18010 - Carl Karr-Fabricate duct work - Carl Karr; 2017-05-17 - 18010 - Carl Karr-Fabricate duct. - Carl Karr; 2017-05-18 - 18010 - William Zimmer-Make bracket for hose. - William Zimmer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-12-05 | 232837 | POLY-115362 | 6830 E Unger. Please check the bathroom Vent System; we are requesting to check to see if the vent system is working properly. We have recently re-caulked the bathroom tub surround because of mold and mildew build up. We just want to make sure that vent systems is working properly. 6830 E. Ung. . . | NA | 6830 E Unger. Please check the bathroom Vent System; we are requesting to check to see if the vent system is working properly. We have recently re-caulked the bathroom tub surround because of mold and mildew build up. We just want to make sure that vent systems is working properly. 6830 E. Ung. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-05 | 232857 | POLY-115342 | STEVE - Please check on this asap. Thanks. !! Our compressed air to the lab is down 42B2GAA | 2016-12-05 - 18030 - Steve Clark-FOUND UPSTAIRS air compressor off on high discharge pressure - reset alarm and unit came on - Steve Clark | STEVE - Please check on this asap. Thanks. !! Our compressed air to the lab is down 42B2GAA 2016-12-05 - 18030 - Steve Clark-FOUND UPSTAIRS air compressor off on high discharge pressure - reset alarm and unit came on - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-05 | 253699 | DTPC-114839 | Make up PM sheets for pumps and A/C units | 2016-12-05 - 10000 - Thomas Klein-Make up PM sheets for pumps and A/C units - Thomas Klein | Make up PM sheets for pumps and A/C units 2016-12-05 - 10000 - Thomas Klein-Make up PM sheets for pumps and A/C units - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-05 | 253709 | DTPC-114829 | AC-L1-09U1 Frozen Up... | 2016-12-05 - 18010 - Ross Hossack-Found thermostat set for 45 degrees and line set and coil frozen up.I shut off the condenser, removed what ice I could from line set, removed cover from unit and just left the fan on to de ice the coil.Cleaned up ice and water on the floor. Placed a fan in the room to dry floor. Checked on unit throughout the day.I will check it tomorrow to see if all the ice has melted. - Ross Hossack; 2016-12-06 - 18010 - Ross Hossack-Checked unit and evaporator is defrosted but the condenser still has ice on it.I reassembled the evaporator and left the fan on,I will check unit again tomorrow. - Ross Hossack; 2016-12-08 - 18010 - Ross Hossack-Checked unit and found ice had melted so I turned unit on and checked it out. Unit is now running normally.Ice that formed was because someone had turned down thermostat to 45 degrees. - Ross Hossack | AC-L1-09U1 Frozen Up... 2016-12-05 - 18010 - Ross Hossack-Found thermostat set for 45 degrees and line set and coil frozen up.I shut off the condenser, removed what ice I could from line set, removed cover from unit and just left the fan on to de ice the coil.Cleaned up ice and water on the floor. Placed a fan in the room to dry floor. Checked on unit throughout the day.I will check it tomorrow to see if all the ice has melted. - Ross Hossack; 2016-12-06 - 18010 - Ross Hossack-Checked unit and evaporator is defrosted but the condenser still has ice on it.I reassembled the evaporator and left the fan on,I will check unit again tomorrow. - Ross Hossack; 2016-12-08 - 18010 - Ross Hossack-Checked unit and found ice had melted so I turned unit on and checked it out. Unit is now running normally.Ice that formed was because someone had turned down thermostat to 45 degrees. - Ross Hossack | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-05 | 3231 | WEST-108018 | At 0730, 12-5-16, Kathy Novak called to report the air vent had dropped and the dean was going to have a meeting there later this morning. Further discussion revealed that the vent slits had been opened more than usual, resulting in more air and cooler temp in room. She was told that we will hand. . . | 2016-12-05 - 18010 - Joseph McCormick-Took call. Passed along info to Al and Tony. - Joseph McCormick; 2016-12-08 - 18010 - Alfred Rohe-Replaced vent and found noise is due to high air volume.Will return to make repair. - Alfred Rohe; 2016-12-08 - 18010 - Alfred Rohe-Attempted to rewire speed control for the heating blower and check fire dampers. Will return. - Alfred Rohe; 2016-12-08 - 18010 - Alfred Rohe-Made speed control operate properly and opened fire damper. Adjusted speed control and checked operation of system. - Alfred Rohe; 2016-12-08 - 18010 - Chad T Ball-Assisted with repairs. - Alfred Rohe; 2016-12-08 - 18010 - Anthony Tucson-Made adjustments on front end for proper operation. - Alfred Rohe | At 0730, 12-5-16, Kathy Novak called to report the air vent had dropped and the dean was going to have a meeting there later this morning. Further discussion revealed that the vent slits had been opened more than usual, resulting in more air and cooler temp in room. She was told that we will hand. . . 2016-12-05 - 18010 - Joseph McCormick-Took call. Passed along info to Al and Tony. - Joseph McCormick; 2016-12-08 - 18010 - Alfred Rohe-Replaced vent and found noise is due to high air volume.Will return to make repair. - Alfred Rohe; 2016-12-08 - 18010 - Alfred Rohe-Attempted to rewire speed control for the heating blower and check fire dampers. Will return. - Alfred Rohe; 2016-12-08 - 18010 - Alfred Rohe-Made speed control operate properly and opened fire damper. Adjusted speed control and checked operation of system. - Alfred Rohe; 2016-12-08 - 18010 - Chad T Ball-Assisted with repairs. - Alfred Rohe; 2016-12-08 - 18010 - Anthony Tucson-Made adjustments on front end for proper operation. - Alfred Rohe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-06 | 45209 | TMPE-204948 | SWO LSC 588 !! It is reported that the ice machine in LSC 588 is not working. Please initiate a work order for HVAC to service at their earliest opportunity. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warrant an estimate. Thank you. 42BLHKH | 2016-12-12 - 18210 - Gail Jackson-Found unit badly rusted, water leaks from all seals, loud grinding/squealing noise, the evap bearings, bore and auger wore out. The cost of parts alone would be more than unit is worth. Recommend replace unit, Spoke with Judy about condition of unit. - Gail Jackson; 2016-12-12 - 18210 - Thomas Gibble-Found unit badly rusted, water leaks from all seals, loud grinding/squealing noise, the evap bearings, bore and auger wore out. The cost of parts alone would be more than unit is worth. Recommend replace unit, Spoke with Judy about condition of unit. - Gail Jackson | SWO LSC 588 !! It is reported that the ice machine in LSC 588 is not working. Please initiate a work order for HVAC to service at their earliest opportunity. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warrant an estimate. Thank you. 42BLHKH 2016-12-12 - 18210 - Gail Jackson-Found unit badly rusted, water leaks from all seals, loud grinding/squealing noise, the evap bearings, bore and auger wore out. The cost of parts alone would be more than unit is worth. Recommend replace unit, Spoke with Judy about condition of unit. - Gail Jackson; 2016-12-12 - 18210 - Thomas Gibble-Found unit badly rusted, water leaks from all seals, loud grinding/squealing noise, the evap bearings, bore and auger wore out. The cost of parts alone would be more than unit is worth. Recommend replace unit, Spoke with Judy about condition of unit. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-06 | 45221 | TMPE-204936 | MWO PSF F64 Please service PSF house compressed air. There is currently a large amount of oil and water coming from the compressed air lines in the student shop (PSF-064). Thanks! 4MOHM4A | 2016-12-07 - 18030 - Brian Qualls-Found some moisture in one line. Inspected auto drains at air compressor. Also filters are due for service, ordered coalescing element. - Brian Qualls; 2017-04-12 - 18030 - Brian Qualls-Installed new coalescing filter (Grainger# 6B250) Flushed out chilled water after cooler. It was partially plugged. - Brian Qualls | MWO PSF F64 Please service PSF house compressed air. There is currently a large amount of oil and water coming from the compressed air lines in the student shop (PSF-064). Thanks! 4MOHM4A 2016-12-07 - 18030 - Brian Qualls-Found some moisture in one line. Inspected auto drains at air compressor. Also filters are due for service, ordered coalescing element. - Brian Qualls; 2017-04-12 - 18030 - Brian Qualls-Installed new coalescing filter (Grainger# 6B250) Flushed out chilled water after cooler. It was partially plugged. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-06 | 45244 | TMPE-204913 | chiller not working on drinking fountain | 2016-12-30 - 18080 - Duane Rider-Checked unit, bad cold control - Duane Rider; 2017-03-29 - 18080 - Duane Rider-Replaced cold control - Duane Rider | chiller not working on drinking fountain 2016-12-30 - 18080 - Duane Rider-Checked unit, bad cold control - Duane Rider; 2017-03-29 - 18080 - Duane Rider-Replaced cold control - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 45257 | TMPE-204900 | drinking fountain chiller not working properly | 2016-12-30 - 18080 - Duane Rider-Checked unit, bad cold control - Duane Rider; 2017-01-12 - 18080 - Duane Rider-Replaced cold control - Duane Rider | drinking fountain chiller not working properly 2016-12-30 - 18080 - Duane Rider-Checked unit, bad cold control - Duane Rider; 2017-01-12 - 18080 - Duane Rider-Replaced cold control - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 45329 | TMPE-204828 | MWO: !! Refrigerated air Dryer for control air not working and shows a high temperature alarm. Send to HVAC services for repair ASAP 42B213C | NA | MWO: !! Refrigerated air Dryer for control air not working and shows a high temperature alarm. Send to HVAC services for repair ASAP 42B213C NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 45344 | TMPE-204813 | MWO CNTRPT !! Repeat Request. 2 HVAC units are down and we need them fixed since new occupants are moving in and Certificate of Occupancy is needed. This is an urgent request. Other tickets were sent in previously for the area. Please all me at 480 2207928 42BIGC1 | 2016-12-08 - 18010 - Mitchell Andrews-replaced two blower motor in two different units...motors were in the cage - Mitchell Andrews; 2016-12-08 - 18010 - Jennifer Moyer-replaced two blower motor in two different units...motors were in the cage - Mitchell Andrews; 2016-12-08 - 18010 - Jennifer Moyer-Replaced blower motor. Very difficult to remove. - Jennifer Moyer; 2016-12-08 - 18010 - Thomas Gibble-Replaced blower motor. Very difficult to remove. - Jennifer Moyer | MWO CNTRPT !! Repeat Request. 2 HVAC units are down and we need them fixed since new occupants are moving in and Certificate of Occupancy is needed. This is an urgent request. Other tickets were sent in previously for the area. Please all me at 480 2207928 42BIGC1 2016-12-08 - 18010 - Mitchell Andrews-replaced two blower motor in two different units...motors were in the cage - Mitchell Andrews; 2016-12-08 - 18010 - Jennifer Moyer-replaced two blower motor in two different units...motors were in the cage - Mitchell Andrews; 2016-12-08 - 18010 - Jennifer Moyer-Replaced blower motor. Very difficult to remove. - Jennifer Moyer; 2016-12-08 - 18010 - Thomas Gibble-Replaced blower motor. Very difficult to remove. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-06 | 172239 | RFMT-136092 | !! The air conditioning unit in our apartment is broken and makes our apartment humid/musty Also, the garbage disposal in the sink will not turn on and clogs the sink regularly. Furthermore, the room facing South campus does not have an Ethernet outlet, and we were wondering if it would be possibl. . . | 2016-12-07 - 18010 - Thomas Zambrano-repaired disposal and explained that the air conditioning is no longer on, only heat. I don't know what to do about the Ethernet connection. - Thomas Zambrano | !! The air conditioning unit in our apartment is broken and makes our apartment humid/musty Also, the garbage disposal in the sink will not turn on and clogs the sink regularly. Furthermore, the room facing South campus does not have an Ethernet outlet, and we were wondering if it would be possibl. . . 2016-12-07 - 18010 - Thomas Zambrano-repaired disposal and explained that the air conditioning is no longer on, only heat. I don't know what to do about the Ethernet connection. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-12-06 | 172258 | RFMT-136073 | Please replace air filter in room 18B | 2016-12-07 - 18170 - John Romero-C.A.R - John Romero | Please replace air filter in room 18B 2016-12-07 - 18170 - John Romero-C.A.R - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 172261 | RFMT-136070 | Please replace air filter in room 711 | 2016-12-07 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | Please replace air filter in room 711 2016-12-07 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 172262 | RFMT-136069 | Please replace air filter in room 710 | 2016-12-07 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | Please replace air filter in room 710 2016-12-07 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 172275 | RFMT-136056 | Check AC | 2016-12-06 - 18010 - Thor Millsaps-Checked ac. Is operating in heat and cool. Vacuumed drain pan. Checked for condensate leaks. Found no leaks. Found no abnormal odors. Cleaned evap coil. System up and running. - Thor Millsaps | Check AC 2016-12-06 - 18010 - Thor Millsaps-Checked ac. Is operating in heat and cool. Vacuumed drain pan. Checked for condensate leaks. Found no leaks. Found no abnormal odors. Cleaned evap coil. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-06 | 172277 | RFMT-136054 | Check all the AC units in rooms at Towers | 2016-12-06 - 18010 - Thomas Zambrano-checked air conditioning unit for leaks. heat was turned on today. - Thomas Zambrano | Check all the AC units in rooms at Towers 2016-12-06 - 18010 - Thomas Zambrano-checked air conditioning unit for leaks. heat was turned on today. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 172280 | RFMT-136051 | Check all the AC units in rooms at Towers | 2016-12-06 - 18010 - Rene Arrieta-check a/c for leaks at towers - Rene Arrieta | Check all the AC units in rooms at Towers 2016-12-06 - 18010 - Rene Arrieta-check a/c for leaks at towers - Rene Arrieta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 172281 | RFMT-136050 | Check all the AC units in rooms at Towers | 2016-12-06 - 18010 - Dan Guerra-We checked all A.C. coils for leaks and found none. - Dan Guerra | Check all the AC units in rooms at Towers 2016-12-06 - 18010 - Dan Guerra-We checked all A.C. coils for leaks and found none. - Dan Guerra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-06 | 213647 | RACC-114963 | !! The AC will not turn on when the thermostat is set to cool. In addition, the AC is leaking water onto the floor. 4NO8K70 | NA | !! The AC will not turn on when the thermostat is set to cool. In addition, the AC is leaking water onto the floor. 4NO8K70 NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-06 | 213663 | RACC-114947 | General Apartment Area: Light bulb in light fixture on wall next to AC system burned out (between rooms A and B) Room A: Ceiling fan shakes when on; window does not open all the way; shower drains slowly 4NJE54M | NA | General Apartment Area: Light bulb in light fixture on wall next to AC system burned out (between rooms A and B) Room A: Ceiling fan shakes when on; window does not open all the way; shower drains slowly 4NJE54M NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 232830 | POLY-115369 | For REY - *THIS WAS A CALL OUT TO REY FROM LAST NIGHT* Lights out at stairs on both side of building. Please send this to Rey because I called him out last night to look at this problem. 42B20MM | 2016-12-20 - 15040 - Reynaldo Martinez-12/5 - RAY WAS CALLED OUT ON THIS (3 HOURS MINIMUM OVERTIME). He found the rib relay not working, and ordered a replacement. *Will be gettine an invoice from Arizona electric Supply for $63.66* - Gayle Swenson | For REY - *THIS WAS A CALL OUT TO REY FROM LAST NIGHT* Lights out at stairs on both side of building. Please send this to Rey because I called him out last night to look at this problem. 42B20MM 2016-12-20 - 15040 - Reynaldo Martinez-12/5 - RAY WAS CALLED OUT ON THIS (3 HOURS MINIMUM OVERTIME). He found the rib relay not working, and ordered a replacement. *Will be gettine an invoice from Arizona electric Supply for $63.66* - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-06 | 253688 | DTPC-114850 | Request to have one of our guys take a look at the office doors 255 and 265 that lead out to the patio. The department in that area is saying that water leaks into those offices when it rains and they want to see if the doors can be resealed. Jeffrey A. Davis | 2016-12-22 - 13070 - Ralph Lemons-Looked at doors and there is construction going on in the rooms. Once construction is completed I will put new felt on the doors. They already have the kick panel guards that are in good condition. - Ralph Lemons; 2016-12-29 - 13070 - Ralph Lemons-Looked at the sweeps and felt in the doors of both suites. The concrete on the outside of the doors is sloping wrong direction. Email has been sent to Jolyn in regards to the problem. - Ralph Lemons | Request to have one of our guys take a look at the office doors 255 and 265 that lead out to the patio. The department in that area is saying that water leaks into those offices when it rains and they want to see if the doors can be resealed. Jeffrey A. Davis 2016-12-22 - 13070 - Ralph Lemons-Looked at doors and there is construction going on in the rooms. Once construction is completed I will put new felt on the doors. They already have the kick panel guards that are in good condition. - Ralph Lemons; 2016-12-29 - 13070 - Ralph Lemons-Looked at the sweeps and felt in the doors of both suites. The concrete on the outside of the doors is sloping wrong direction. Email has been sent to Jolyn in regards to the problem. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-07 | 45020 | TMPE-205137 | MWO: Remove portable 30HP Ingersoll/Rand air compressor and bring to shop. PM unit and return to a central location on campus. This is a temporary machine on casters that is used in emergencies. | 2017-04-04 - 18030 - Michael Kelley-moved to shop. Had problems with casters on unit. Needed to get boom truck to move to shop. - Michael Kelley; 2017-04-04 - 18030 - Derek Gittings-moved to shop. Had problems with casters on unit. Needed to get boom truck to move to shop. - Michael Kelley | MWO: Remove portable 30HP Ingersoll/Rand air compressor and bring to shop. PM unit and return to a central location on campus. This is a temporary machine on casters that is used in emergencies. 2017-04-04 - 18030 - Michael Kelley-moved to shop. Had problems with casters on unit. Needed to get boom truck to move to shop. - Michael Kelley; 2017-04-04 - 18030 - Derek Gittings-moved to shop. Had problems with casters on unit. Needed to get boom truck to move to shop. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-07 | 45084 | TMPE-205073 | re-circ pump is running but is not circulating hot water | 2016-12-12 - 23100 - Zhi Yu-We located the recir. pump above the east entrance. We test the CHW @ 91deg. We run the water for 15 min water temp still @ 91 deg. We removed the recir. pump and tested good. - Zhi Yu; 2016-12-12 - 23100 - Robert Dauscher-We located the recir. pump above the east entrance. We test the CHW @ 91deg. We run the water for 15 min water temp still @ 91 deg. We removed the recir. pump and tested good. - Zhi Yu | re-circ pump is running but is not circulating hot water 2016-12-12 - 23100 - Zhi Yu-We located the recir. pump above the east entrance. We test the CHW @ 91deg. We run the water for 15 min water temp still @ 91 deg. We removed the recir. pump and tested good. - Zhi Yu; 2016-12-12 - 23100 - Robert Dauscher-We located the recir. pump above the east entrance. We test the CHW @ 91deg. We run the water for 15 min water temp still @ 91 deg. We removed the recir. pump and tested good. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-07 | 45118 | TMPE-205039 | Dehumidifer motor is bad, needs replaced | 2016-12-22 - 18140 - Duane Rider-Replaced motor and run cap on blower motor - Duane Rider | Dehumidifer motor is bad, needs replaced 2016-12-22 - 18140 - Duane Rider-Replaced motor and run cap on blower motor - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-07 | 45168 | TMPE-204989 | Repeat Request of WO 200828. The Ice Machine is still out of service. Please see Judy Swartz !! It is reported, "LSA L1-73 (basement); back left corner after you walk through the door Details: The ice machine in this room is not producing ice. The machine is running, but it's not at the correct t. . . | 2016-12-12 - 18210 - Gail Jackson-Found condenser fan not running, gave spin; took off, replaced condenser fan motor and blade. Run test. Trip to ARS tempe for parts. - Gail Jackson; 2016-12-12 - 18210 - Thomas Gibble-Found condenser fan not running, gave spin; took off, replaced condenser fan motor and blade. Run test. Trip to ARS tempe for parts. - Gail Jackson; 2016-12-16 - 18210 - Gail Jackson-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson; 2016-12-16 - 18210 - Gail Jackson-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson; 2016-12-16 - 18210 - Thomas Gibble-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson | Repeat Request of WO 200828. The Ice Machine is still out of service. Please see Judy Swartz !! It is reported, "LSA L1-73 (basement); back left corner after you walk through the door Details: The ice machine in this room is not producing ice. The machine is running, but it's not at the correct t. . . 2016-12-12 - 18210 - Gail Jackson-Found condenser fan not running, gave spin; took off, replaced condenser fan motor and blade. Run test. Trip to ARS tempe for parts. - Gail Jackson; 2016-12-12 - 18210 - Thomas Gibble-Found condenser fan not running, gave spin; took off, replaced condenser fan motor and blade. Run test. Trip to ARS tempe for parts. - Gail Jackson; 2016-12-16 - 18210 - Gail Jackson-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson; 2016-12-16 - 18210 - Gail Jackson-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson; 2016-12-16 - 18210 - Thomas Gibble-Follow up on unit found bin full of ice but compressor still running. Found contactor fried. Replaced contactor, trip to ARS for part, Checked warehouse; did not have. Installed and run test COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-12-07 | 172156 | RFMT-136175 | Inspect air handler in rm. T207 for possible condensate leak per Mike G. work log request. | 2016-12-07 - 18010 - Thor Millsaps-Inspected air handler, no traces of condensation moisture in pan or drain line. Unit functioning properly in heating mode. - Thor Millsaps | Inspect air handler in rm. T207 for possible condensate leak per Mike G. work log request. 2016-12-07 - 18010 - Thor Millsaps-Inspected air handler, no traces of condensation moisture in pan or drain line. Unit functioning properly in heating mode. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-07 | 172175 | RFMT-136156 | Check fan coil supply air and return temps.in common rooms. | 2016-12-07 - 18010 - Eric Miller-Checked Kitchen 71/69 B106 68/64 and B206 72/68 - Eric Miller | Check fan coil supply air and return temps.in common rooms. 2016-12-07 - 18010 - Eric Miller-Checked Kitchen 71/69 B106 68/64 and B206 72/68 - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-07 | 172209 | RFMT-136122 | !! Repeat Request. The air conditioner does not turn on anymore when we want to put it cooler. The dorm is very warm and muggy. Also, we asked for a new air filter because we do not have one and it was not replaced. 4NJ75KI | 2016-12-09 - 18010 - Thomas Zambrano-already explained to one student about how the building is cooled/heated. HEAT IS ON, NO AIR CONDITION. INTALLED AIR FILTER. - Thomas Zambrano | !! Repeat Request. The air conditioner does not turn on anymore when we want to put it cooler. The dorm is very warm and muggy. Also, we asked for a new air filter because we do not have one and it was not replaced. 4NJ75KI 2016-12-09 - 18010 - Thomas Zambrano-already explained to one student about how the building is cooled/heated. HEAT IS ON, NO AIR CONDITION. INTALLED AIR FILTER. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-07 | 232797 | POLY-115402 | The air blow from the vent is not warm enough. Need technicians to check. Running almost all night and noisy. Thanks. 4NHK4F3 | NA | The air blow from the vent is not warm enough. Need technicians to check. Running almost all night and noisy. Thanks. 4NHK4F3 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-08 | 44899 | TMPE-205258 | SPECIAL FUNDING: Best C L1 EQ- CHWS valve seized, and not operational. | NA | SPECIAL FUNDING: Best C L1 EQ- CHWS valve seized, and not operational. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2016-12-08 | 44999 | TMPE-205158 | MWO: BAC L1-18 AHU-3 ID 8189 install hasps on hatches inside filter banks and locks assign to AC Mike Kelley | 2017-01-11 - 18010 - Michael Kelley-Checked out job with Steve and John. Need to install Hasp and locks - Michael Kelley; 2017-03-01 - 18010 - Michael Kelley-job completed someone screwed the doors shut. - Michael Kelley | MWO: BAC L1-18 AHU-3 ID 8189 install hasps on hatches inside filter banks and locks assign to AC Mike Kelley 2017-01-11 - 18010 - Michael Kelley-Checked out job with Steve and John. Need to install Hasp and locks - Michael Kelley; 2017-03-01 - 18010 - Michael Kelley-job completed someone screwed the doors shut. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-12-08 | 45000 | TMPE-205157 | MWO: Not enough cooling from fan coil #3 to adequately cool room. Need cooling coil acid cleaned internally to increase cooling capability. Send to HVAC services. HVAC to coordinate with EMS. For more info call Mike Cozens 480-330-3235 42B213C | 2017-02-23 - 18090 - This coil will be cleaned after the humidifier is repaired. This coil and the portable A/C in the room just barely keep up with the heat load of the room. The humidifier leaks steam into the room. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer-Installed portable A/C - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer - Replaced filters and cleaned coil with foam evaporator cleaner. This unit is difficult to access. There is equipment directly under the access panel and there is duct work on the other side. There is critical research equipment in this room. - Jennifer Moyer [Modified: 2017-05-11 Jennifer Moyer] | MWO: Not enough cooling from fan coil #3 to adequately cool room. Need cooling coil acid cleaned internally to increase cooling capability. Send to HVAC services. HVAC to coordinate with EMS. For more info call Mike Cozens 480-330-3235 42B213C 2017-02-23 - 18090 - This coil will be cleaned after the humidifier is repaired. This coil and the portable A/C in the room just barely keep up with the heat load of the room. The humidifier leaks steam into the room. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer-Installed portable A/C - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer - Replaced filters and cleaned coil with foam evaporator cleaner. This unit is difficult to access. There is equipment directly under the access panel and there is duct work on the other side. There is critical research equipment in this room. - Jennifer Moyer [Modified: 2017-05-11 Jennifer Moyer] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 7
2016-12-08 | 45649 | TMPE-204508 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45650 | TMPE-204507 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45651 | TMPE-204506 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45652 | TMPE-204505 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45722 | TMPE-204435 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45723 | TMPE-204434 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45724 | TMPE-204433 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45725 | TMPE-204432 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45727 | TMPE-204430 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45728 | TMPE-204429 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45729 | TMPE-204428 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45730 | TMPE-204427 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45731 | TMPE-204426 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-08 | 45740 | TMPE-204417 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-08 | 45741 | TMPE-204416 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-08 | 45742 | TMPE-204415 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-08 | 45954 | TMPE-204203 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-08 | 45955 | TMPE-204202 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-08 | 172094 | RFMT-136237 | RES LIFE / Thor: Please replace condenser fan motor on A/C roof package unit. Tag # 160A-EXF-01016, ser # 3905G30004 | 2016-12-14 - 18010 - Thor Millsaps-Replaced condenser fan motor (closest to controls compartment). Part not in TMA. Motor part # HC39GE471. 1/3 HP, 460 v, 1100 RPM, CW Rotation - Thor Millsaps | RES LIFE / Thor: Please replace condenser fan motor on A/C roof package unit. Tag # 160A-EXF-01016, ser # 3905G30004 2016-12-14 - 18010 - Thor Millsaps-Replaced condenser fan motor (closest to controls compartment). Part not in TMA. Motor part # HC39GE471. 1/3 HP, 460 v, 1100 RPM, CW Rotation - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-09 | 44741 | TMPE-205416 | MWO: Exhause Fan #1 out fuses just replaced about 2 weeks ago. | 2016-12-15 - 18060 - Zhi Yu-We Arrived the C phase fuse blow. We Replaced 10amps fuse to 12amps fuse. Cycle the exhaust. - Zhi Yu | MWO: Exhause Fan #1 out fuses just replaced about 2 weeks ago. 2016-12-15 - 18060 - Zhi Yu-We Arrived the C phase fuse blow. We Replaced 10amps fuse to 12amps fuse. Cycle the exhaust. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-09 | 44743 | TMPE-205414 | MWO: Dear Madam or Sir, Most days I find black particles on my desk. They might be coming from the vent. Could you please inspect the vent and the particles? I would like to know what it is; it may be soot, animal/insect droppings, or something else; and if possible, I would like this stuff not. . . | 2017-01-19 - 18010 - Carl Karr-Fabricate and install filter over grille. - Carl Karr | MWO: Dear Madam or Sir, Most days I find black particles on my desk. They might be coming from the vent. Could you please inspect the vent and the particles? I would like to know what it is; it may be soot, animal/insect droppings, or something else; and if possible, I would like this stuff not. . . 2017-01-19 - 18010 - Carl Karr-Fabricate and install filter over grille. - Carl Karr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-09 | 44760 | TMPE-205397 | SWO: Please change out the filter in the ice machine. Please see Danny for location. Thank you 42ABLNJ | 2016-12-13 - 18170 - Gail Jackson-Found filter broke off in housing, had to remove unit to repair/replace filter. Ran cleaner through machine, emptied bin. Removed and cleaned all parts. - Gail Jackson; 2016-12-13 - 18170 - Thomas Gibble-Found filter broke off in housing, had to remove unit to repair/replace filter. Ran cleaner through machine, emptied bin. Removed and cleaned all parts. - Gail Jackson | SWO: Please change out the filter in the ice machine. Please see Danny for location. Thank you 42ABLNJ 2016-12-13 - 18170 - Gail Jackson-Found filter broke off in housing, had to remove unit to repair/replace filter. Ran cleaner through machine, emptied bin. Removed and cleaned all parts. - Gail Jackson; 2016-12-13 - 18170 - Thomas Gibble-Found filter broke off in housing, had to remove unit to repair/replace filter. Ran cleaner through machine, emptied bin. Removed and cleaned all parts. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-12-09 | 44801 | TMPE-205356 | MWO: !! The transformer is unusually loud on the north side of CAVC under the outdoor stairs. It is distracting to my staff member who has an office down there. Could someone please come over and check it out? 4N47EFI | 2016-12-19 - 15080 - Justin Curcio-Checked on transformer. At this time there isn't any loud noises coming from the equipment. - Justin Curcio; 2017-03-16 - 15080 - Robert Kirk-The source of this humming sound is from the 2 large evaporator cooling fans located in the refrigerator just across the hall from the door of her office,and on other side of wall.Unfortunately there is know way to correct this issue. - Robert Kirk | MWO: !! The transformer is unusually loud on the north side of CAVC under the outdoor stairs. It is distracting to my staff member who has an office down there. Could someone please come over and check it out? 4N47EFI 2016-12-19 - 15080 - Justin Curcio-Checked on transformer. At this time there isn't any loud noises coming from the equipment. - Justin Curcio; 2017-03-16 - 15080 - Robert Kirk-The source of this humming sound is from the 2 large evaporator cooling fans located in the refrigerator just across the hall from the door of her office,and on other side of wall.Unfortunately there is know way to correct this issue. - Robert Kirk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-09 | 44830 | TMPE-205327 | MWO: Please send to mechanical shop Attn : Steve Polumbo We previously had a motor replaced on exhaust fan #16 and the old motor needs replacement bearing installed so that it can be back in reserve . Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A | NA | MWO: Please send to mechanical shop Attn : Steve Polumbo We previously had a motor replaced on exhaust fan #16 and the old motor needs replacement bearing installed so that it can be back in reserve . Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-09 | 150547 | RNLD-100754 | The light bulbs in the kitchen are out (3 of the 4 are out). Also the vent over the stovetop in the kitchen is not working either. Can both of these items be looked into. Thank you. 4NI91HM | 2016-12-13 - 15040 - Ramon Urena-12/13 - Cesar went there, and no motor fan on it, and somebody else put the lights up. - Gayle Swenson | The light bulbs in the kitchen are out (3 of the 4 are out). Also the vent over the stovetop in the kitchen is not working either. Can both of these items be looked into. Thank you. 4NI91HM 2016-12-13 - 15040 - Ramon Urena-12/13 - Cesar went there, and no motor fan on it, and somebody else put the lights up. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-09 | 171934 | RFMT-136397 | The Air conditioner is not working Contact Name: Mir Hasin Contact Phone Number: 4803265738 Contact Email: 4NGGFCC | 2016-12-12 - 18010 - Thomas Zambrano-explained to students that ac is turned off till next summer. - Thomas Zambrano | The Air conditioner is not working Contact Name: Mir Hasin Contact Phone Number: 4803265738 Contact Email: 4NGGFCC 2016-12-12 - 18010 - Thomas Zambrano-explained to students that ac is turned off till next summer. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-09 | 171937 | RFMT-136394 | !! A/C is broken both heat and cooling. It been broken for a couple weeks 4O18IAG | 2016-12-12 - 18010 - Gabriel Figueroa-Checked a/c unit, all is working good. Set on cold and it was dropping below 60 degrees. Same as heat side, so the unit is operating properly - Gabriel Figueroa | !! A/C is broken both heat and cooling. It been broken for a couple weeks 4O18IAG 2016-12-12 - 18010 - Gabriel Figueroa-Checked a/c unit, all is working good. Set on cold and it was dropping below 60 degrees. Same as heat side, so the unit is operating properly - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2016-12-09 | 171967 | RFMT-136364 | Checked roof top dry exhaust hood assembly. | 2016-12-09 - 18010 - Eric Miller-Took pictures of dryer vent for Greg. - Eric Miller | Checked roof top dry exhaust hood assembly. 2016-12-09 - 18010 - Eric Miller-Took pictures of dryer vent for Greg. - Eric Miller | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-09 | 172005 | RFMT-136326 | HVAC Semi-Annual | 2016-12-16 - 50016 - Thor Millsaps-PMed fan coil unit. No problems found. Belt changed 4/16. Next belt change is 4/18. Belt size A48 - Thor Millsaps | HVAC Semi-Annual 2016-12-16 - 50016 - Thor Millsaps-PMed fan coil unit. No problems found. Belt changed 4/16. Next belt change is 4/18. Belt size A48 - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-09 | 172006 | RFMT-136325 | HVAC Semi-Annual | 2016-12-16 - 50016 - Thor Millsaps-PMed fan coil unit. No problems found. Filter clean. - Thor Millsaps | HVAC Semi-Annual 2016-12-16 - 50016 - Thor Millsaps-PMed fan coil unit. No problems found. Filter clean. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-09 | 172015 | RFMT-136316 | RES LIFE /Casey: Wall pak outside of elevator lobby is not blowing heat. Please inspect and repair | 2016-12-13 - 18010 - Casey Faultner-Checked unit for no heat. Replaced Thermostat. - Casey Faultner | RES LIFE /Casey: Wall pak outside of elevator lobby is not blowing heat. Please inspect and repair 2016-12-13 - 18010 - Casey Faultner-Checked unit for no heat. Replaced Thermostat. - Casey Faultner | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-09 | 253616 | DTPC-114922 | AHU-2 in alarm hi static pressure. | 2016-12-09 - 18050 - Thomas Klein-Found temperature sensor was bad made adjustments on EMS so air handler would work until it could be repaired. Called Climatec and they came out and made the repairs. - Thomas Klein | AHU-2 in alarm hi static pressure. 2016-12-09 - 18050 - Thomas Klein-Found temperature sensor was bad made adjustments on EMS so air handler would work until it could be repaired. Called Climatec and they came out and made the repairs. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-11 | 171952 | RFMT-136379 | HVAC check for Monday. Check fan coil temps. at common rooms and vacant room. | 2016-12-12 - 18010 - Eric Miller-Took room temps in various rooms. 68 at the coil 66 at the split. - Eric Miller | HVAC check for Monday. Check fan coil temps. at common rooms and vacant room. 2016-12-12 - 18010 - Eric Miller-Took room temps in various rooms. 68 at the coil 66 at the split. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-11 | 232783 | POLY-115416 | Coils | 2017-02-15 - 18090 - Suresh Nair-SERVICED UNITS - - Steve Clark; 2017-02-15 - 18090 - Esli Arvizo-SERVICED UNITS - - Steve Clark | Coils 2017-02-15 - 18090 - Suresh Nair-SERVICED UNITS - - Steve Clark; 2017-02-15 - 18090 - Esli Arvizo-SERVICED UNITS - - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-12 | 44161 | TMPE-205996 | SWO: MU CATERING KITCHEN Had repair done a couple of weeks ago on small reach in cooler and they replaced the thermostat and has not worked properly since | 2016-12-15 - 18010 - Zhi Yu-This is duplicate work order. I Went over the refrig @38-40 deg. - Zhi Yu | SWO: MU CATERING KITCHEN Had repair done a couple of weeks ago on small reach in cooler and they replaced the thermostat and has not worked properly since 2016-12-15 - 18010 - Zhi Yu-This is duplicate work order. I Went over the refrig @38-40 deg. - Zhi Yu | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-12 | 44162 | TMPE-205995 | SWO: MU CATERING KITCHEN Evap coolers seem to have no water on them blowing hot air | 2017-04-11 - 18100 - Thomas Gibble-adjusted water level and replaced door that was laying on the ground. Replaced bleed off line also. - Thomas Gibble | SWO: MU CATERING KITCHEN Evap coolers seem to have no water on them blowing hot air 2017-04-11 - 18100 - Thomas Gibble-adjusted water level and replaced door that was laying on the ground. Replaced bleed off line also. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-12 | 171849 | RFMT-136482 | Res. Life HVAC Dept.. Roof top Evap. Coolers inspection and pm for winter. Please also insure water supply lines and valves are insulated to protect from freeze. | 2016-12-21 - 18010 - Thor Millsaps-Inspected newly installed evap coolers, stands, electrical boxes and connections. Drained coolers, cleaned bottoms and drain lines. Checked belts. Insulated water lines. Lubricated bearings. High voltage electrical conduit from disconnect going into the units does not have connectors. Conduit is resting on sharp metal. (see attached pics) - Thor Millsaps | Res. Life HVAC Dept.. Roof top Evap. Coolers inspection and pm for winter. Please also insure water supply lines and valves are insulated to protect from freeze. 2016-12-21 - 18010 - Thor Millsaps-Inspected newly installed evap coolers, stands, electrical boxes and connections. Drained coolers, cleaned bottoms and drain lines. Checked belts. Insulated water lines. Lubricated bearings. High voltage electrical conduit from disconnect going into the units does not have connectors. Conduit is resting on sharp metal. (see attached pics) - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-12-12 | 171852 | RFMT-136479 | Res. Life HVAC Dept.. Roof top Evap. Coolers inspection and pm for winter. Please also insure water supply lines and valves are insulated to protect from freeze. | 2016-12-21 - 18010 - Simon Fernandez-checked,winterized and insulated all evaporator coolers - Simon Fernandez | Res. Life HVAC Dept.. Roof top Evap. Coolers inspection and pm for winter. Please also insure water supply lines and valves are insulated to protect from freeze. 2016-12-21 - 18010 - Simon Fernandez-checked,winterized and insulated all evaporator coolers - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-12-12 | 208568 | RAMA-100696 | The air conditioner control's lid popped off. I can't get it back on correctly. Perhaps maitance can get it back on correctly. The lid is on the counter. Attachment(s) 4O10I64 | NA | The air conditioner control's lid popped off. I can't get it back on correctly. Perhaps maitance can get it back on correctly. The lid is on the counter. Attachment(s) 4O10I64 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-12 | 213469 | RACC-115141 | !! 1. We have a recent outbreak of flies. We've cleaned the rooms (except for one and that roommate is gone for most of winter break) and the kitchen, and have killed off quite a few (90+), but we cannot locate the source. 2. Our air conditioning does not work. It simply refuses to cool the room. T. . . | 2016-12-15 - 10010 - replaced thermostat replaced light switch repaired towel bar Aaron - Jim Deal | !! 1. We have a recent outbreak of flies. We've cleaned the rooms (except for one and that roommate is gone for most of winter break) and the kitchen, and have killed off quite a few (90+), but we cannot locate the source. 2. Our air conditioning does not work. It simply refuses to cool the room. T. . . 2016-12-15 - 10010 - replaced thermostat replaced light switch repaired towel bar Aaron - Jim Deal | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-12 | 232785 | POLY-115414 | Coils | 2017-01-17 - 18090 - Suresh Nair-REPLACED AIR FILTERS- CHECKED UNITS - Steve Clark; 2017-01-17 - 18090 - Esli Arvizo-REPLACED AIR FILTERS- CHECKED UNITS - Steve Clark | Coils 2017-01-17 - 18090 - Suresh Nair-REPLACED AIR FILTERS- CHECKED UNITS - Steve Clark; 2017-01-17 - 18090 - Esli Arvizo-REPLACED AIR FILTERS- CHECKED UNITS - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-13 | 43934 | TMPE-206223 | MWO - PSH RM H471 AH#1 Please replace the filters on AH#1 they are extremely dirty and its causing low static pressure on the air handler unit. | 2016-12-13 - 18170 - 12.13.16 Cancel call, filter crew is already working in the building and they will get AH#1 first thing in the morning. Per Brian Q. CSJ - Cheryl St. John | MWO - PSH RM H471 AH#1 Please replace the filters on AH#1 they are extremely dirty and its causing low static pressure on the air handler unit. 2016-12-13 - 18170 - 12.13.16 Cancel call, filter crew is already working in the building and they will get AH#1 first thing in the morning. Per Brian Q. CSJ - Cheryl St. John | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-13 | 43949 | TMPE-206208 | MWO: I know I have put in a few tickets about the temperature in here and sorry if I seem to be a complainer but is it possible to have the vent above me closed off or at least have something place around it so the air blows out rather than down on me? In the summer I was always cold and now that. . . | 2016-12-15 - 18290 - Roque Garcia-Relocated register, tried to locate an air deflector from Grainger, ACE, Ferguson, Norman S. Wright, home depot and was not able to find one. - Roque Garcia | MWO: I know I have put in a few tickets about the temperature in here and sorry if I seem to be a complainer but is it possible to have the vent above me closed off or at least have something place around it so the air blows out rather than down on me? In the summer I was always cold and now that. . . 2016-12-15 - 18290 - Roque Garcia-Relocated register, tried to locate an air deflector from Grainger, ACE, Ferguson, Norman S. Wright, home depot and was not able to find one. - Roque Garcia | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-13 | 43969 | TMPE-206188 | MWO: Air conditioning system is louder than usual. There is a buzzing sound when active. Contact Name: Victoria Fox Contact Phone Number: 4809652966 Contact Email: vicki.fox@asu.edu 4N8I1J3 | 2017-02-17 - 18010 - Mitchell Andrews-replaced the fan motor - Mitchell Andrews | MWO: Air conditioning system is louder than usual. There is a buzzing sound when active. Contact Name: Victoria Fox Contact Phone Number: 4809652966 Contact Email: vicki.fox@asu.edu 4N8I1J3 2017-02-17 - 18010 - Mitchell Andrews-replaced the fan motor - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-13 | 44031 | TMPE-206126 | MWO SHESC room 120U1 pump leaking - found upon monthly inspection REF 202318 | 2016-12-20 - 23100 - Gail Jackson-Search for pump not found. - Gail Jackson; 2016-12-20 - 23100 - Thomas Gibble-Search for pump not found. - Gail Jackson; 2016-12-20 - 23100 - Gail Jackson-Found pump in EQ room 120U1 Anthropology, NOT Armstrong, wrong building/ right campus, condensate pump leaks from seal; tightened bolts on both pumps no leaks. COMPLETE - Gail Jackson; 2016-12-20 - 23100 - Zhi Yu-Found pump in EQ room 120U1 Anthropology, NOT Armstrong, wrong building/ right campus, condensate pump leaks from seal; tightened bolts on both pumps no leaks. COMPLETE - Gail Jackson | MWO SHESC room 120U1 pump leaking - found upon monthly inspection REF 202318 2016-12-20 - 23100 - Gail Jackson-Search for pump not found. - Gail Jackson; 2016-12-20 - 23100 - Thomas Gibble-Search for pump not found. - Gail Jackson; 2016-12-20 - 23100 - Gail Jackson-Found pump in EQ room 120U1 Anthropology, NOT Armstrong, wrong building/ right campus, condensate pump leaks from seal; tightened bolts on both pumps no leaks. COMPLETE - Gail Jackson; 2016-12-20 - 23100 - Zhi Yu-Found pump in EQ room 120U1 Anthropology, NOT Armstrong, wrong building/ right campus, condensate pump leaks from seal; tightened bolts on both pumps no leaks. COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-13 | 150541 | RNLD-100760 | AC remote wont work with system. 4NIL357 | 2016-12-22 - 18010 - Allan Blair-12/16 - Esli and Allan ensured unit heated and cools. Changed remote batteries (Used 2 "AAA" batteries from Century Hall stock) - Gayle Swenson | AC remote wont work with system. 4NIL357 2016-12-22 - 18010 - Allan Blair-12/16 - Esli and Allan ensured unit heated and cools. Changed remote batteries (Used 2 "AAA" batteries from Century Hall stock) - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-13 | 171699 | RFMT-136632 | Tim Smith has requested JCI to check chiller for unusual noise coming from the condensor unit. Please meet with JCI mechanic at site. | 2016-12-14 - 18080 - Simon Fernandez-met with JCI ,donnie could not duplicate noise at this time,said the noise could be from a starved evap and the vanes are reacting and system pressure is the noise we hearing. - Simon Fernandez | Tim Smith has requested JCI to check chiller for unusual noise coming from the condensor unit. Please meet with JCI mechanic at site. 2016-12-14 - 18080 - Simon Fernandez-met with JCI ,donnie could not duplicate noise at this time,said the noise could be from a starved evap and the vanes are reacting and system pressure is the noise we hearing. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-13 | 171711 | RFMT-136620 | HVAC filter change out all bathrooms. | 2016-12-15 - 18010 - Salvatore Marasco Jr-Replaced air filters in all restrooms of Hayden Hall West. - Salvatore Marasco Jr | HVAC filter change out all bathrooms. 2016-12-15 - 18010 - Salvatore Marasco Jr-Replaced air filters in all restrooms of Hayden Hall West. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-13 | 171712 | RFMT-136619 | HVAC filter change out all bathrooms. | 2016-12-16 - 18010 - Salvatore Marasco Jr-Completed bathroom A/C air filter changes in Hayden East. - Salvatore Marasco Jr | HVAC filter change out all bathrooms. 2016-12-16 - 18010 - Salvatore Marasco Jr-Completed bathroom A/C air filter changes in Hayden East. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-13 | 171713 | RFMT-136618 | HVAC filter change out all bathrooms. | 2016-12-14 - 18010 - Salvatore Marasco Jr-Replaced all air filters in bathrooms. - Salvatore Marasco Jr | HVAC filter change out all bathrooms. 2016-12-14 - 18010 - Salvatore Marasco Jr-Replaced all air filters in bathrooms. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-13 | 3170 | WEST-108079 | Air Compressor - Monthly Maintenance | 2016-12-16 - xPM-0100-M - Robert Gailey-checked fluids and tire pressure. operated compressor. - Robert Gailey | Air Compressor - Monthly Maintenance 2016-12-16 - xPM-0100-M - Robert Gailey-checked fluids and tire pressure. operated compressor. - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-14 | 43821 | TMPE-206336 | MWO: ECD 119 The lab air is not working. Please check on this asap. | 2016-12-14 - 18290 - Received a call about low oxygen levels in the room so called out to EMS to expedite the work. AT - Amanda Thomas; 2017-05-11 - 18290 - Roque Garcia-reset compressor - Roque Garcia | MWO: ECD 119 The lab air is not working. Please check on this asap. 2016-12-14 - 18290 - Received a call about low oxygen levels in the room so called out to EMS to expedite the work. AT - Amanda Thomas; 2017-05-11 - 18290 - Roque Garcia-reset compressor - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-14 | 43840 | TMPE-206317 | MWO: !! Please see employee's complaint below. "There are serious issues with the air in the building \\u2013 there is a significant amount of dust which is causing respiratory problems. Others have noticed dust (foggy) in the air, as well as a very strong dusty smell." Can you please send someone. . . | 2016-12-16 - 18010 - Zhi Yu-Arrived Check 4 unit located on the roof. All indoor coil looks very clean and no problem were found. The filter last replaced 6/12/16. We pickup filters from warehouse and replaced them. - Zhi Yu | MWO: !! Please see employee's complaint below. "There are serious issues with the air in the building \\u2013 there is a significant amount of dust which is causing respiratory problems. Others have noticed dust (foggy) in the air, as well as a very strong dusty smell." Can you please send someone. . . 2016-12-16 - 18010 - Zhi Yu-Arrived Check 4 unit located on the roof. All indoor coil looks very clean and no problem were found. The filter last replaced 6/12/16. We pickup filters from warehouse and replaced them. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-14 | 43862 | TMPE-206295 | HVAC to EL Please add electricians to work order# 187591. To assist HVAC mechanic with motor connection. Derek Gittings is the HVAC contact. ORIG REQUEST Pump has a bad vibration. I have created a work order for EL to look at pump 3 VFD so we can change lead/lag | 2016-12-21 - 23100 - Gary Conover-VFD is locked out will need HVAC to remove lock and further explain what they need. Not sure to accomplish task without further inspection. - Gary Conover; 2016-12-21 - 23100 - Gary Conover-VFD is locked out. Will need HVAC to remove lock for further inspection. - Gary Conover; 2017-01-23 - 23100 - Semeon Haile-reprogram VFD, checked rotation chill water pump #4 and back on line - Semeon Haile | HVAC to EL Please add electricians to work order# 187591. To assist HVAC mechanic with motor connection. Derek Gittings is the HVAC contact. ORIG REQUEST Pump has a bad vibration. I have created a work order for EL to look at pump 3 VFD so we can change lead/lag 2016-12-21 - 23100 - Gary Conover-VFD is locked out will need HVAC to remove lock and further explain what they need. Not sure to accomplish task without further inspection. - Gary Conover; 2016-12-21 - 23100 - Gary Conover-VFD is locked out. Will need HVAC to remove lock for further inspection. - Gary Conover; 2017-01-23 - 23100 - Semeon Haile-reprogram VFD, checked rotation chill water pump #4 and back on line - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-12-14 | 171637 | RFMT-136694 | Bathroom fan is not working. 4NNH6KO | 2016-12-15 - 18160 - Mike Guckian-installed new fart fan. - Mike Guckian | Bathroom fan is not working. 4NNH6KO 2016-12-15 - 18160 - Mike Guckian-installed new fart fan. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-14 | 171656 | RFMT-136675 | The air conditioning vent rattles very loudly and It seems something is loose inside it. Contact Name: Contact Phone Number: 7196415633 Contact Email: 4NLFJB2 | 2016-12-19 - 18010 - Russell Peterson- noise in the lounge a/c is coming from loose vent vanes rattling. - Russell Peterson | The air conditioning vent rattles very loudly and It seems something is loose inside it. Contact Name: Contact Phone Number: 7196415633 Contact Email: 4NLFJB2 2016-12-19 - 18010 - Russell Peterson- noise in the lounge a/c is coming from loose vent vanes rattling. - Russell Peterson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-14 | 171831 | RFMT-136500 | The lockbox covering the air conditioning control in this lounge is broken. It is either just not locked or the lock has detached. 4NHENI7 | 2016-12-16 - 11000 - Scott Berndt-re attached lock box - Scott Berndt | The lockbox covering the air conditioning control in this lounge is broken. It is either just not locked or the lock has detached. 4NHENI7 2016-12-16 - 11000 - Scott Berndt-re attached lock box - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2
2016-12-15 | 43606 | TMPE-206551 | ED 201U1 It sounds like the air handler bearings are going out. It's making a clicking noise. | 2016-12-21 - 18050 - Gail Jackson-Called central plant, shut unit down locally. Took belt guard off; found 5 B belts; tension ok. Greased bearings inside and out. Restart unit slight clicking sound from belts this is common on units with 5 belts. Restart A/H, called central plant informed unit back on line. COMPLETE - Gail Jackson | ED 201U1 It sounds like the air handler bearings are going out. It's making a clicking noise. 2016-12-21 - 18050 - Gail Jackson-Called central plant, shut unit down locally. Took belt guard off; found 5 B belts; tension ok. Greased bearings inside and out. Restart unit slight clicking sound from belts this is common on units with 5 belts. Restart A/H, called central plant informed unit back on line. COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 43627 | TMPE-206530 | Repeat Request. Exhaust fan for flammable cabinets is not operating and causing the system alarm to sound, can you send someone to investigate the problem? Thanks, Fred 42AB8AC | 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Gregory Wann-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2017-01-23 - 18160 - Robert Dauscher-Call complete. motor under warranty. new unit. handled by outside contractor - Robert Dauscher | Repeat Request. Exhaust fan for flammable cabinets is not operating and causing the system alarm to sound, can you send someone to investigate the problem? Thanks, Fred 42AB8AC 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Gregory Wann-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2016-12-18 - 18160 - Robert Dauscher-No power at unit had to trace down panel as room number is not listed on fused disconnect. Found unit drawing lock rotor amps. Unit has proper voltage and start cap is in good condition. FAULTY MOTOR Newer looking unit may be under warranty. Not able to verify on weekend. - Robert Dauscher; 2017-01-23 - 18160 - Robert Dauscher-Call complete. motor under warranty. new unit. handled by outside contractor - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2016-12-15 | 43680 | TMPE-206477 | FOR ELECTRIC SHOP. Please remove bad relays in ceiling. See BT for location. 4MO271K | 2016-12-21 - 15040 - Chet Harvey-system seems to be working ok, think the run time of the lights needs to be reset, BT states lamps are burning out rapidly due to the constant on and off, meeting with John B. at 8am on 12/21 to see what can be done to correct this - Chet Harvey; 2016-12-23 - 15040 - Chet Harvey-met with john B. he is going to try and adjust light run time through the candiglo system. - Chet Harvey | FOR ELECTRIC SHOP. Please remove bad relays in ceiling. See BT for location. 4MO271K 2016-12-21 - 15040 - Chet Harvey-system seems to be working ok, think the run time of the lights needs to be reset, BT states lamps are burning out rapidly due to the constant on and off, meeting with John B. at 8am on 12/21 to see what can be done to correct this - Chet Harvey; 2016-12-23 - 15040 - Chet Harvey-met with john B. he is going to try and adjust light run time through the candiglo system. - Chet Harvey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-15 | 43706 | TMPE-206451 | The thermostat on the wall in 101 is taped to the wall so it doesn't fall. Please fix this. Contact Name: Emily Patterson Contact Phone Number: 4809658917 Contact Email: Emily.M.Patterson@asu.edu Attachment(s) 4NGM9CB | 2016-12-18 - 18010 - Robert Dauscher-Found building controls thermostat base broken. T-stat requires Ethernet cable to program. Called in EMS oncall to replace thermostat - AC Complete - Robert Dauscher | The thermostat on the wall in 101 is taped to the wall so it doesn't fall. Please fix this. Contact Name: Emily Patterson Contact Phone Number: 4809658917 Contact Email: Emily.M.Patterson@asu.edu Attachment(s) 4NGM9CB 2016-12-18 - 18010 - Robert Dauscher-Found building controls thermostat base broken. T-stat requires Ethernet cable to program. Called in EMS oncall to replace thermostat - AC Complete - Robert Dauscher | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-12-15 | 43723 | TMPE-206434 | MWO: WFA Please Transfer this work order over to AC as an alarm is going of periodically at this Ejector Pit External to Wells Fargo. Contact Luis Flores or John Scudellari for questions. FOR PLUMBING - On the north side exterior, there's an alarm that's beeping by the panel & disconnect. Not . . . | 2017-01-11 - 18010 - Michael Kelley-checked floats in pit. checked pumps. All were working - Michael Kelley | MWO: WFA Please Transfer this work order over to AC as an alarm is going of periodically at this Ejector Pit External to Wells Fargo. Contact Luis Flores or John Scudellari for questions. FOR PLUMBING - On the north side exterior, there's an alarm that's beeping by the panel & disconnect. Not . . . 2017-01-11 - 18010 - Michael Kelley-checked floats in pit. checked pumps. All were working - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 43742 | TMPE-206415 | !! We are once again having frequent temperature spikes in our lab in ECD 106 and ECD 113. We had one 3 weeks back and again this morning. This morning the temperature became so high that the sputtering system chiller, which was replaced only a few months back, stopped working. We were able to resta. . . | 2016-12-18 - 18290 - Robert Dauscher-found both rooms are controlled by EMS and fed from building air handler. One room does not contain a t-stat of any kind. Contacted EMS oncall to address customer complaint These rooms do not have individual HVAC Systems AC Complete - Robert Dauscher | !! We are once again having frequent temperature spikes in our lab in ECD 106 and ECD 113. We had one 3 weeks back and again this morning. This morning the temperature became so high that the sputtering system chiller, which was replaced only a few months back, stopped working. We were able to resta. . . 2016-12-18 - 18290 - Robert Dauscher-found both rooms are controlled by EMS and fed from building air handler. One room does not contain a t-stat of any kind. Contacted EMS oncall to address customer complaint These rooms do not have individual HVAC Systems AC Complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44233 | TMPE-205924 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44235 | TMPE-205922 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44322 | TMPE-205835 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44323 | TMPE-205834 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44324 | TMPE-205833 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44325 | TMPE-205832 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44326 | TMPE-205831 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44327 | TMPE-205830 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44328 | TMPE-205829 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44329 | TMPE-205828 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44330 | TMPE-205827 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44331 | TMPE-205826 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-15 | 44332 | TMPE-205825 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-16 | 150538 | RNLD-100763 | The room North of trash room area needs to have it air duct repaired. 42B97GA | 2016-12-22 - 17000 - Allan Blair-12/16 - Esli and Allan repaired the broken duct in QS Room #186. (Used 2 Panduit straps at $1.00 each) - Gayle Swenson | The room North of trash room area needs to have it air duct repaired. 42B97GA 2016-12-22 - 17000 - Allan Blair-12/16 - Esli and Allan repaired the broken duct in QS Room #186. (Used 2 Panduit straps at $1.00 each) - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 2
2016-12-16 | 171543 | RFMT-136788 | Running water noise coming from air vent. Please look in to. Thank you! 4NC9826 | 2016-12-16 - 18010 - Eric Miller-The sound is the water going thru the coil, worked both valves. working fine. - Eric Miller | Running water noise coming from air vent. Please look in to. Thank you! 4NC9826 2016-12-16 - 18010 - Eric Miller-The sound is the water going thru the coil, worked both valves. working fine. - Eric Miller | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2016-12-16 | 232566 | POLY-115632 | frozen coil | NA | frozen coil NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-18 | 213406 | RACC-115204 | Our air filter needs replacing, please. Thank you! 4NJ1JGK | 2016-12-20 - 10010 - replace filter Richard - Jim Deal | Our air filter needs replacing, please. Thank you! 4NJ1JGK 2016-12-20 - 10010 - replace filter Richard - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-19 | 41033 | TMPE-209124 | Bad Motor ( locked up ) | NA | Bad Motor ( locked up ) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2016-12-19 | 41042 | TMPE-209115 | unit has bad shaft bearings. | NA | unit has bad shaft bearings. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-19 | 41043 | TMPE-209114 | unit has noisy motor bearings. | 2016-12-29 - 18050 - Gail Jackson-Found blower motor burned out, motor bracket broke, filter dirty, and all 3 coils plugged. Removed motor assembly. - Gail Jackson; 2016-12-29 - 18050 - Thomas Gibble-Found blower motor burned out, motor bracket broke, filter dirty, and all 3 coils plugged. Removed motor assembly. - Gail Jackson; 2016-12-29 - 18050 - Gail Jackson-Replaced 1/3 hp 230v motor with 1 from cage. Trip to warehouse for 7.5 run cap, 3 20x20x1 filters. Trip to ARS Tempe for motor bracket and puller. Installed motor assembly, run cap and filters. Run test. Power washed all 3 fan coil units as coils extremely dirty. Replaced filters; only been installed for 2 months. FILTERS NEED CHANGED MORE THAN EVERY 6 CLOGGED. - Gail Jackson; 2016-12-29 - 18050 - Thomas Gibble-Replaced 1/3 hp 230v motor with 1 from cage. Trip to warehouse for 7.5 run cap, 3 20x20x1 filters. Trip to ARS Tempe for motor bracket and puller. Installed motor assembly, run cap and filters. Run test. Power washed all 3 fan coil units as coils extremely dirty. Replaced filters; only been installed for 2 months. FILTERS NEED CHANGED MORE THAN EVERY 6 CLOGGED. - Gail Jackson | unit has noisy motor bearings. 2016-12-29 - 18050 - Gail Jackson-Found blower motor burned out, motor bracket broke, filter dirty, and all 3 coils plugged. Removed motor assembly. - Gail Jackson; 2016-12-29 - 18050 - Thomas Gibble-Found blower motor burned out, motor bracket broke, filter dirty, and all 3 coils plugged. Removed motor assembly. - Gail Jackson; 2016-12-29 - 18050 - Gail Jackson-Replaced 1/3 hp 230v motor with 1 from cage. Trip to warehouse for 7.5 run cap, 3 20x20x1 filters. Trip to ARS Tempe for motor bracket and puller. Installed motor assembly, run cap and filters. Run test. Power washed all 3 fan coil units as coils extremely dirty. Replaced filters; only been installed for 2 months. FILTERS NEED CHANGED MORE THAN EVERY 6 CLOGGED. - Gail Jackson; 2016-12-29 - 18050 - Thomas Gibble-Replaced 1/3 hp 230v motor with 1 from cage. Trip to warehouse for 7.5 run cap, 3 20x20x1 filters. Trip to ARS Tempe for motor bracket and puller. Installed motor assembly, run cap and filters. Run test. Power washed all 3 fan coil units as coils extremely dirty. Replaced filters; only been installed for 2 months. FILTERS NEED CHANGED MORE THAN EVERY 6 CLOGGED. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7
2016-12-19 | 42997 | TMPE-207160 | !! The heating units are not working RSS! Room 130 42BFO11 | 2016-12-21 - 18300 - 1st call list, goes to HVAC. csj - Cheryl St. John; 2017-01-06 - 18300 - Thomas Gibble-re-set two units.heating is doing good. - Thomas Gibble; 2017-01-06 - 18300 - Gail Jackson-re-set two units.heating is doing good. - Thomas Gibble | !! The heating units are not working RSS! Room 130 42BFO11 2016-12-21 - 18300 - 1st call list, goes to HVAC. csj - Cheryl St. John; 2017-01-06 - 18300 - Thomas Gibble-re-set two units.heating is doing good. - Thomas Gibble; 2017-01-06 - 18300 - Gail Jackson-re-set two units.heating is doing good. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-19 | 171425 | RFMT-136906 | Please inspect M 214's A/C unit. I'm not sure it's cooling properly based on the set temperature and the actual temperature in the room when I went in. Thanks, Carli 4NF4L2O | 2016-12-19 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | Please inspect M 214's A/C unit. I'm not sure it's cooling properly based on the set temperature and the actual temperature in the room when I went in. Thanks, Carli 4NF4L2O 2016-12-19 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-19 | 253343 | DTPC-115195 | Exhaust Fan-Bi-Annual | 2016-12-24 - xPM-2100.02-B - Keith Griffin-PMs Fan is non-operation due to seized motor, parts secured, waiting for P.O. to be approved - Keith Griffin; 2016-12-24 - xPM-2100.02-B - Bruce Pickford-PMs Fan is non-operation due to seized motor, parts secured, waiting for P.O. to be approved - Keith Griffin; 2016-12-28 - xPM-2100.02-B - This is in the old chlorine room. Was porter office. No need for a fan in this location. - Patricia Best | Exhaust Fan-Bi-Annual 2016-12-24 - xPM-2100.02-B - Keith Griffin-PMs Fan is non-operation due to seized motor, parts secured, waiting for P.O. to be approved - Keith Griffin; 2016-12-24 - xPM-2100.02-B - Bruce Pickford-PMs Fan is non-operation due to seized motor, parts secured, waiting for P.O. to be approved - Keith Griffin; 2016-12-28 - xPM-2100.02-B - This is in the old chlorine room. Was porter office. No need for a fan in this location. - Patricia Best | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-19 | 36185 | TMPE-213972 | Request for Estimate. The 253C icemaker machine in ISTB1 has a broken dispenser lever. One of the metal arms has come off of the back metal wall and the thin metal arms are also distorted. I believe it is a Scotsman AFE424 UNDERCOUNTER product. We would appreciate an esetimate of how much it will be. . . | 2017-01-27 - 18210 - Gail Jackson-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-27 - 18210 - Thomas Gibble-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-27 - 18210 - Carl Karr-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-30 - 18210 - Gail Jackson-installed H2O filter. COMPLETE - Gail Jackson | Request for Estimate. The 253C icemaker machine in ISTB1 has a broken dispenser lever. One of the metal arms has come off of the back metal wall and the thin metal arms are also distorted. I believe it is a Scotsman AFE424 UNDERCOUNTER product. We would appreciate an esetimate of how much it will be. . . 2017-01-27 - 18210 - Gail Jackson-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-27 - 18210 - Thomas Gibble-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-27 - 18210 - Carl Karr-Found bin stat prob bracket broke off, removed assembly, and took back to shop for Carl to repair. Replaced both retainers and reinstalled unit, will return with new H2O filter. - Gail Jackson; 2017-01-30 - 18210 - Gail Jackson-installed H2O filter. COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3
2016-12-20 | 40826 | TMPE-209331 | Transferred to HVAC, HP1-12 Calling for cooling and it's 80 deg in space. HVAC to reset the HP. EMS WO#209295, HVAC WO#209331. ASUHC-Agent: Kyle Van Bergen Description: To hot in entire office, server room is reaching unacceptable temperature. Who was dispatched: Time of dispatch: | 2016-12-23 - 18290 - Zhi Yu-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Jennifer Moyer-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Roque Garcia-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Midhat Mukanovic-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Jennifer Moyer-For this unit, diagnostics indicate that it was a possible incorrect charge/restriction, so all refrigerant was removed from this unit and it was weighed in to ensure correctness. The unit had no changes, so it is still back to the water restriction or flow problem. - Jennifer Moyer; 2016-12-23 - 18290 - Zhi Yu-For this unit, diagnostics indicate that it was a possible incorrect charge/restriction, so all refrigerant was removed from this unit and it was weighed in to ensure correctness. The unit had no changes, so it is still back to the water restriction or flow problem. - Jennifer Moyer; 2017-01-03 - 18290 - Jennifer Moyer-call to check on condition of A/C.(any temp alarms) - Jennifer Moyer; 2017-02-01 - 18290 - Jennifer Moyer-Assist plumbing &amp; flush coil. - Jennifer Moyer | Transferred to HVAC, HP1-12 Calling for cooling and it's 80 deg in space. HVAC to reset the HP. EMS WO#209295, HVAC WO#209331. ASUHC-Agent: Kyle Van Bergen Description: To hot in entire office, server room is reaching unacceptable temperature. Who was dispatched: Time of dispatch: 2016-12-23 - 18290 - Zhi Yu-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Jennifer Moyer-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Roque Garcia-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Midhat Mukanovic-Upon arrival, the unit was in "lock out" code. This means the unit has had 3 error codes which shut the unit off. We reset the unit by turning off the disconnect and when power was restored, the unit began cooling again, as was done in the past. For this unit, according to the manual, this erases the previous error codes. So, we troubleshot this unit without the assistance of the units built in diagnostics system. All troubleshooting techniques led to the conclusion that there is a restriction either in the refrigerant line, or the water line. Restrictions in the refrigerant line are usually located by the frost in an unusual part of the system. This system is enclosed, and not all is easily accessible, therefore we will rule out a refrigerant restriction by ruling out a water restriction. This unit does not have isolation valves, so I will request a work order for the plumbing shop to install them. The unit was put into troubleshooting mode, but did not fail in our presence. - Jennifer Moyer; 2016-12-23 - 18290 - Jennifer Moyer-For this unit, diagnostics indicate that it was a possible incorrect charge/restriction, so all refrigerant was removed from this unit and it was weighed in to ensure correctness. The unit had no changes, so it is still back to the water restriction or flow problem. - Jennifer Moyer; 2016-12-23 - 18290 - Zhi Yu-For this unit, diagnostics indicate that it was a possible incorrect charge/restriction, so all refrigerant was removed from this unit and it was weighed in to ensure correctness. The unit had no changes, so it is still back to the water restriction or flow problem. - Jennifer Moyer; 2017-01-03 - 18290 - Jennifer Moyer-call to check on condition of A/C.(any temp alarms) - Jennifer Moyer; 2017-02-01 - 18290 - Jennifer Moyer-Assist plumbing &amp; flush coil. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 5
2016-12-20 | 40827 | TMPE-209330 | For HVAC. The refrigeration unit underneath the drinking fountain located outside room 333 is low on Freon. It keep running all day so I unplugged it. Please fix. 42C9GKG | 2017-01-26 - 18010 - Thomas Gibble-chiller under drinking fountain is old with R-12 and is empty. the angle stop is broken and drain is slow. transferred to plumping shop - Thomas Gibble; 2017-01-26 - 18010 - Gail Jackson-chiller under drinking fountain is old with R-12 and is empty. the angle stop is broken and drain is slow. transferred to plumping shop - Thomas Gibble | For HVAC. The refrigeration unit underneath the drinking fountain located outside room 333 is low on Freon. It keep running all day so I unplugged it. Please fix. 42C9GKG 2017-01-26 - 18010 - Thomas Gibble-chiller under drinking fountain is old with R-12 and is empty. the angle stop is broken and drain is slow. transferred to plumping shop - Thomas Gibble; 2017-01-26 - 18010 - Gail Jackson-chiller under drinking fountain is old with R-12 and is empty. the angle stop is broken and drain is slow. transferred to plumping shop - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2016-12-20 | 40877 | TMPE-209280 | MUSIC WB52U1 Please create a SWO for AC, to look at FCU-1 & 2 at Music West EQ. room WB 52U1. There is a leak coming from both units. Thank you Terry Martin | 2017-02-06 - 18010 - Roque Garcia-The two units condensate line was clogged cleared and checked ok. - Roque Garcia | MUSIC WB52U1 Please create a SWO for AC, to look at FCU-1 & 2 at Music West EQ. room WB 52U1. There is a leak coming from both units. Thank you Terry Martin 2017-02-06 - 18010 - Roque Garcia-The two units condensate line was clogged cleared and checked ok. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-20 | 40879 | TMPE-209278 | USB Bldg 150. Fabricate and install auxiliary drain pans under each air handler. Rout PVC drain line through ceiling tiles. Assign to Carl Karr. | 2017-01-03 - 18270 - Carl Karr-Fabricate ductwork. - Carl Karr; 2017-01-04 - 18270 - Carl Karr-Measure and fabricate - Carl Karr; 2017-01-09 - 18270 - Carl Karr-Fabricate duct. - Carl Karr; 2017-01-09 - 18270 - Gail Jackson-Fabricate duct. - Carl Karr; 2017-01-18 - 18270 - Carl Karr-Fabricate pans - Carl Karr; 2017-02-27 - 18270 - Carl Karr-Fabricate pan. - Carl Karr | USB Bldg 150. Fabricate and install auxiliary drain pans under each air handler. Rout PVC drain line through ceiling tiles. Assign to Carl Karr. 2017-01-03 - 18270 - Carl Karr-Fabricate ductwork. - Carl Karr; 2017-01-04 - 18270 - Carl Karr-Measure and fabricate - Carl Karr; 2017-01-09 - 18270 - Carl Karr-Fabricate duct. - Carl Karr; 2017-01-09 - 18270 - Gail Jackson-Fabricate duct. - Carl Karr; 2017-01-18 - 18270 - Carl Karr-Fabricate pans - Carl Karr; 2017-02-27 - 18270 - Carl Karr-Fabricate pan. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2016-12-20 | 40882 | TMPE-209275 | CAVC 3. College Avenue Commons (CAVC) Bldg. 178. Decorative fountain recirc pump not operating. Assign to Jose Lopez | 2016-12-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-30 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-31 - 23100 - Gail Jackson-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Thomas Gibble-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Robert Dauscher-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Michael Longtin-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-02-16 - 23100 - Gail Jackson-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson; 2017-02-16 - 23100 - Thomas Gibble-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson; 2017-02-16 - 23100 - Carl Karr-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson | CAVC 3. College Avenue Commons (CAVC) Bldg. 178. Decorative fountain recirc pump not operating. Assign to Jose Lopez 2016-12-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-30 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-01-31 - 23100 - Gail Jackson-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Thomas Gibble-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Robert Dauscher-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-01-31 - 23100 - Michael Longtin-Barrow manhole cage from plumbers; shops was disposed of in the PAYLESS CLEANOUT. Remove old burned out pump motor. Transport to shop, disassemble. Trip to Martins Fluid Masters for new SEALS. Clean and reassemble pump. Back to Collage Commons to install and run test. Sheet metal man needed for drip pan install to prevent this burn out again. - Gail Jackson; 2017-02-16 - 23100 - Gail Jackson-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson; 2017-02-16 - 23100 - Thomas Gibble-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson; 2017-02-16 - 23100 - Carl Karr-Use plumbers manhole cage with Tom Gibble as Topside safety man with Carl and Wes in pit to install drip hood over large electric panel to stop rain water. Caulk all hard pipe electrical connections. Install water sheild over pump to protect motor. This is the 3rd motor that has been installed. Carl made pan and hoods. - Gail Jackson | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2016-12-20 | 40892 | TMPE-209265 | 5. USB Bldg. 150. Clean all return air filter grilles on first floor. Assign to Jennifer Moyer and Thomas Gibble and Gail Jackson | NA | 5. USB Bldg. 150. Clean all return air filter grilles on first floor. Assign to Jennifer Moyer and Thomas Gibble and Gail Jackson NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-20 | 40929 | TMPE-209228 | PS BETWEEN B & C The chiller outside; the fans are not on. Please send someone from HVAC as soon as possible. | 2016-12-20 - 18080 - CALLED TO STEVE P. - Monica Moraga; 2016-12-20 - 18080 - Robert Ecabert-Reset the chiller after the power outage. - Robert Ecabert | PS BETWEEN B & C The chiller outside; the fans are not on. Please send someone from HVAC as soon as possible. 2016-12-20 - 18080 - CALLED TO STEVE P. - Monica Moraga; 2016-12-20 - 18080 - Robert Ecabert-Reset the chiller after the power outage. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-20 | 40974 | TMPE-209183 | UCENT B 3RD FL PL transfer to AC: The AHU has a leak but don\\u2019t really know from were. It wasn\\u2019t leaking when we checked but we know it\\u2019s from a AHU. Third floor North end of office space. Ceiling tile is sagging a little. There's a ceiling leaking in the south center of the 3rd floor. The ceiling . . . | 2017-01-04 - 18050 - Jennifer Moyer-Unit just needed a new filter. It took me some time to locate a 10ft ladder, as I had a 12ft. I also changed a filter in the server room. I am sure all of the filters on this floor need changed.I went to material services to get the filters.I also located where the ceiling tiles were stored and replaced them so the job would be completely finished. - Jennifer Moyer | UCENT B 3RD FL PL transfer to AC: The AHU has a leak but don\\u2019t really know from were. It wasn\\u2019t leaking when we checked but we know it\\u2019s from a AHU. Third floor North end of office space. Ceiling tile is sagging a little. There's a ceiling leaking in the south center of the 3rd floor. The ceiling . . . 2017-01-04 - 18050 - Jennifer Moyer-Unit just needed a new filter. It took me some time to locate a 10ft ladder, as I had a 12ft. I also changed a filter in the server room. I am sure all of the filters on this floor need changed.I went to material services to get the filters.I also located where the ceiling tiles were stored and replaced them so the job would be completely finished. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-20 | 171325 | RFMT-137006 | Assist Sal: Service and clean out debris from roof top laundry room exhaust vent hood. | 2016-12-21 - 18010 - Eric Miller-Marked vent for cutting. - Eric Miller; 2016-12-30 - 18010 - Eric Miller-Cut hole in vent, cleaned out lint. - Eric Miller | Assist Sal: Service and clean out debris from roof top laundry room exhaust vent hood. 2016-12-21 - 18010 - Eric Miller-Marked vent for cutting. - Eric Miller; 2016-12-30 - 18010 - Eric Miller-Cut hole in vent, cleaned out lint. - Eric Miller | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-20 | 171381 | RFMT-136950 | Service and clean out debris from roof top laundry room exhaust vent hood. | 2016-12-21 - 18010 - Salvatore Marasco Jr-Measured and mark out where hole will be cut. - Salvatore Marasco Jr | Service and clean out debris from roof top laundry room exhaust vent hood. 2016-12-21 - 18010 - Salvatore Marasco Jr-Measured and mark out where hole will be cut. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-20 | 232503 | POLY-115695 | BILLED STEVE - *OK TO PROCEED WITH THIS WORK* Install condenser fan on refrigerated chiller outside Rm 116. Have replacement fan. Use blanket PO. 42B55N2 BILL TO BLANKET PO #WAS02000040 | NA | BILLED STEVE - *OK TO PROCEED WITH THIS WORK* Install condenser fan on refrigerated chiller outside Rm 116. Have replacement fan. Use blanket PO. 42B55N2 BILL TO BLANKET PO #WAS02000040 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-21 | 40708 | TMPE-209449 | This air compressor needs to be replaced. Found the piston in one of the heads broken on pump 1 and the pump is seized. Pump 2 has bad valves in one of the three heads and is struggling to pump up to set point of 90 psi. | NA | This air compressor needs to be replaced. Found the piston in one of the heads broken on pump 1 and the pump is seized. Pump 2 has bad valves in one of the three heads and is struggling to pump up to set point of 90 psi. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 5
2016-12-22 | 40493 | TMPE-209664 | MWO - Design North Transferred call to HVAC - Control air refrigerated dryer is plugged and not allowing air to pass through. Compressor alarm going off. Send to EMS Bob Borucki 42B213C | 2017-01-25 - 18040 - Jose Lopez-remove oil separator replaced unit check for leaks working ok - Jose Lopez | MWO - Design North Transferred call to HVAC - Control air refrigerated dryer is plugged and not allowing air to pass through. Compressor alarm going off. Send to EMS Bob Borucki 42B213C 2017-01-25 - 18040 - Jose Lopez-remove oil separator replaced unit check for leaks working ok - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-22 | 40522 | TMPE-209635 | ECF F130H There is a leak in the conference room, lots of water, steady drip/stream. | 2016-12-22 - 10130 - Sent over to Bob and Sean - Amanda Thomas; 2017-01-03 - 10130 - Timothy Grabowski-Transferred to A/C shop cover installed by them needed to be reinstsalled - Sean Chrisman | ECF F130H There is a leak in the conference room, lots of water, steady drip/stream. 2016-12-22 - 10130 - Sent over to Bob and Sean - Amanda Thomas; 2017-01-03 - 10130 - Timothy Grabowski-Transferred to A/C shop cover installed by them needed to be reinstsalled - Sean Chrisman | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-22 | 40525 | TMPE-209632 | LSD Roof !! LSD HVAC fan, blade, or motor needs replacement. Included picture on request. This is on the West side of the building, closest motor towards central plant. I know we had this looked at before, spins out of balance intermittently causing excessive vibration and noise. Thanks i. . . | 2017-01-06 - 18010 - Robert Ecabert-Installed a new fan blade on the condenser fan motor because the old one was bent badly causing the air conditioning unit to vibrate uncontrollably and now with the new blade on the condenser fan motor runs fine. - Robert Ecabert | LSD Roof !! LSD HVAC fan, blade, or motor needs replacement. Included picture on request. This is on the West side of the building, closest motor towards central plant. I know we had this looked at before, spins out of balance intermittently causing excessive vibration and noise. Thanks i. . . 2017-01-06 - 18010 - Robert Ecabert-Installed a new fan blade on the condenser fan motor because the old one was bent badly causing the air conditioning unit to vibrate uncontrollably and now with the new blade on the condenser fan motor runs fine. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-22 | 40561 | TMPE-209596 | CAVC 332 add AC shop: water is dripping from fan, Reuben roof is the contact There is a roof fan leaking onto the 3rd floor atrium area. Reoccurring issue, please repair. Contact Alan with any questions. Thank you! | 2017-05-18 - 10130 - Mitchell Andrews-cleared the condenstate drain for the air handler - Mitchell Andrews | CAVC 332 add AC shop: water is dripping from fan, Reuben roof is the contact There is a roof fan leaking onto the 3rd floor atrium area. Reoccurring issue, please repair. Contact Alan with any questions. Thank you! 2017-05-18 - 10130 - Mitchell Andrews-cleared the condenstate drain for the air handler - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-22 | 40563 | TMPE-209594 | USB 2131: Ceiling leak | 2016-12-22 - 10130 - Send over to Bob and Sean - Amanda Thomas; 2016-12-23 - 10130 - Christopher Dovales-Checking on roof leaks need to flash joints on metal curb pan - Christopher Dovales; 2017-01-12 - 10130 - Christopher Dovales-checking on roof in RM2131 need to seal curb pan - Christopher Dovales; 2017-01-13 - 10130 - Christopher Dovales-Sealed metal flashing under cooler and curb pan joint - Christopher Dovales | USB 2131: Ceiling leak 2016-12-22 - 10130 - Send over to Bob and Sean - Amanda Thomas; 2016-12-23 - 10130 - Christopher Dovales-Checking on roof leaks need to flash joints on metal curb pan - Christopher Dovales; 2017-01-12 - 10130 - Christopher Dovales-checking on roof in RM2131 need to seal curb pan - Christopher Dovales; 2017-01-13 - 10130 - Christopher Dovales-Sealed metal flashing under cooler and curb pan joint - Christopher Dovales | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 40580 | TMPE-209577 | CAVC 332 There is a roof fan leaking onto the 3rd floor atrium area. Reoccurring issue, please repair. Contact Alan with any questions. Thank you! | 2016-12-22 - 10130 - Called out to Bob - Amanda Thomas; 2016-12-28 - 10130 - Reuben Bilducia-Completed turned over to AC shop fan appears to be leaking internally. - Reuben Bilducia | CAVC 332 There is a roof fan leaking onto the 3rd floor atrium area. Reoccurring issue, please repair. Contact Alan with any questions. Thank you! 2016-12-22 - 10130 - Called out to Bob - Amanda Thomas; 2016-12-28 - 10130 - Reuben Bilducia-Completed turned over to AC shop fan appears to be leaking internally. - Reuben Bilducia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43035 | TMPE-207122 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43039 | TMPE-207118 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43261 | TMPE-206896 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43262 | TMPE-206895 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43263 | TMPE-206894 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43264 | TMPE-206893 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43265 | TMPE-206892 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43266 | TMPE-206891 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43267 | TMPE-206890 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43268 | TMPE-206889 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43269 | TMPE-206888 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43270 | TMPE-206887 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43271 | TMPE-206886 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43272 | TMPE-206885 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43273 | TMPE-206884 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43274 | TMPE-206883 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43275 | TMPE-206882 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43276 | TMPE-206881 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43277 | TMPE-206880 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43278 | TMPE-206879 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43279 | TMPE-206878 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43280 | TMPE-206877 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43281 | TMPE-206876 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43282 | TMPE-206875 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43283 | TMPE-206874 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-22 | 43396 | TMPE-206761 | Air Compressor-Biannual | 2016-12-21 - xPM-0100-B - Matthew Smith-Found the piston broken on pump 1 and the pump is seized. Pump 2 has bad valves in one of the three heads. Submitted a WO for the replacement of the air compressor. - Matthew Smith | Air Compressor-Biannual 2016-12-21 - xPM-0100-B - Matthew Smith-Found the piston broken on pump 1 and the pump is seized. Pump 2 has bad valves in one of the three heads. Submitted a WO for the replacement of the air compressor. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 6
2016-12-22 | 43400 | TMPE-206757 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-22 | 171093 | RFMT-137238 | Roof top exhaust fan: Rain cover is detached. Exhaust fan is malfunctioning. | 2016-12-29 - 18010 - Thor Millsaps-Re-attached fan cover and adjusted motor to reduce vibration. - Thor Millsaps | Roof top exhaust fan: Rain cover is detached. Exhaust fan is malfunctioning. 2016-12-29 - 18010 - Thor Millsaps-Re-attached fan cover and adjusted motor to reduce vibration. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-22 | 171158 | RFMT-137173 | Please replace the heating valve in the stack of 34 and 35 in the penthouse of PV East. Simon | 2016-12-23 - 18010 - Thor Millsaps-Picked up actuators for heating water line at United Refrigeration. Replaced 2 actuators with Belimo actuators. - Simon Fernandez | Please replace the heating valve in the stack of 34 and 35 in the penthouse of PV East. Simon 2016-12-23 - 18010 - Thor Millsaps-Picked up actuators for heating water line at United Refrigeration. Replaced 2 actuators with Belimo actuators. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2016-12-23 | 40385 | TMPE-209772 | Roof Leak in Penthouse Mechanical Room at ISTB-4, Leak is northwest corner of building near roof drain scuppers and makeup air roof jack penetrations. There is a trash can beneath location in mechanical room. Thank You | 2017-01-05 - 13120 - Christopher Dovales-Roof is under warranty contractor sealed above metal flashing on curb - Christopher Dovales | Roof Leak in Penthouse Mechanical Room at ISTB-4, Leak is northwest corner of building near roof drain scuppers and makeup air roof jack penetrations. There is a trash can beneath location in mechanical room. Thank You 2017-01-05 - 13120 - Christopher Dovales-Roof is under warranty contractor sealed above metal flashing on curb - Christopher Dovales | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-23 | 40420 | TMPE-209737 | LSE 541 !! It is reported, "One of the Conviron growth chambers in LSE 541 is overheating. We have shut it down and moved cultures but need it looked at ASAP." Please open a work order for HVAC to address as quickly as possible. Thank you. 42BLHKH | 2017-01-06 - 18140 - Robert Ecabert-Found return air damper closed for this room causing the room to over heat and trip the conviron growth chambers to over heat. Ever since I have opened the return air damper to onehundred percent the room is staying much cooler and the convirons have not tripped off since. - Robert Ecabert | LSE 541 !! It is reported, "One of the Conviron growth chambers in LSE 541 is overheating. We have shut it down and moved cultures but need it looked at ASAP." Please open a work order for HVAC to address as quickly as possible. Thank you. 42BLHKH 2017-01-06 - 18140 - Robert Ecabert-Found return air damper closed for this room causing the room to over heat and trip the conviron growth chambers to over heat. Ever since I have opened the return air damper to onehundred percent the room is staying much cooler and the convirons have not tripped off since. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-23 | 40430 | TMPE-209727 | ASU Police Building: BT transfer to HVAC - Unit outside 324H has a buzzing sound and red light flashing. Buzzing sound that is very concerning. Please check, ASAP. | 2016-12-23 - 18010 - Zhi Yu- Room 324. No buzzing noise at arrival. We check the VAV Box N2=63 all contactor and transformer appears normal. We call EMS, spoke to John Howell see if we can duplicate buzzing noise by cycling the VMA. Notice the Rib control light is off. We lose signal. This call Will transfer to EMS.. - Zhi Yu [Modified: 2016-12-23 Zhi Yu] | ASU Police Building: BT transfer to HVAC - Unit outside 324H has a buzzing sound and red light flashing. Buzzing sound that is very concerning. Please check, ASAP. 2016-12-23 - 18010 - Zhi Yu- Room 324. No buzzing noise at arrival. We check the VAV Box N2=63 all contactor and transformer appears normal. We call EMS, spoke to John Howell see if we can duplicate buzzing noise by cycling the VMA. Notice the Rib control light is off. We lose signal. This call Will transfer to EMS.. - Zhi Yu [Modified: 2016-12-23 Zhi Yu] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-23 | 40438 | TMPE-209719 | ASU Police Building: Buzzing sound that is very concerning. Please check, ASAP. | 2016-12-23 - 10010 - Lance Tapia-Transferred to HVAC. I received a call from service center, Francis, and she said there is a loud buzzing noise coming from a light fixture. Waited to be escorted and removed ceiling tile from the ceiling and noticed that the A/C unit door was open and one of the electrical contactors had a red indicator lit and was buzzing very loud. Called service center back and spoke with Francis to ask her to transfer the work order to HVAC. I did not know the severity of the issue so I asked her to have HVAC come out soon to check on the A/C unit. Materials-n/a .75 hrs - Lance Tapia | ASU Police Building: Buzzing sound that is very concerning. Please check, ASAP. 2016-12-23 - 10010 - Lance Tapia-Transferred to HVAC. I received a call from service center, Francis, and she said there is a loud buzzing noise coming from a light fixture. Waited to be escorted and removed ceiling tile from the ceiling and noticed that the A/C unit door was open and one of the electrical contactors had a red indicator lit and was buzzing very loud. Called service center back and spoke with Francis to ask her to transfer the work order to HVAC. I did not know the severity of the issue so I asked her to have HVAC come out soon to check on the A/C unit. Materials-n/a .75 hrs - Lance Tapia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-23 | 253348 | DTPC-115190 | The fan on the south west side of the Post Office is not working. | 2016-12-23 - 15000 - Ross Hossack-Diagnosed problem with fan and found it to have a blown fuse.I then located a new fuse and replaced it. Fan is now working. - Ross Hossack | The fan on the south west side of the Post Office is not working. 2016-12-23 - 15000 - Ross Hossack-Diagnosed problem with fan and found it to have a blown fuse.I then located a new fuse and replaced it. Fan is now working. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-23 | 3054 | WEST-108195 | Portable Generator Maintenance-Monthly | NA | Portable Generator Maintenance-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-27 | 40172 | TMPE-209985 | Naumann Hobbs: Located unit and found unit had bad front brake pads and bearings and seal to motor leak. Removed motor pulled input shaft/ replaced seal reinstalled motor and fixed breaks and bearings. Total: 1208.21 | NA | Naumann Hobbs: Located unit and found unit had bad front brake pads and bearings and seal to motor leak. Removed motor pulled input shaft/ replaced seal reinstalled motor and fixed breaks and bearings. Total: 1208.21 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-27 | 40359 | TMPE-209798 | ASUHD-Agent: Connie Brown Description: Hot water pump refer by Mike to Hvac Who was dispatched: Call Jose Lopez Time of dispatch:10:15a Mike called to advise has no Hot water at Carson and had called plubmer but is need to have HVAC check for Hot water Pump at this location has not hot water ca. . . | 2016-12-29 - 23100 - 12/27/2016 5OT 10:45am-3:45pm Jose Lopez - CARSON Carson HW pump - Rebuild. - Kerri Perkins; 2016-12-30 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-30 - 23100 - Jose Lopez-remove pump replaced coupling and hub add oil and replaced bearing check for leaks - Jose Lopez | ASUHD-Agent: Connie Brown Description: Hot water pump refer by Mike to Hvac Who was dispatched: Call Jose Lopez Time of dispatch:10:15a Mike called to advise has no Hot water at Carson and had called plubmer but is need to have HVAC check for Hot water Pump at this location has not hot water ca. . . 2016-12-29 - 23100 - 12/27/2016 5OT 10:45am-3:45pm Jose Lopez - CARSON Carson HW pump - Rebuild. - Kerri Perkins; 2016-12-30 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2016-12-30 - 23100 - Jose Lopez-remove pump replaced coupling and hub add oil and replaced bearing check for leaks - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-28 | 40210 | TMPE-209947 | MUSIC W224U1 Please create WO for HVAC and Electric Shop to determine why AHU # 7 will not run. The VFD does not respond properly and the motor might have an issue?! Thanks Jeffrey Contact Name: Robert Zaller Contact Phone Number: 965-4521 Contact Email: 4N00ABB | 2016-12-30 - 15100 - Greg Urena-Assisted Bob with drive issue. - Robert Kirk | MUSIC W224U1 Please create WO for HVAC and Electric Shop to determine why AHU # 7 will not run. The VFD does not respond properly and the motor might have an issue?! Thanks Jeffrey Contact Name: Robert Zaller Contact Phone Number: 965-4521 Contact Email: 4N00ABB 2016-12-30 - 15100 - Greg Urena-Assisted Bob with drive issue. - Robert Kirk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-28 | 40220 | TMPE-209937 | Central Plant R1 - Please have vendor come out to repair cooling tower motor 4A. See Mike T for information. 4NNI9H6 | NA | Central Plant R1 - Please have vendor come out to repair cooling tower motor 4A. See Mike T for information. 4NNI9H6 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-28 | 40318 | TMPE-209839 | USB 1176F Transferred call to HVAC, please check HP 17, it has no power. EMS WO#209823, HVAC WO#209839. The heat doesn't seem to be on in this area...is it possible to check? Thank you. 42AF4CA | 2016-12-29 - 18010 - Gail Jackson-Found 1 fuse blew and tstat marked wrong; unit #16 not #17. Trouble shoot and found motor burned out. Work needs to be done early AM to avoid office help. - Gail Jackson; 2016-12-29 - 18010 - Thomas Gibble-Found 1 fuse blew and tstat marked wrong; unit #16 not #17. Trouble shoot and found motor burned out. Work needs to be done early AM to avoid office help. - Gail Jackson; 2016-12-30 - 18010 - Gail Jackson-Found motor burned out, trip to Trane Tempe for replacement motor and run cap. Installed motor and replaced in A/H unit 16. Run test complete. Installation of blower assembly in unit is dangerous; great care must be taken for install; a safer method needs to be figured out. - Gail Jackson; 2016-12-30 - 18010 - Thomas Gibble-Found motor burned out, trip to Trane Tempe for replacement motor and run cap. Installed motor and replaced in A/H unit 16. Run test complete. Installation of blower assembly in unit is dangerous; great care must be taken for install; a safer method needs to be figured out. - Gail Jackson | USB 1176F Transferred call to HVAC, please check HP 17, it has no power. EMS WO#209823, HVAC WO#209839. The heat doesn't seem to be on in this area...is it possible to check? Thank you. 42AF4CA 2016-12-29 - 18010 - Gail Jackson-Found 1 fuse blew and tstat marked wrong; unit #16 not #17. Trouble shoot and found motor burned out. Work needs to be done early AM to avoid office help. - Gail Jackson; 2016-12-29 - 18010 - Thomas Gibble-Found 1 fuse blew and tstat marked wrong; unit #16 not #17. Trouble shoot and found motor burned out. Work needs to be done early AM to avoid office help. - Gail Jackson; 2016-12-30 - 18010 - Gail Jackson-Found motor burned out, trip to Trane Tempe for replacement motor and run cap. Installed motor and replaced in A/H unit 16. Run test complete. Installation of blower assembly in unit is dangerous; great care must be taken for install; a safer method needs to be figured out. - Gail Jackson; 2016-12-30 - 18010 - Thomas Gibble-Found motor burned out, trip to Trane Tempe for replacement motor and run cap. Installed motor and replaced in A/H unit 16. Run test complete. Installation of blower assembly in unit is dangerous; great care must be taken for install; a safer method needs to be figured out. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-28 | 170982 | RFMT-137349 | Repeat Request. My AC has leaked multiple times this semester with a lot of water, almost ruining my bedding. I would like it to be fixed so it doesn't drain water anymore. Attachment(s) 4NG57I2 | 2016-12-30 - 18010 - Simon Fernandez-searched for leak found non at this time. - Simon Fernandez | Repeat Request. My AC has leaked multiple times this semester with a lot of water, almost ruining my bedding. I would like it to be fixed so it doesn't drain water anymore. Attachment(s) 4NG57I2 2016-12-30 - 18010 - Simon Fernandez-searched for leak found non at this time. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-28 | 171017 | RFMT-137314 | The pool seems to be draining unintentionally. It's filling up but draining at the same time. CALLED TO GREG S. Submitted by 4NID637 | 2016-12-29 - 24000 - Gabriel Figueroa-Ran more water in pool to get it back to proper level. Started up pool pump and bleed out air out of system. Will leave running for the day to make sure all is working proper. Will return tomarrow to vacuum out debri out of pool. - Gabriel Figueroa | The pool seems to be draining unintentionally. It's filling up but draining at the same time. CALLED TO GREG S. Submitted by 4NID637 2016-12-29 - 24000 - Gabriel Figueroa-Ran more water in pool to get it back to proper level. Started up pool pump and bleed out air out of system. Will leave running for the day to make sure all is working proper. Will return tomarrow to vacuum out debri out of pool. - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-28 | 253267 | DTPC-115271 | RTU 5 has a bad circuit board and the thermostat is blank. Please repair | 2017-01-23 - 18010 - Reassigned from James Herman to Ralph Lemons. - Patricia Best; 2017-01-23 - 18010 - Ralph Lemons-This has been completed by Mike with BLS Mechanical. Unit is running good at this time. - Ralph Lemons | RTU 5 has a bad circuit board and the thermostat is blank. Please repair 2017-01-23 - 18010 - Reassigned from James Herman to Ralph Lemons. - Patricia Best; 2017-01-23 - 18010 - Ralph Lemons-This has been completed by Mike with BLS Mechanical. Unit is running good at this time. - Ralph Lemons | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-29 | 40081 | TMPE-210076 | INTDSA A130U1 Air Handler is making a very loud audible noise, possibly an alarm? Anyhow, does not sound good. Please inspect asap. Thank you. | 2016-12-30 - 18050 - Jennifer Moyer-Install filters, clean coil. - Jennifer Moyer; 2016-12-30 - 18050 - 12/29/16 Jennifer Moyer 1 hr. CE over pressurized due to dirty filters - Juliana Blusiewicz | INTDSA A130U1 Air Handler is making a very loud audible noise, possibly an alarm? Anyhow, does not sound good. Please inspect asap. Thank you. 2016-12-30 - 18050 - Jennifer Moyer-Install filters, clean coil. - Jennifer Moyer; 2016-12-30 - 18050 - 12/29/16 Jennifer Moyer 1 hr. CE over pressurized due to dirty filters - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2016-12-29 | 40129 | TMPE-210028 | Add: AC shop exhaust fan motor is bad *original message* The VFD drive for exhaust fan #1253, located in corrridor behind 6th Fl. MRR , normally is set to run in hand at 49 Hz. Currently it is only able to ramp up to 29 Hz causing related fume hoods to alarm. Need Electrical services to chec. . . | NA | Add: AC shop exhaust fan motor is bad *original message* The VFD drive for exhaust fan #1253, located in corrridor behind 6th Fl. MRR , normally is set to run in hand at 49 Hz. Currently it is only able to ramp up to 29 Hz causing related fume hoods to alarm. Need Electrical services to chec. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-29 | 40158 | TMPE-209999 | sewer pump has become disconnected from discharge line needs repair - Haydon Library Rm C00U7- caution black widows -recommend pumping and cleaning of tank | 2017-02-15 - 23100 - Derek Gittings-need pit cleaned out first. - Derek Gittings; 2017-02-21 - 23100 - Derek Gittings-replacing bearings seals. - Derek Gittings; 2017-03-21 - 23100 - Derek Gittings-pump did not show up. - Derek Gittings; 2017-03-31 - 23100 - Derek Gittings-replaced pipe unblocked impeler. - Derek Gittings; 2017-03-31 - 23100 - Mike kelly-replaced pipe unblocked impeler. - Derek Gittings; 2017-04-03 - 23100 - Brian Qualls-#1 and 2 pumps not working. Pumping service called to pump sump pit. - Brian Qualls; 2017-04-03 - 23100 - Brian Qualls-Stayed with and assisted pumping contractor until job was complete, left at 12am Friday 3/31/17. - Brian Qualls | sewer pump has become disconnected from discharge line needs repair - Haydon Library Rm C00U7- caution black widows -recommend pumping and cleaning of tank 2017-02-15 - 23100 - Derek Gittings-need pit cleaned out first. - Derek Gittings; 2017-02-21 - 23100 - Derek Gittings-replacing bearings seals. - Derek Gittings; 2017-03-21 - 23100 - Derek Gittings-pump did not show up. - Derek Gittings; 2017-03-31 - 23100 - Derek Gittings-replaced pipe unblocked impeler. - Derek Gittings; 2017-03-31 - 23100 - Mike kelly-replaced pipe unblocked impeler. - Derek Gittings; 2017-04-03 - 23100 - Brian Qualls-#1 and 2 pumps not working. Pumping service called to pump sump pit. - Brian Qualls; 2017-04-03 - 23100 - Brian Qualls-Stayed with and assisted pumping contractor until job was complete, left at 12am Friday 3/31/17. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2016-12-29 | 40159 | TMPE-209998 | LIB Roof There is a small EQ room next to the elevator shaft on the roof. In this room, the motor to the relief fan has gone caput. Please | 2017-02-07 - 18230 - Jennifer Moyer-Located motor on roof, went back to truck to get ladder to read motor info. Gathered motor info. then researched vendor prices and options. Could not pick up ladder and get shaft size, as the door would not open. Service center was called for the door lock. - Jennifer Moyer; 2017-05-11 - 18230 - Jennifer Moyer-Review motor removal with LEAD. - Jennifer Moyer; 2017-05-17 - 18230 - Jennifer Moyer-Removed bad motor and brought back to shop. Planned new install next week. - Jennifer Moyer; 2017-05-17 - 18230 - Chad Hargrave-Removed bad motor and brought back to shop. Planned new install next week. - Jennifer Moyer | LIB Roof There is a small EQ room next to the elevator shaft on the roof. In this room, the motor to the relief fan has gone caput. Please 2017-02-07 - 18230 - Jennifer Moyer-Located motor on roof, went back to truck to get ladder to read motor info. Gathered motor info. then researched vendor prices and options. Could not pick up ladder and get shaft size, as the door would not open. Service center was called for the door lock. - Jennifer Moyer; 2017-05-11 - 18230 - Jennifer Moyer-Review motor removal with LEAD. - Jennifer Moyer; 2017-05-17 - 18230 - Jennifer Moyer-Removed bad motor and brought back to shop. Planned new install next week. - Jennifer Moyer; 2017-05-17 - 18230 - Chad Hargrave-Removed bad motor and brought back to shop. Planned new install next week. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2016-12-29 | 40164 | TMPE-209993 | LIB C00U4 Air Compressor #801 is violently shaking. Please service asap. Thank you. | 2016-12-29 - 18030 - Called out to Steve - Amanda Thomas; 2017-01-09 - 18030 - Gail Jackson-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-09 - 18030 - Carl Karr-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-09 - 18030 - Zhi Yu-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-18 - 18030 - Gail Jackson-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Zhi Yu-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Midhat Mukanovic-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Michael Kelley-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Gail Jackson-Remove lift from basement and transport to shop and reassemble. - Gail Jackson; 2017-01-20 - 18030 - Gail Jackson-Found used compressed air filter dryer in mech. shop; installed in line; no leaks. #2 compressor went down on twin unit, tripped breaker, will restart but has issues; Steve said to talk to Brian. Condensate line will not bleed off, needs work. - Gail Jackson; 2017-01-20 - 18030 - Thomas Gibble-Found used compressed air filter dryer in mech. shop; installed in line; no leaks. #2 compressor went down on twin unit, tripped breaker, will restart but has issues; Steve said to talk to Brian. Condensate line will not bleed off, needs work. - Gail Jackson; 2017-01-27 - 18030 - Gail Jackson-Install new air compressor condensate bleed off, trip to ARS Tempe for parts. Cap off air line running into tunnel, it was open end blowing out causing compressors to wear out and quit, continuous run time. HOW LONG HAD THIS BEEN GOING ON? Run test compressors now cycle off. - Gail Jackson; 2017-01-27 - 18030 - Thomas Gibble-Install new air compressor condensate bleed off, trip to ARS Tempe for parts. Cap off air line running into tunnel, it was open end blowing out causing compressors to wear out and quit, continuous run time. HOW LONG HAD THIS BEEN GOING ON? Run test compressors now cycle off. - Gail Jackson | LIB C00U4 Air Compressor #801 is violently shaking. Please service asap. Thank you. 2016-12-29 - 18030 - Called out to Steve - Amanda Thomas; 2017-01-09 - 18030 - Gail Jackson-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-09 - 18030 - Carl Karr-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-09 - 18030 - Zhi Yu-found motor burned out, breaker tripped and primary compressor out on tripped breaker. Air leak in water filter. - Gail Jackson; 2017-01-18 - 18030 - Gail Jackson-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Zhi Yu-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Midhat Mukanovic-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Michael Kelley-Bench test test new motor, transport plumber lift and motor to sub basement, contacted police to access emergency door to transport equipment to basement. - Gail Jackson; 2017-01-18 - 18030 - Gail Jackson-Remove lift from basement and transport to shop and reassemble. - Gail Jackson; 2017-01-20 - 18030 - Gail Jackson-Found used compressed air filter dryer in mech. shop; installed in line; no leaks. #2 compressor went down on twin unit, tripped breaker, will restart but has issues; Steve said to talk to Brian. Condensate line will not bleed off, needs work. - Gail Jackson; 2017-01-20 - 18030 - Thomas Gibble-Found used compressed air filter dryer in mech. shop; installed in line; no leaks. #2 compressor went down on twin unit, tripped breaker, will restart but has issues; Steve said to talk to Brian. Condensate line will not bleed off, needs work. - Gail Jackson; 2017-01-27 - 18030 - Gail Jackson-Install new air compressor condensate bleed off, trip to ARS Tempe for parts. Cap off air line running into tunnel, it was open end blowing out causing compressors to wear out and quit, continuous run time. HOW LONG HAD THIS BEEN GOING ON? Run test compressors now cycle off. - Gail Jackson; 2017-01-27 - 18030 - Thomas Gibble-Install new air compressor condensate bleed off, trip to ARS Tempe for parts. Cap off air line running into tunnel, it was open end blowing out causing compressors to wear out and quit, continuous run time. HOW LONG HAD THIS BEEN GOING ON? Run test compressors now cycle off. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
2016-12-29 | 40177 | TMPE-209980 | Transferred Call to HVAC, Hot water pump has been disconnected (LOTO) by HVAC. Per Rick Florence "We are hosting an International Piano Competition beginning this Sunday. The cooler temperature has caused most of our pianos to go out of tune and we are scrambling to get things back in shape. The. . . | NA | Transferred Call to HVAC, Hot water pump has been disconnected (LOTO) by HVAC. Per Rick Florence "We are hosting an International Piano Competition beginning this Sunday. The cooler temperature has caused most of our pianos to go out of tune and we are scrambling to get things back in shape. The. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2016-12-29 | 40180 | TMPE-209977 | SCOB !! Floor sink overflowing ; called in by Scot Wilson Add HVAC ___ Greg went to unclog floor sink and found the the sump pump was not working 4NN0EFK | 2017-01-11 - 23100 - Michael Kelley-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Roque Garcia-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Midhat Mukanovic-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Michael Kelley-Checked pump and floats - Michael Kelley | SCOB !! Floor sink overflowing ; called in by Scot Wilson Add HVAC ___ Greg went to unclog floor sink and found the the sump pump was not working 4NN0EFK 2017-01-11 - 23100 - Michael Kelley-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Roque Garcia-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Midhat Mukanovic-Found 3 of the 4 floats bad. Pump number 2 has become unattached from pipe. Replaced floats. Tested. - Michael Kelley; 2017-01-11 - 23100 - Michael Kelley-Checked pump and floats - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-29 | 170981 | RFMT-137350 | Repeat Request. My AC has leaked multiple times this semester with a lot of water, almost ruining my bedding. I would like it to be fixed so it doesn't drain water anymore. Attachment(s) 4NG57I2 | 2016-12-29 - 18010 - Thor Millsaps-Inspected fan coil and surrounding area. Found no evidence of water leaking. Suspect leaking may be related to improper drainage in main condensate drain line. Water had been leaking in adjacent bathroom during summer because main drain line is clogged. - Thor Millsaps | Repeat Request. My AC has leaked multiple times this semester with a lot of water, almost ruining my bedding. I would like it to be fixed so it doesn't drain water anymore. Attachment(s) 4NG57I2 2016-12-29 - 18010 - Thor Millsaps-Inspected fan coil and surrounding area. Found no evidence of water leaking. Suspect leaking may be related to improper drainage in main condensate drain line. Water had been leaking in adjacent bathroom during summer because main drain line is clogged. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2016-12-29 | 28449 | TMPE-221708 | Tennant Sales and service company machine tested and running servie labor vr element, fltr, oil, spin-on oil motor 1qt total:361.76 | NA | Tennant Sales and service company machine tested and running servie labor vr element, fltr, oil, spin-on oil motor 1qt total:361.76 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-29 | 253242 | DTPC-115296 | Meet with Drago from Central Air. | 2016-12-29 - 18010 - Robert Bartels-Escort Drago to get filter and belt sizes from all data air units - Robert Bartels | Meet with Drago from Central Air. 2016-12-29 - 18010 - Robert Bartels-Escort Drago to get filter and belt sizes from all data air units - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-30 | 39658 | TMPE-210499 | HC - Simone Description: Can't get into 1130 building Dispatched to: Tom Gibble Time of Dispatch - 7:07pm | 2017-01-04 - 18010 - Thomas Gibble-water leaking from a/c unit. I vacuumed water out from cond pan. - Thomas Gibble; 2017-01-10 - 18010 - 12/30/2016 1.75 OT 7:15pm-9pm Thomas Gibble - UCENT B Water leaking from A/C unit - Kerri Perkins | HC - Simone Description: Can't get into 1130 building Dispatched to: Tom Gibble Time of Dispatch - 7:07pm 2017-01-04 - 18010 - Thomas Gibble-water leaking from a/c unit. I vacuumed water out from cond pan. - Thomas Gibble; 2017-01-10 - 18010 - 12/30/2016 1.75 OT 7:15pm-9pm Thomas Gibble - UCENT B Water leaking from A/C unit - Kerri Perkins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-30 | 40053 | TMPE-210104 | MUSIC EB1-1 !! Please create a WO for HVAC shop to repair blow down on air compressor. We had an issue with compressor loss it might be tripping on motor overload. Needs to be repaired ASAP due to music event this is Old Music EB1 EQ Room, also found one CHW pump was leaking on floor not runni. . . | 2017-01-05 - 18030 - Brian Qualls-Blow down is in good working condition. Found motor starter #1 heaters tripped. B phase line and load terminals loose on starter, tightened. Amp check good. 3.0amps-rated 3.2. Will check tomorrow. - Brian Qualls | MUSIC EB1-1 !! Please create a WO for HVAC shop to repair blow down on air compressor. We had an issue with compressor loss it might be tripping on motor overload. Needs to be repaired ASAP due to music event this is Old Music EB1 EQ Room, also found one CHW pump was leaking on floor not runni. . . 2017-01-05 - 18030 - Brian Qualls-Blow down is in good working condition. Found motor starter #1 heaters tripped. B phase line and load terminals loose on starter, tightened. Amp check good. 3.0amps-rated 3.2. Will check tomorrow. - Brian Qualls | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2016-12-30 | 253231 | DTPC-115307 | Fan Coil 1J is in alarm. | 2016-12-30 - 18010 - Ross Hossack-Checked out fan coil and found it had a broken belt. i replaced the belt.The unit is now working properly. - Ross Hossack | Fan Coil 1J is in alarm. 2016-12-30 - 18010 - Ross Hossack-Checked out fan coil and found it had a broken belt. i replaced the belt.The unit is now working properly. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2016-12-31 | 170889 | RFMT-137442 | Please pick up all electrical portable room heaters from all Best and Irish Buildings and stage on the Irish B basement store room shelf unit for pick up and return to the warehouse. | 2017-01-04 - 18010 - Eric Miller-Picked up room heaters. - Eric Miller | Please pick up all electrical portable room heaters from all Best and Irish Buildings and stage on the Irish B basement store room shelf unit for pick up and return to the warehouse. 2017-01-04 - 18010 - Eric Miller-Picked up room heaters. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-31 | 170890 | RFMT-137441 | Please pick up all electrical portable room heaters from all Hayden and Irish Buildings and stage on the Irish B basement store room shelf unit for pick up and return to the warehouse. | 2017-01-03 - 18010 - Salvatore Marasco Jr-Picked up/collected all (three) portable space heaters and returned to warehouse personally at 4:30pm. - Salvatore Marasco Jr | Please pick up all electrical portable room heaters from all Hayden and Irish Buildings and stage on the Irish B basement store room shelf unit for pick up and return to the warehouse. 2017-01-03 - 18010 - Salvatore Marasco Jr-Picked up/collected all (three) portable space heaters and returned to warehouse personally at 4:30pm. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2016-12-31 | 232356 | POLY-115842 | BILLED !! The residents bathtub is clogged and needs to be unclogged. The vent is also slightly open and leaks sometimes. The sprinkler pipe next to the entrance has also been leaking and need to be repaired. If you can repair this as soon as possible that would be greatly appreciated. Thank you.. . . | NA | BILLED !! The residents bathtub is clogged and needs to be unclogged. The vent is also slightly open and leaks sometimes. The sprinkler pipe next to the entrance has also been leaking and need to be repaired. If you can repair this as soon as possible that would be greatly appreciated. Thank you.. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-01 | 41483 | TMPE-208674 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41484 | TMPE-208673 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41485 | TMPE-208672 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41486 | TMPE-208671 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41487 | TMPE-208670 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41488 | TMPE-208669 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41489 | TMPE-208668 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 41490 | TMPE-208667 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 42520 | TMPE-207637 | Vehicle Inspection-Monthly | 2017-01-03 - xPM-VEH-M - Gail Jackson-Astro was towed to repair shop, will not start, Warren thinks maybe fuel pump. - Gail Jackson | Vehicle Inspection-Monthly 2017-01-03 - xPM-VEH-M - Gail Jackson-Astro was towed to repair shop, will not start, Warren thinks maybe fuel pump. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 2807 | WEST-108442 | HVAC-GENERAL-MA South Filters | 2017-01-05 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | HVAC-GENERAL-MA South Filters 2017-01-05 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 2808 | WEST-108441 | HVAC-GENERAL-MA North Filters | 2017-01-05 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | HVAC-GENERAL-MA North Filters 2017-01-05 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 2827 | WEST-108422 | Cooling Tower-Annual-CT-002 | 2017-01-04 - xPM-1300-A - James Spratta-Cooling Tower annual completed, new motor and gearbox installed. - James Spratta | Cooling Tower-Annual-CT-002 2017-01-04 - xPM-1300-A - James Spratta-Cooling Tower annual completed, new motor and gearbox installed. - James Spratta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 2836 | WEST-108413 | Centrifugal Pump-Quarterly-CWP-014 | 2017-01-09 - xPM-3200.09-Q - Joseph McCormick-Inboard motor grease seal has popped out of its groove. Pushed it back in as best as possible. Will get changed next time the motor is rebuilt. Pump has grease zerk fitting, but no drain plug. Sealed bearings. - Joseph McCormick; 2017-01-10 - xPM-3200.09-Q - Joseph McCormick-Test ran pump. Wiped up excess grease. Re-installed plugs. Electric readings as follows: L-L A-B 489 A-C 490 B-C 490 L-N A 283 B 284 C 284 Amps A 83.0 B 86.2 C 87.3 - Joseph McCormick | Centrifugal Pump-Quarterly-CWP-014 2017-01-09 - xPM-3200.09-Q - Joseph McCormick-Inboard motor grease seal has popped out of its groove. Pushed it back in as best as possible. Will get changed next time the motor is rebuilt. Pump has grease zerk fitting, but no drain plug. Sealed bearings. - Joseph McCormick; 2017-01-10 - xPM-3200.09-Q - Joseph McCormick-Test ran pump. Wiped up excess grease. Re-installed plugs. Electric readings as follows: L-L A-B 489 A-C 490 B-C 490 L-N A 283 B 284 C 284 Amps A 83.0 B 86.2 C 87.3 - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-01 | 2837 | WEST-108412 | Centrifugal Pump-Quarterly-CWP-013 | 2017-01-09 - xPM-3200.09-Q - Joseph McCormick-Pump 13 has no zerk fitting on pump housing. Also no drain plugs. Sealed bearings. - Joseph McCormick; 2017-01-10 - xPM-3200.09-Q - Joseph McCormick-Ran pump. Wiped up excess. Re-installed grease plugs. Electric readings as follows: L-L AB 481 AC 483 BC 484 L-N A 279 B 280 C 280 Amps A 80.8 B 85.2 C 80.8 - Joseph McCormick | Centrifugal Pump-Quarterly-CWP-013 2017-01-09 - xPM-3200.09-Q - Joseph McCormick-Pump 13 has no zerk fitting on pump housing. Also no drain plugs. Sealed bearings. - Joseph McCormick; 2017-01-10 - xPM-3200.09-Q - Joseph McCormick-Ran pump. Wiped up excess. Re-installed grease plugs. Electric readings as follows: L-L AB 481 AC 483 BC 484 L-N A 279 B 280 C 280 Amps A 80.8 B 85.2 C 80.8 - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-01 | 34704 | TMPE-215453 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34705 | TMPE-215452 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34706 | TMPE-215451 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34707 | TMPE-215450 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34708 | TMPE-215449 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34709 | TMPE-215448 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34710 | TMPE-215447 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34711 | TMPE-215446 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34712 | TMPE-215445 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34713 | TMPE-215444 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34714 | TMPE-215443 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34715 | TMPE-215442 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34716 | TMPE-215441 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 34717 | TMPE-215440 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-01 | 37441 | TMPE-212716 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-03 | 39735 | TMPE-210422 | ED 321U1 Can you create a workorder for the AC shop to look into way thus piece is tagged out? Dated 3-4-02. | 2017-01-05 - 18010 - Brian Qualls-There was once a pneumatic control leak here. Building is now on DDC. Air compressor has been removed. Complete. - Brian Qualls | ED 321U1 Can you create a workorder for the AC shop to look into way thus piece is tagged out? Dated 3-4-02. 2017-01-05 - 18010 - Brian Qualls-There was once a pneumatic control leak here. Building is now on DDC. Air compressor has been removed. Complete. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-03 | 39771 | TMPE-210386 | USB Break room 1951 Ice machine has a clogged drain line in the ice dispenser bin. Also clean and sanitize water distribution system and the ice bin. assign to Gail Jackson | 2017-01-05 - 18210 - Gail Jackson-found drain line plugged, unit will need disassembled for repair, blower with nitrogen, just made worse - Gail Jackson; 2017-01-05 - 18210 - Thomas Gibble-found drain line plugged, unit will need disassembled for repair, blower with nitrogen, just made worse - Gail Jackson; 2017-01-05 - 18210 - Gail Jackson-Removed ice pan, drain assembly, it was plugged with rotten fruit and sugar products scrubbed and disinfect, reassembled run test complete - Gail Jackson | USB Break room 1951 Ice machine has a clogged drain line in the ice dispenser bin. Also clean and sanitize water distribution system and the ice bin. assign to Gail Jackson 2017-01-05 - 18210 - Gail Jackson-found drain line plugged, unit will need disassembled for repair, blower with nitrogen, just made worse - Gail Jackson; 2017-01-05 - 18210 - Thomas Gibble-found drain line plugged, unit will need disassembled for repair, blower with nitrogen, just made worse - Gail Jackson; 2017-01-05 - 18210 - Gail Jackson-Removed ice pan, drain assembly, it was plugged with rotten fruit and sugar products scrubbed and disinfect, reassembled run test complete - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-01-03 | 39826 | TMPE-210331 | The AC unit in the Visitors' Clubhouse at Phx Muni is making a loud rumbling sound. It has been turned off to prevent further damage. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF | 2017-02-06 - 18010 - Roque Garcia-Replaced the blower assy and checked ok - Roque Garcia | The AC unit in the Visitors' Clubhouse at Phx Muni is making a loud rumbling sound. It has been turned off to prevent further damage. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF 2017-02-06 - 18010 - Roque Garcia-Replaced the blower assy and checked ok - Roque Garcia | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-03 | 39904 | TMPE-210253 | Carpentry: The roof leak in room C115 has become active once again. Please re-patch the roof. Thanks. 42C9GKG | 2017-01-12 - 13120 - Timothy Grabowski-prepped area to be sealed under cooler , sealed area with three course system , mastic , webbing &amp; mastic - Timothy Grabowski | Carpentry: The roof leak in room C115 has become active once again. Please re-patch the roof. Thanks. 42C9GKG 2017-01-12 - 13120 - Timothy Grabowski-prepped area to be sealed under cooler , sealed area with three course system , mastic , webbing &amp; mastic - Timothy Grabowski | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-03 | 39909 | TMPE-210248 | Freezer running very warm, please check today. We will be reopening the dining hall tomorrow. | 2017-01-09 - 18180 - Zhi Yu-Freezer call turn-out to be Sandwich line cooler unit "E".. We check unit is at 49deg, low on charge. We charge 3 lbs R22. No leaks were found. - Zhi Yu | Freezer running very warm, please check today. We will be reopening the dining hall tomorrow. 2017-01-09 - 18180 - Zhi Yu-Freezer call turn-out to be Sandwich line cooler unit "E".. We check unit is at 49deg, low on charge. We charge 3 lbs R22. No leaks were found. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-04 | 38874 | TMPE-211283 | Naumann Hobbs Located unit, inspected and found battery charge low. Placed unit on charger, returned and retested. Found bad rear tail light due to unplugged wire. Removed light, reattached wiring and reinstalled. Tested operations & charging system. Returned unit to service. Total: 187.59 | NA | Naumann Hobbs Located unit, inspected and found battery charge low. Placed unit on charger, returned and retested. Found bad rear tail light due to unplugged wire. Removed light, reattached wiring and reinstalled. Tested operations & charging system. Returned unit to service. Total: 187.59 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-04 | 39558 | TMPE-210599 | FAC B00U3 transfer bt to HVAC A control panel has already been shorted out and they have sent a request for the electric shop. The leak needs to be stopped first. This has been a problem in the past which is apparent from the drip pans that have been installed. This is in the museum. Contact museu. . . | 2017-01-09 - 13050 - Carl Karr-Measure for drip pan. - Carl Karr; 2017-01-09 - 13050 - Gail Jackson-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Gail Jackson-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Carl Karr-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Bhuna Nhieu-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-12 - 13050 - Carl Karr-Fabricate drip pan. - Carl Karr | FAC B00U3 transfer bt to HVAC A control panel has already been shorted out and they have sent a request for the electric shop. The leak needs to be stopped first. This has been a problem in the past which is apparent from the drip pans that have been installed. This is in the museum. Contact museu. . . 2017-01-09 - 13050 - Carl Karr-Measure for drip pan. - Carl Karr; 2017-01-09 - 13050 - Gail Jackson-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Gail Jackson-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Carl Karr-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-09 - 13050 - Bhuna Nhieu-Found H2O leaking through ceiling, rain water, will make drain pan for drips, many pans already on ceiling. - Gail Jackson; 2017-01-12 - 13050 - Carl Karr-Fabricate drip pan. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-04 | 39571 | TMPE-210586 | LL 174 I\\u2019m one of the many residents of LL 174 and our office has a loud, constant buzzing coming from the overhead vents in the office. It\\u2019s only been happening for a day or so, but it is headache-inducing torture. Can someone check it out at your earliest convenience? Thanks! | 2017-01-04 - 18010 - Donald Crowe-work in progress I found 10 inch round snap lock duct going to VAV mixing box for supply air was not properly put together and leaking air. They sealed length of pipe with one strip of duct tape which has now come loose and making high pitch squealing noise. I pressed tape down as well as possible temporarily stopping noise. I will need to order some duct tape clean pipe and reapply duct tape or get some duct sealer to put on seam. materials: warehouse duct tape or rubberized duct sealer. time .75 hours - Donald Crowe; 2017-01-09 - 18010 - Donald Crowe-completed I removed old tape from seam and then cleaned seam with wet rag then dried seam with dry rag then applied aluminum tape to seal seam. materials: warehouse duct tape - Donald Crowe | LL 174 I\\u2019m one of the many residents of LL 174 and our office has a loud, constant buzzing coming from the overhead vents in the office. It\\u2019s only been happening for a day or so, but it is headache-inducing torture. Can someone check it out at your earliest convenience? Thanks! 2017-01-04 - 18010 - Donald Crowe-work in progress I found 10 inch round snap lock duct going to VAV mixing box for supply air was not properly put together and leaking air. They sealed length of pipe with one strip of duct tape which has now come loose and making high pitch squealing noise. I pressed tape down as well as possible temporarily stopping noise. I will need to order some duct tape clean pipe and reapply duct tape or get some duct sealer to put on seam. materials: warehouse duct tape or rubberized duct sealer. time .75 hours - Donald Crowe; 2017-01-09 - 18010 - Donald Crowe-completed I removed old tape from seam and then cleaned seam with wet rag then dried seam with dry rag then applied aluminum tape to seal seam. materials: warehouse duct tape - Donald Crowe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5
2017-01-04 | 39592 | TMPE-210565 | MU 126 We are scheduling to have the kitchens steam cleaned on Friday (Jan. 6) from 2am \\u2013 6am. We will be concentrating our time in the bakery and main cook line in the main kitchen on the first floor of the MU Building. Would it be possible to de-activate the detectors in this area while th. . . | 2017-01-06 - 17000 - Due to technical issue with the steam cleaning equipment the scheduled cleaning will be postponed until spring break. - Charles Daprato | MU 126 We are scheduling to have the kitchens steam cleaned on Friday (Jan. 6) from 2am \\u2013 6am. We will be concentrating our time in the bakery and main cook line in the main kitchen on the first floor of the MU Building. Would it be possible to de-activate the detectors in this area while th. . . 2017-01-06 - 17000 - Due to technical issue with the steam cleaning equipment the scheduled cleaning will be postponed until spring break. - Charles Daprato | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-04 | 39679 | TMPE-210478 | PSF F12 URGENT, please place a portable ac unit in this area asap per mike cozens. Thank you! | 2017-02-01 - 18010 - Jennifer Moyer-Portable unit M85-1003 installed. - Jennifer Moyer | PSF F12 URGENT, please place a portable ac unit in this area asap per mike cozens. Thank you! 2017-02-01 - 18010 - Jennifer Moyer-Portable unit M85-1003 installed. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-04 | 39699 | TMPE-210458 | Oner Munoz 03/09/2017 14:20 - USB 2466 Bruce Nevels office is far too cold, please make an urgent adjustment. Thank you! | 2017-01-04 - 18300 - Mitchell Andrews-unit was low on charge couldn't find leak at the time...gased the unit to proper charge - Mitchell Andrews; 2017-01-09 - 18300 - SENT EMAIL TO HVAC. NANCY GRAF SAID IT'S STILL VERY COLD. MM - Monica Moraga; 2017-01-10 - 18300 - Mitchell Andrews-We arrived at the unit. The system completely flat. We pressurized with nitrogen and found 2 leaks. one at the branch connection and other on the TXV capillary tube. We repair connection and replaced TXV Power head. Pressurized again for leaks and vacuum unit to 500 micron. We Charge to manufacture spec. 6.6 lbs R410a.. - Zhi Yu; 2017-01-10 - 18300 - Zhi Yu-We arrived at the unit. The system completely flat. We pressurized with nitrogen and found 2 leaks. one at the branch connection and other on the TXV capillary tube. We repair connection and replaced TXV Power head. Pressurized again for leaks and vacuum unit to 500 micron. We Charge to manufacture spec. 6.6 lbs R410a.. - Zhi Yu | Oner Munoz 03/09/2017 14:20 - USB 2466 Bruce Nevels office is far too cold, please make an urgent adjustment. Thank you! 2017-01-04 - 18300 - Mitchell Andrews-unit was low on charge couldn't find leak at the time...gased the unit to proper charge - Mitchell Andrews; 2017-01-09 - 18300 - SENT EMAIL TO HVAC. NANCY GRAF SAID IT'S STILL VERY COLD. MM - Monica Moraga; 2017-01-10 - 18300 - Mitchell Andrews-We arrived at the unit. The system completely flat. We pressurized with nitrogen and found 2 leaks. one at the branch connection and other on the TXV capillary tube. We repair connection and replaced TXV Power head. Pressurized again for leaks and vacuum unit to 500 micron. We Charge to manufacture spec. 6.6 lbs R410a.. - Zhi Yu; 2017-01-10 - 18300 - Zhi Yu-We arrived at the unit. The system completely flat. We pressurized with nitrogen and found 2 leaks. one at the branch connection and other on the TXV capillary tube. We repair connection and replaced TXV Power head. Pressurized again for leaks and vacuum unit to 500 micron. We Charge to manufacture spec. 6.6 lbs R410a.. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-04 | 170797 | RFMT-137534 | Air conditioner and controls aren't working. I can't turn on the air or heat, on any level. Hasn't worked in 2 days/ 4NK3GNI | 2017-01-04 - 18010 - Casey Faultner-Investigated control issues for the heating and cooling system. Found a loose connects in the wiring harness. Tightened connection and corrected the issue. Everything working normal at this time. - Casey Faultner | Air conditioner and controls aren't working. I can't turn on the air or heat, on any level. Hasn't worked in 2 days/ 4NK3GNI 2017-01-04 - 18010 - Casey Faultner-Investigated control issues for the heating and cooling system. Found a loose connects in the wiring harness. Tightened connection and corrected the issue. Everything working normal at this time. - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-04 | 170815 | RFMT-137516 | Please inspect heat in Cluster D's chapter room. Cold air blows out of vents though heat is on. Residents have let it run for approx 2 hours and indicated it was still blowing cold air. Thanks, Carli 4NF4L2O | 2017-01-05 - 18300 - David Cates-Air coming out of vent at 53 degrees. Motor is still working. Talked to Greg about having Thor and Simon check the issue. - David Cates; 2017-01-06 - 18300 - David Cates-Thor and Simon resolved issue by rewiring the reversing valve - David Cates | Please inspect heat in Cluster D's chapter room. Cold air blows out of vents though heat is on. Residents have let it run for approx 2 hours and indicated it was still blowing cold air. Thanks, Carli 4NF4L2O 2017-01-05 - 18300 - David Cates-Air coming out of vent at 53 degrees. Motor is still working. Talked to Greg about having Thor and Simon check the issue. - David Cates; 2017-01-06 - 18300 - David Cates-Thor and Simon resolved issue by rewiring the reversing valve - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-01-04 | 213250 | RACC-115360 | !! The air conditioner when turned on smells smokey. The resident believes there may be something wrong with the electrical wire in the vents. Please check soon. Contact Name: Zesong Guo Contact Phone Number: Contact Email: zguo55@asu.edu 4NKA28O | NA | !! The air conditioner when turned on smells smokey. The resident believes there may be something wrong with the electrical wire in the vents. Please check soon. Contact Name: Zesong Guo Contact Phone Number: Contact Email: zguo55@asu.edu 4NKA28O NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-04 | 232295 | POLY-115903 | !! The fan in the kitchen ventilation system isnt working properly. Contact Name: Contact Phone Number: 6024059549 Contact Email: 4NJDDHD | NA | !! The fan in the kitchen ventilation system isnt working properly. Contact Name: Contact Phone Number: 6024059549 Contact Email: 4NJDDHD NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-05 | 39289 | TMPE-210868 | !! Hayden Library - 4th floor - Room #434 (Staff Lounge) - Refrigerator Refrigerator is still leaking. The issue has not been resolved. Staff is putting paper to soak the water. Please send someone to fix it. Thank you. Shirin 4MNA207 | 2017-02-06 - 18240 - Roque Garcia-Repaired refrigerator and tested ok - Roque Garcia | !! Hayden Library - 4th floor - Room #434 (Staff Lounge) - Refrigerator Refrigerator is still leaking. The issue has not been resolved. Staff is putting paper to soak the water. Please send someone to fix it. Thank you. Shirin 4MNA207 2017-02-06 - 18240 - Roque Garcia-Repaired refrigerator and tested ok - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-05 | 39413 | TMPE-210744 | Tracy Brown (USB 1150C; 7-7747) and Vanessa Helfrey (USB 1150B; 7-6420) would like to have the diffuser (ceiling vent deflector) put back up. When the air comes on, it blows right on Tracy and Vanessa. It gets very, very cold. Please have HVAC check this out. Thanks. 42BFDCH | 2017-01-10 - 18300 - Jennifer Moyer-Install temporary deflector. - Jennifer Moyer; 2017-01-17 - 18300 - Carl Karr-Created diffusers. - Jennifer Moyer | Tracy Brown (USB 1150C; 7-7747) and Vanessa Helfrey (USB 1150B; 7-6420) would like to have the diffuser (ceiling vent deflector) put back up. When the air comes on, it blows right on Tracy and Vanessa. It gets very, very cold. Please have HVAC check this out. Thanks. 42BFDCH 2017-01-10 - 18300 - Jennifer Moyer-Install temporary deflector. - Jennifer Moyer; 2017-01-17 - 18300 - Carl Karr-Created diffusers. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-05 | 170733 | RFMT-137598 | I have my A/C on cool and it is only blowing hot air 4NJD9JJ | 2017-01-05 - 18010 - Gabriel Figueroa-Ran a/c unit on cool for awhile, checked actuators on unit. All are working fine, a/c temp started dropping after it running awhile. Last temp reading at the vent was 67 degrees and dropping. Left unit running. - Gabriel Figueroa | I have my A/C on cool and it is only blowing hot air 4NJD9JJ 2017-01-05 - 18010 - Gabriel Figueroa-Ran a/c unit on cool for awhile, checked actuators on unit. All are working fine, a/c temp started dropping after it running awhile. Last temp reading at the vent was 67 degrees and dropping. Left unit running. - Gabriel Figueroa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-05 | 232253 | POLY-115945 | send 2 people to compressor service class 4O216EO | 2017-01-17 - 10140 - Allan Blair-attended class - Steve Clark; 2017-01-17 - 10140 - Suresh Nair-attended class - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark | send 2 people to compressor service class 4O216EO 2017-01-17 - 10140 - Allan Blair-attended class - Steve Clark; 2017-01-17 - 10140 - Suresh Nair-attended class - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Allan Blair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark; 2017-01-19 - 10140 - Suresh Nair-AT CLASS - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-06 | 39230 | TMPE-210927 | FCA important safety recall driver airbag inflator. the driver airbag inflator housing in your vehicle may rupture, due to excessive internal pressure, during normal airbag deployment events. This condition is more likely to occur if your vehicle has been exposed to high levels of absolute humidi. . . | NA | FCA important safety recall driver airbag inflator. the driver airbag inflator housing in your vehicle may rupture, due to excessive internal pressure, during normal airbag deployment events. This condition is more likely to occur if your vehicle has been exposed to high levels of absolute humidi. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-06 | 39238 | TMPE-210919 | LSC 588 HVAC-Please initiate coordinating work orders for the Plumbing and HVAC Shops for work as follows in LSC 588: move existing lines for an old ice machine from the east wall to the south wall for a new ice machine. The new machine is in at the ASU main receiving dock. Please schedule HVAC. . . | 2017-01-13 - 18210 - Gail Jackson-Remove old ice machine and filter system, transport to shop. Recover refrigerant. Trip to ACE, ARS and warehouse for parts. - Gail Jackson; 2017-01-13 - 18210 - Thomas Gibble-Remove old ice machine and filter system, transport to shop. Recover refrigerant. Trip to ACE, ARS and warehouse for parts. Transport new machine to Life C room 588. - Gail Jackson; 2017-01-13 - 18210 - Gail Jackson-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson; 2017-01-13 - 18210 - Thomas Gibble-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson; 2017-01-13 - 18210 - Robert Dauscher-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson | LSC 588 HVAC-Please initiate coordinating work orders for the Plumbing and HVAC Shops for work as follows in LSC 588: move existing lines for an old ice machine from the east wall to the south wall for a new ice machine. The new machine is in at the ASU main receiving dock. Please schedule HVAC. . . 2017-01-13 - 18210 - Gail Jackson-Remove old ice machine and filter system, transport to shop. Recover refrigerant. Trip to ACE, ARS and warehouse for parts. - Gail Jackson; 2017-01-13 - 18210 - Thomas Gibble-Remove old ice machine and filter system, transport to shop. Recover refrigerant. Trip to ACE, ARS and warehouse for parts. Transport new machine to Life C room 588. - Gail Jackson; 2017-01-13 - 18210 - Gail Jackson-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson; 2017-01-13 - 18210 - Thomas Gibble-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson; 2017-01-13 - 18210 - Robert Dauscher-Install new filter, water lime and drain line, hook up electrical. Run test, COMPLETE. Trip to warehouse for drain line parts. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-06 | 39291 | TMPE-210866 | Clean air vents in the graduate office, multiple vents in our office are dropping dust. 231 is the worst, but if you can clean the air vents in the entire office that would be much appreciated! Thank you! 4O5LJ57 | 2017-02-27 - 18010 - Jennifer Moyer-Spoke with Margaret about the issue, examined area, and left a message with requester. Margaret suggested that I speak with Mr. Luczak regarding the filters. - Jennifer Moyer; 2017-03-06 - 18010 - Jennifer Moyer-This building was added to the filter crew schedule to address the problem. Voicemail left on requestor's phone addressing the work order. - Jennifer Moyer | Clean air vents in the graduate office, multiple vents in our office are dropping dust. 231 is the worst, but if you can clean the air vents in the entire office that would be much appreciated! Thank you! 4O5LJ57 2017-02-27 - 18010 - Jennifer Moyer-Spoke with Margaret about the issue, examined area, and left a message with requester. Margaret suggested that I speak with Mr. Luczak regarding the filters. - Jennifer Moyer; 2017-03-06 - 18010 - Jennifer Moyer-This building was added to the filter crew schedule to address the problem. Voicemail left on requestor's phone addressing the work order. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-07 | 150519 | RNLD-100782 | !! Dust coming out of AC. Needs to be cleaned and checked. Contact Name: ryan bodhipaksha Contact Phone Number: 4807472485 Contact Email: rbodhipa@asu.edu 4NG86IJ | 2017-01-26 - 18010 - Allan Blair-1/9 - Esli, Darusman an Allan cleaned filter, and checked system. - Gayle Swenson | !! Dust coming out of AC. Needs to be cleaned and checked. Contact Name: ryan bodhipaksha Contact Phone Number: 4807472485 Contact Email: rbodhipa@asu.edu 4NG86IJ 2017-01-26 - 18010 - Allan Blair-1/9 - Esli, Darusman an Allan cleaned filter, and checked system. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-07 | 170530 | RFMT-137801 | ASUHC-Agent: Spencer Leisy Description: The AC/Heat system is not working in room 107, room is very cold. Who was dispatched: Joe Swan Time of dispatch: 19:57 | 2017-01-09 - 18010 - Joe Swan-Found that heater had a bad blower motor occupant was ok with room until Monday to be fixed - Joe Swan | ASUHC-Agent: Spencer Leisy Description: The AC/Heat system is not working in room 107, room is very cold. Who was dispatched: Joe Swan Time of dispatch: 19:57 2017-01-09 - 18010 - Joe Swan-Found that heater had a bad blower motor occupant was ok with room until Monday to be fixed - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-07 | 213078 | RACC-115532 | !! Air conditioning unit is leaking. 4NO84L4 | NA | !! Air conditioning unit is leaking. 4NO84L4 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-07 | 213183 | RACC-115427 | Fan is broken. Shakes and makes noise when on. 4NMC4F4 | NA | Fan is broken. Shakes and makes noise when on. 4NMC4F4 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-08 | 41245 | TMPE-208912 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 41256 | TMPE-208901 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 42188 | TMPE-207969 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 42189 | TMPE-207968 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 42190 | TMPE-207967 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 42191 | TMPE-207966 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-08 | 170405 | RFMT-137926 | new air filter 4O0GI79 | 2017-01-12 - 18170 - Mike Guckian-new filter. - Mike Guckian | new air filter 4O0GI79 2017-01-12 - 18170 - Mike Guckian-new filter. - Mike Guckian | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-08 | 170489 | RFMT-137842 | !! There is an air conditioning problem. It makes a crackling noise and no air is coming out. It is pretty warm in the room as well. Contact Name: Contact Phone Number: 8057489287 Contact Email: 4NNODH8 | 2017-01-11 - 18010 - Eric Miller-Pulled motor, bench checked motor re-installed motor and new thermostat. - Eric Miller | !! There is an air conditioning problem. It makes a crackling noise and no air is coming out. It is pretty warm in the room as well. Contact Name: Contact Phone Number: 8057489287 Contact Email: 4NNODH8 2017-01-11 - 18010 - Eric Miller-Pulled motor, bench checked motor re-installed motor and new thermostat. - Eric Miller | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-08 | 213066 | RACC-115544 | !! AC/Heating unit makes buzzing noise 24/7 and the heater does not work at all, please fix the heater and buzzing. 4O047CD | NA | !! AC/Heating unit makes buzzing noise 24/7 and the heater does not work at all, please fix the heater and buzzing. 4O047CD NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-09 | 38951 | TMPE-211206 | HAV POD MARKET the strip of lights in front of the freezer are all out | 2017-01-13 - 15040 - Zhi Yu-I responded to the job. All the ceiling Track-light not working. HVAC transfer to Electrician. - Zhi Yu | HAV POD MARKET the strip of lights in front of the freezer are all out 2017-01-13 - 15040 - Zhi Yu-I responded to the job. All the ceiling Track-light not working. HVAC transfer to Electrician. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-09 | 38954 | TMPE-211203 | HAV POD MARKET Can you create a work order to see what is wrong with the freezer inside the Hassayampa POD MARKET It is currently down | 2017-01-13 - 18180 - Zhi Yu-I spoke to JIM. Ecolab is working on their 4dr freezer. - Zhi Yu | HAV POD MARKET Can you create a work order to see what is wrong with the freezer inside the Hassayampa POD MARKET It is currently down 2017-01-13 - 18180 - Zhi Yu-I spoke to JIM. Ecolab is working on their 4dr freezer. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-09 | 38964 | TMPE-211193 | ASUHC-Agent: Kyle Green Description: Large puddle of water accumulated under refrigerators/Ice Maker, leaking into the other side of the wall into the carpets. Who was dispatched: Olympus/Plumber Time of dispatch: 20:42/20:50 ASUHC-Agent: Kyle Green Time: 21:00-22:00 - Olympus came out. . . | 2017-01-11 - 18210 - Thomas Gibble-picked up parts from two parts stores. - Thomas Gibble; 2017-01-11 - 18210 - Gail Jackson-picked up parts from two parts stores. - Thomas Gibble; 2017-01-11 - 18210 - Gail Jackson-Found purge valve, H2O valve, condensate pump burned out, discharge line PLUGGED , dirty ice machine and dirty filters. Replaced all parts as needed, cleaned and run tested. COMPLETE. notified PLUMBERS ABOUT PLUGGED DRAIN LINE. - Gail Jackson; 2017-01-11 - 18210 - Thomas Gibble-Found purge valve, H2O valve, condensate pump burned out, discharge line PLUGGED , dirty ice machine and dirty filters. Replaced all parts as needed, cleaned and run tested. COMPLETE. notified PLUMBERS ABOUT PLUGGED DRAIN LINE. - Gail Jackson | ASUHC-Agent: Kyle Green Description: Large puddle of water accumulated under refrigerators/Ice Maker, leaking into the other side of the wall into the carpets. Who was dispatched: Olympus/Plumber Time of dispatch: 20:42/20:50 ASUHC-Agent: Kyle Green Time: 21:00-22:00 - Olympus came out. . . 2017-01-11 - 18210 - Thomas Gibble-picked up parts from two parts stores. - Thomas Gibble; 2017-01-11 - 18210 - Gail Jackson-picked up parts from two parts stores. - Thomas Gibble; 2017-01-11 - 18210 - Gail Jackson-Found purge valve, H2O valve, condensate pump burned out, discharge line PLUGGED , dirty ice machine and dirty filters. Replaced all parts as needed, cleaned and run tested. COMPLETE. notified PLUMBERS ABOUT PLUGGED DRAIN LINE. - Gail Jackson; 2017-01-11 - 18210 - Thomas Gibble-Found purge valve, H2O valve, condensate pump burned out, discharge line PLUGGED , dirty ice machine and dirty filters. Replaced all parts as needed, cleaned and run tested. COMPLETE. notified PLUMBERS ABOUT PLUGGED DRAIN LINE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-01-09 | 38984 | TMPE-211173 | sump pump is seized not working | 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-16 - 23100 - Derek Gittings-replaced pump. - Derek Gittings; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-remove pump,re pipe new pump/motor/float.adjust float,clean EQ room.pump running ok. - Jose Lopez | sump pump is seized not working 2017-01-25 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-16 - 23100 - Derek Gittings-replaced pump. - Derek Gittings; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-remove pump,re pipe new pump/motor/float.adjust float,clean EQ room.pump running ok. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-09 | 39013 | TMPE-211144 | Please initiate a work order for HVAC to PM a Thermo Fisher -80 freezer in ISTB1 room 353K (Model Number ULT1490-5-A34 , Ser #1194). The unit is currently off, thoroughly defrosted and ready for PM at the earliest opportunity. All charges for this request may be billed to PO #LM502001099. Thank. . . | 2017-01-19 - 18180 - Zhi Yu-we clean filter check start cap and run cap. the runcap low on tolerance and door inner gasket torn need replacement.. - Zhi Yu; 2017-02-01 - 18180 - Zhi Yu-Removed old gasket and install New gasket. also replaced 2 40mfd capacitor. we silicone all 4 corner. - Zhi Yu; 2017-02-27 - 18180 - Zhi Yu-We have and estimate to repair. - Zhi Yu | Please initiate a work order for HVAC to PM a Thermo Fisher -80 freezer in ISTB1 room 353K (Model Number ULT1490-5-A34 , Ser #1194). The unit is currently off, thoroughly defrosted and ready for PM at the earliest opportunity. All charges for this request may be billed to PO #LM502001099. Thank. . . 2017-01-19 - 18180 - Zhi Yu-we clean filter check start cap and run cap. the runcap low on tolerance and door inner gasket torn need replacement.. - Zhi Yu; 2017-02-01 - 18180 - Zhi Yu-Removed old gasket and install New gasket. also replaced 2 40mfd capacitor. we silicone all 4 corner. - Zhi Yu; 2017-02-27 - 18180 - Zhi Yu-We have and estimate to repair. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-09 | 39048 | TMPE-211109 | LL BASEMENT Transferred call to HVAC - Air compressor is going in and out of alarm every minute. Creating hot calls. EMS WO#210853, HVAC WO#211109. Please adjust the temperature. The south wing of the basement is very hot! | 2017-01-09 - 18030 - Brian Qualls-Checked both compressors for building. Both operating per specs. Auto drains working correctly. No heaters tripped. Nut and bolted north wing starters. Checked contact blocks, OK. - Brian Qualls | LL BASEMENT Transferred call to HVAC - Air compressor is going in and out of alarm every minute. Creating hot calls. EMS WO#210853, HVAC WO#211109. Please adjust the temperature. The south wing of the basement is very hot! 2017-01-09 - 18030 - Brian Qualls-Checked both compressors for building. Both operating per specs. Auto drains working correctly. No heaters tripped. Nut and bolted north wing starters. Checked contact blocks, OK. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-01-09 | 39053 | TMPE-211104 | !! One sewage ejection pump in EQ 82 will not start - Y6066 PU2. It was in overtemperature alarm. Reset okay, but would not run - locked rotor. Please check. 42AI0GO | 2017-02-09 - 23100 - Derek Gittings-pull underwear out of impeler - Derek Gittings | !! One sewage ejection pump in EQ 82 will not start - Y6066 PU2. It was in overtemperature alarm. Reset okay, but would not run - locked rotor. Please check. 42AI0GO 2017-02-09 - 23100 - Derek Gittings-pull underwear out of impeler - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-01-09 | 170366 | RFMT-137965 | !! Heat is not working 4NL564O | 2017-01-10 - 18010 - Chester Duncan-Heat supply stop was shut off Turned it on: system blowing good hot air *** Stop only opened part way and operation was not smooth. Did not see any leaking. *** - Chester Duncan | !! Heat is not working 4NL564O 2017-01-10 - 18010 - Chester Duncan-Heat supply stop was shut off Turned it on: system blowing good hot air *** Stop only opened part way and operation was not smooth. Did not see any leaking. *** - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-09 | 170418 | RFMT-137913 | The A/C unit makes a weird noise (not all the time) but it sounds like some sort of leaking noise like air is coming out of something and making a blowing sound that is not normal. 4NHJOLE | 2017-01-10 - 18010 - Scott Berndt-a/c working fine and found no noises - Scott Berndt | The A/C unit makes a weird noise (not all the time) but it sounds like some sort of leaking noise like air is coming out of something and making a blowing sound that is not normal. 4NHJOLE 2017-01-10 - 18010 - Scott Berndt-a/c working fine and found no noises - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-09 | 170447 | RFMT-137884 | Please check the fan coil blower motor in Irish C 107. | 2017-01-09 - 18010 - Salvatore Marasco Jr-Rebuilt blower assembly and motor. - Salvatore Marasco Jr | Please check the fan coil blower motor in Irish C 107. 2017-01-09 - 18010 - Salvatore Marasco Jr-Rebuilt blower assembly and motor. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-09 | 212960 | RACC-115650 | !! Air conditioning broken, it's very hot and no cold air comes out of the vents or even air. 4O0C3BO | NA | !! Air conditioning broken, it's very hot and no cold air comes out of the vents or even air. 4O0C3BO NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-09 | 2655 | WEST-108594 | A call about "knocking noises"from the ceiling. | 2017-01-09 - 18010 - Alfred Rohe-Found a slight knocking noise. Will have to access ceiling so I will return tomorrow when the customer is not going to be there.Customer agrees. - Alfred Rohe; 2017-01-12 - 18010 - Alfred Rohe-Chad B. and I have made three return trips in an attempt to locate the source of the noise. The noise is slight and difficult to hear and with the heat fan running the knocking noise can not be heard. Will continue to investigate. - Alfred Rohe; 2017-01-24 - 18010 - Alfred Rohe-After making several calls it was determined that the slight noise is coming from AHU#2. This unit has a new motor-just installed-and new belts. There is nothing to do to make it better. The noise is not detectable when the heat is on, only when the air handler is running between 30 and 40 HZ. without heat. - Alfred Rohe; 2017-01-24 - 18010 - Chad T Ball-Assisted with checking the system. Was not able to hear sound that the customer was complaining about.Assisted with attic work. - Alfred Rohe | A call about "knocking noises"from the ceiling. 2017-01-09 - 18010 - Alfred Rohe-Found a slight knocking noise. Will have to access ceiling so I will return tomorrow when the customer is not going to be there.Customer agrees. - Alfred Rohe; 2017-01-12 - 18010 - Alfred Rohe-Chad B. and I have made three return trips in an attempt to locate the source of the noise. The noise is slight and difficult to hear and with the heat fan running the knocking noise can not be heard. Will continue to investigate. - Alfred Rohe; 2017-01-24 - 18010 - Alfred Rohe-After making several calls it was determined that the slight noise is coming from AHU#2. This unit has a new motor-just installed-and new belts. There is nothing to do to make it better. The noise is not detectable when the heat is on, only when the air handler is running between 30 and 40 HZ. without heat. - Alfred Rohe; 2017-01-24 - 18010 - Chad T Ball-Assisted with checking the system. Was not able to hear sound that the customer was complaining about.Assisted with attic work. - Alfred Rohe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-10 | 38820 | TMPE-211337 | MU POD Market The ice cream freezer is not staying at temp. It does not go below 20 | 2017-05-11 - 18180 - Roque Garcia-Replaced the compressor and unit working - Roque Garcia | MU POD Market The ice cream freezer is not staying at temp. It does not go below 20 2017-05-11 - 18180 - Roque Garcia-Replaced the compressor and unit working - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-10 | 38869 | TMPE-211288 | !! ELECTRICAL fuse box: EF-1 exhaust fan in ECF 103 is not working. EF-3 was working all day yesterday but it wont turn on this morning. Terry Martin changed out the fuses to EF-3 and EF-2 last week on work order number TMPE-210767. Please send someone from the electrical shop to change out fuse. . . | 2017-01-10 - 15000 - Semeon Haile-troubleshoot and repaired starter - Semeon Haile | !! ELECTRICAL fuse box: EF-1 exhaust fan in ECF 103 is not working. EF-3 was working all day yesterday but it wont turn on this morning. Terry Martin changed out the fuses to EF-3 and EF-2 last week on work order number TMPE-210767. Please send someone from the electrical shop to change out fuse. . . 2017-01-10 - 15000 - Semeon Haile-troubleshoot and repaired starter - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-10 | 170152 | RFMT-138179 | ASUHC-Agent Jesse Tannous Description AC blowing hot air only Who was dispatched Joe Swan Time of dispatch 630pm | 2017-01-11 - 18010 - Casey Faultner-Follow up on a call that Joe Swan had the night before. The A/C unit needed to have the heat and cooling selector valve exercised. Everything is working normal at this time. - Casey Faultner; 2017-01-11 - 18010 - Scott Berndt-Follow up on a call that Joe Swan had the night before. The A/C unit needed to have the heat and cooling selector valve exercised. Everything is working normal at this time. - Casey Faultner; 2017-01-11 - 18010 - Joe Swan-Check on A/C unit and going to let the day shift take care of issue. - Casey Faultner | ASUHC-Agent Jesse Tannous Description AC blowing hot air only Who was dispatched Joe Swan Time of dispatch 630pm 2017-01-11 - 18010 - Casey Faultner-Follow up on a call that Joe Swan had the night before. The A/C unit needed to have the heat and cooling selector valve exercised. Everything is working normal at this time. - Casey Faultner; 2017-01-11 - 18010 - Scott Berndt-Follow up on a call that Joe Swan had the night before. The A/C unit needed to have the heat and cooling selector valve exercised. Everything is working normal at this time. - Casey Faultner; 2017-01-11 - 18010 - Joe Swan-Check on A/C unit and going to let the day shift take care of issue. - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-01-10 | 170157 | RFMT-138174 | HC Agent: Matthew Briggs Issue: Water leak from AC Vent in room Who was dispatched: Joe Swan Time of dispatch: 6:07 PM | 2017-01-11 - 18010 - Joe Swan-Tried to get up in A/C unit to find leak but was unable to get to area were leak was with out pulling blower and drip pan out. Placed trash can under leak until day shift can fix it. - Joe Swan | HC Agent: Matthew Briggs Issue: Water leak from AC Vent in room Who was dispatched: Joe Swan Time of dispatch: 6:07 PM 2017-01-11 - 18010 - Joe Swan-Tried to get up in A/C unit to find leak but was unable to get to area were leak was with out pulling blower and drip pan out. Placed trash can under leak until day shift can fix it. - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-10 | 170158 | RFMT-138173 | ASU HC Agent: Amanda Kennedy Description: Room is extremely hot, stating air conditioning not working Time of dispatch: 5:53pm Who was dispatched: Joe Swan | 2017-01-11 - 18010 - Joe Swan-Found that A/C unit had bad blower motor. turned over to Dale to be replaced - Joe Swan | ASU HC Agent: Amanda Kennedy Description: Room is extremely hot, stating air conditioning not working Time of dispatch: 5:53pm Who was dispatched: Joe Swan 2017-01-11 - 18010 - Joe Swan-Found that A/C unit had bad blower motor. turned over to Dale to be replaced - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-10 | 170166 | RFMT-138165 | !! The AC is not working in this room. Please fix asap Submitted by 4O077C3 | 2017-01-11 - 18010 - Casey Faultner-Follow up from Joe Swan the night before. Found the blower motor was burnt out. Removed and cleaned the housing, squirrel cage and installed new blower motor. We used a HC/00209 Blower motor. There is no blower motors in the inventory to take it from. - Casey Faultner; 2017-01-11 - 18010 - Scott Berndt-Follow up from Joe Swan the night before. Found the blower motor was burnt out. Removed and cleaned the housing, squirrel cage and installed new blower motor. - Casey Faultner; 2017-01-11 - 18010 - Joe Swan-Checked out the issue and sent it to the day time guys to fix the problem. - Casey Faultner | !! The AC is not working in this room. Please fix asap Submitted by 4O077C3 2017-01-11 - 18010 - Casey Faultner-Follow up from Joe Swan the night before. Found the blower motor was burnt out. Removed and cleaned the housing, squirrel cage and installed new blower motor. We used a HC/00209 Blower motor. There is no blower motors in the inventory to take it from. - Casey Faultner; 2017-01-11 - 18010 - Scott Berndt-Follow up from Joe Swan the night before. Found the blower motor was burnt out. Removed and cleaned the housing, squirrel cage and installed new blower motor. - Casey Faultner; 2017-01-11 - 18010 - Joe Swan-Checked out the issue and sent it to the day time guys to fix the problem. - Casey Faultner | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-10 | 170184 | RFMT-138147 | !! the lightbulbs in our light are flickering/out and need to be replaced also the AC isn't working very well the room is warm and stuffy. Contact Name: Andrew Contact Phone Number: 4049014416 Contact Email: 4O018EO | 2017-01-12 - 15040 - Russell Peterson-CAR 1. replace 2- 13watt 2pin. 2. room temp 74 - vent 75 called supervisor. - Russell Peterson | !! the lightbulbs in our light are flickering/out and need to be replaced also the AC isn't working very well the room is warm and stuffy. Contact Name: Andrew Contact Phone Number: 4049014416 Contact Email: 4O018EO 2017-01-12 - 15040 - Russell Peterson-CAR 1. replace 2- 13watt 2pin. 2. room temp 74 - vent 75 called supervisor. - Russell Peterson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-10 | 170194 | RFMT-138137 | !! There is an air conditioning problem. It makes a crackling noise and no air is coming out. It is pretty warm in the room as well. Contact Name: Contact Phone Number: 8057489287 Contact Email: 4NNODH8 | 2017-01-10 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | !! There is an air conditioning problem. It makes a crackling noise and no air is coming out. It is pretty warm in the room as well. Contact Name: Contact Phone Number: 8057489287 Contact Email: 4NNODH8 2017-01-10 - 18010 - Thor Millsaps-Replaced thermostat. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-10 | 170269 | RFMT-138062 | !! It appears our heater is on and it just keeps going and going and hasn't stopped all night. All of us complained it was ridiculously hot last night. So this morning at 8am I looked at the thermometer, which read it is 80 degrees in here, but the AC and heater was turned off. We just need somebody. . . | 2017-01-10 - 18010 - Gabriel Figueroa-Room vent at 89 degrees. Chillers where down to blding so no cooling. Checked later and a/c unit is cooling now - Gabriel Figueroa | !! It appears our heater is on and it just keeps going and going and hasn't stopped all night. All of us complained it was ridiculously hot last night. So this morning at 8am I looked at the thermometer, which read it is 80 degrees in here, but the AC and heater was turned off. We just need somebody. . . 2017-01-10 - 18010 - Gabriel Figueroa-Room vent at 89 degrees. Chillers where down to blding so no cooling. Checked later and a/c unit is cooling now - Gabriel Figueroa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-10 | 170271 | RFMT-138060 | Please check the A/C on the roof at San Pablo on the west end | 2017-01-10 - 18010 - John Romero-Checked out unit and is not running. Advised Simon of the situation and he took a look at it and advised that need to replace the fuses, will need to order... Need to send to Simon - John Romero | Please check the A/C on the roof at San Pablo on the west end 2017-01-10 - 18010 - John Romero-Checked out unit and is not running. Advised Simon of the situation and he took a look at it and advised that need to replace the fuses, will need to order... Need to send to Simon - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-10 | 170277 | RFMT-138054 | !! It's too hot in the dorms. I'm waking up in the middle of the night because of how hot it is. It is so uncomfortable. 4NC9C11 | 2017-01-10 - 18010 - Gabriel Figueroa-Ran a/c on cool for awhile and it dropped to 88 degrees. Checked chillers in EQ and both where off. Called Stetka to have a/c techs go and start chillers back up. Also informed Stetka that the acuators for a/c units wern't moving. To have them replaced - Gabriel Figueroa | !! It's too hot in the dorms. I'm waking up in the middle of the night because of how hot it is. It is so uncomfortable. 4NC9C11 2017-01-10 - 18010 - Gabriel Figueroa-Ran a/c on cool for awhile and it dropped to 88 degrees. Checked chillers in EQ and both where off. Called Stetka to have a/c techs go and start chillers back up. Also informed Stetka that the acuators for a/c units wern't moving. To have them replaced - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-10 | 212948 | RACC-115662 | !! My apartment smells. It has smelled for a while. I can't seem to find the location of the smell. But it is pretty much my entire house. Theres kind of a musty smell. I feel like it must be mold or mildew. I can't find the source. I keep my house pretty clean and through away my trash pretty regul. . . | 2017-01-12 - 10010 - inspected apartment and found no signs of mold . Inspected A/C duct , Under all sink . behind tubs, Washer and dryer, Found no signs of mildew or mold Richard - Jim Deal | !! My apartment smells. It has smelled for a while. I can't seem to find the location of the smell. But it is pretty much my entire house. Theres kind of a musty smell. I feel like it must be mold or mildew. I can't find the source. I keep my house pretty clean and through away my trash pretty regul. . . 2017-01-12 - 10010 - inspected apartment and found no signs of mold . Inspected A/C duct , Under all sink . behind tubs, Washer and dryer, Found no signs of mildew or mold Richard - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-01-11 | 38563 | TMPE-211594 | INTDSA HALLWAY OUTSIDE OF A111 The air handler just started making a very loud noise. Please send someone from HVAC to check it out. | 2017-01-11 - 18050 - CALLED TO BRIAN Q. - Monica Moraga; 2017-01-12 - 18050 - Zhi Yu-We diagnose unit blowing wheel bearing shaft wear out. - Zhi Yu; 2017-01-13 - 18050 - Zhi Yu-Removed the blower house and bring back to shop. - Zhi Yu; 2017-01-19 - 18050 - Zhi Yu-retrofit to direct drive. we replaced 1/3 hp 115 volt., blower wheel and cap. - Zhi Yu | INTDSA HALLWAY OUTSIDE OF A111 The air handler just started making a very loud noise. Please send someone from HVAC to check it out. 2017-01-11 - 18050 - CALLED TO BRIAN Q. - Monica Moraga; 2017-01-12 - 18050 - Zhi Yu-We diagnose unit blowing wheel bearing shaft wear out. - Zhi Yu; 2017-01-13 - 18050 - Zhi Yu-Removed the blower house and bring back to shop. - Zhi Yu; 2017-01-19 - 18050 - Zhi Yu-retrofit to direct drive. we replaced 1/3 hp 115 volt., blower wheel and cap. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-11 | 38584 | TMPE-211573 | 1/11/17 The freezer in the kitchen doesn\\u2019t seem to be \\u201csealing\\u201d when it closes only a the bottom. We have checked to make sure its not being obstructed. The bottom shelf items are defrosting but the res t of the freezer is fine. Bill to TL502001138. 42A042B | 2017-01-17 - 18180 - Zhi Yu-The freezer is pack to the roof and lack of circulation. notice the condenser coil very dirty. We rinse condenser coil. - Zhi Yu; 2017-01-17 - 18180 - Derek Gittings-The freezer is pack to the roof and lack of circulation. notice the condenser coil very dirty. We rinse condenser coil. - Zhi Yu | 1/11/17 The freezer in the kitchen doesn\\u2019t seem to be \\u201csealing\\u201d when it closes only a the bottom. We have checked to make sure its not being obstructed. The bottom shelf items are defrosting but the res t of the freezer is fine. Bill to TL502001138. 42A042B 2017-01-17 - 18180 - Zhi Yu-The freezer is pack to the roof and lack of circulation. notice the condenser coil very dirty. We rinse condenser coil. - Zhi Yu; 2017-01-17 - 18180 - Derek Gittings-The freezer is pack to the roof and lack of circulation. notice the condenser coil very dirty. We rinse condenser coil. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-11 | 38681 | TMPE-211476 | RSS1 !! Heater/AC unit not working. Was fix last month, is out again. Request 247484 42BFO11 | 2017-01-19 - 18300 - Gail Jackson-Found tstat damage, trouble shoot, no lights in EQ room; VERY DANGEROUS WHEN COMING OFF ROOF CALLED Chesler for tech to fix. - Gail Jackson; 2017-01-19 - 18300 - Carl Karr-Found tstat damage, trouble shoot, no lights in EQ room; VERY DANGEROUS WHEN COMING OFF ROOF CALLED Chesler for tech to fix. - Gail Jackson; 2017-01-19 - 18300 - Gail Jackson-Trip to central plant for Tstat; Nick said bldg. not on line put on warehouse stat. Trip to warehouse all out, trip to ARS Tempe picked up 8; 7 for stock. Installed new tstat; run test. Took 7 back to Danny. COMPLETE. bldg. TECH THERE TO REPAIR LIGHTS. - Gail Jackson; 2017-01-19 - 18300 - Thomas Gibble-Trip to central plant for Tstat; Nick said bldg. not on line put on warehouse stat. Trip to warehouse all out, trip to ARS Tempe picked up 8; 7 for stock. Installed new tstat; run test. Took 7 back to Danny. COMPLETE. bldg. TECH THERE TO REPAIR LIGHTS. - Gail Jackson | RSS1 !! Heater/AC unit not working. Was fix last month, is out again. Request 247484 42BFO11 2017-01-19 - 18300 - Gail Jackson-Found tstat damage, trouble shoot, no lights in EQ room; VERY DANGEROUS WHEN COMING OFF ROOF CALLED Chesler for tech to fix. - Gail Jackson; 2017-01-19 - 18300 - Carl Karr-Found tstat damage, trouble shoot, no lights in EQ room; VERY DANGEROUS WHEN COMING OFF ROOF CALLED Chesler for tech to fix. - Gail Jackson; 2017-01-19 - 18300 - Gail Jackson-Trip to central plant for Tstat; Nick said bldg. not on line put on warehouse stat. Trip to warehouse all out, trip to ARS Tempe picked up 8; 7 for stock. Installed new tstat; run test. Took 7 back to Danny. COMPLETE. bldg. TECH THERE TO REPAIR LIGHTS. - Gail Jackson; 2017-01-19 - 18300 - Thomas Gibble-Trip to central plant for Tstat; Nick said bldg. not on line put on warehouse stat. Trip to warehouse all out, trip to ARS Tempe picked up 8; 7 for stock. Installed new tstat; run test. Took 7 back to Danny. COMPLETE. bldg. TECH THERE TO REPAIR LIGHTS. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-11 | 38686 | TMPE-211471 | !! The thermostat for this room also handles the air in ECD 106. Unfortunately one room is cool and the other is Hot. We have equipment that cannot reach high temperatures in ECD 113. I would like to request a temporary cooling system placed in this room until the roof and Air handlers are replaced . . . | 2017-01-11 - 18010 - 01.11.17 Created WO#211544 for HVAC to install a spot cooler. And referred questions to John Holloway. No time charged. - Cheryl St. John | !! The thermostat for this room also handles the air in ECD 106. Unfortunately one room is cool and the other is Hot. We have equipment that cannot reach high temperatures in ECD 113. I would like to request a temporary cooling system placed in this room until the roof and Air handlers are replaced . . . 2017-01-11 - 18010 - 01.11.17 Created WO#211544 for HVAC to install a spot cooler. And referred questions to John Holloway. No time charged. - Cheryl St. John | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-11 | 38712 | TMPE-211445 | Newly installed pump. Motor is running extremely hot, and looks like additional support under motor head should be required, or turning 90*s. | 2017-02-14 - 18230 - Derek Gittings-secured pump - Derek Gittings | Newly installed pump. Motor is running extremely hot, and looks like additional support under motor head should be required, or turning 90*s. 2017-02-14 - 18230 - Derek Gittings-secured pump - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-11 | 170121 | RFMT-138210 | Please repair A/C on the San Pablo's roof at the west end. (Simon) | 2017-01-13 - 18010 - Simon Fernandez-troubleshoot a/c unit found bad fuses replaced (2) 35amp fuses.Also found breakers tripped,reset, then main breaker tripped with a loud bang.transferred to electric shop. - Simon Fernandez | Please repair A/C on the San Pablo's roof at the west end. (Simon) 2017-01-13 - 18010 - Simon Fernandez-troubleshoot a/c unit found bad fuses replaced (2) 35amp fuses.Also found breakers tripped,reset, then main breaker tripped with a loud bang.transferred to electric shop. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-11 | 170140 | RFMT-138191 | !! The thermostat is not working. It is only blowing out hot air. Contact Name: Jakquelin Wells Contact Phone Number: Contact Email: jnwells3@asu.edu 4NJNAOK | 2017-01-11 - 18290 - Gabriel Figueroa-Turned a/c unit on and let it run for awhile. took a temp reading and the air is at 62 degrees out the vent. - Gabriel Figueroa | !! The thermostat is not working. It is only blowing out hot air. Contact Name: Jakquelin Wells Contact Phone Number: Contact Email: jnwells3@asu.edu 4NJNAOK 2017-01-11 - 18290 - Gabriel Figueroa-Turned a/c unit on and let it run for awhile. took a temp reading and the air is at 62 degrees out the vent. - Gabriel Figueroa | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-11 | 212896 | RACC-115714 | !! Repeat Request. My AC unit is not blowing warm air, even when set at 85 degrees. My bathroom light is burnt out. Maintenance came in around noon and reset the computer in the AC; there is still no hot air blowing. Contact Name: Contact Phone Number: 6025406872 Contact Email: 4NCGOOJ | NA | !! Repeat Request. My AC unit is not blowing warm air, even when set at 85 degrees. My bathroom light is burnt out. Maintenance came in around noon and reset the computer in the AC; there is still no hot air blowing. Contact Name: Contact Phone Number: 6025406872 Contact Email: 4NCGOOJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-11 | 212897 | RACC-115713 | !! The restroom light, in the sink area, does not work. Also the air conditioning does not work. 4O249CM | NA | !! The restroom light, in the sink area, does not work. Also the air conditioning does not work. 4O249CM NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-11 | 252714 | DTPC-115824 | !! The thermostat in office/room #C100B is not working. Would like it checked out. Thank you. 42AG8BL | 2017-01-11 - 18010 - Ralph Lemons-Found no power at t-stat. Removed panel at Air Handler and found that the fuse was blown. Replaced fuse and now all is working good. - Ralph Lemons | !! The thermostat in office/room #C100B is not working. Would like it checked out. Thank you. 42AG8BL 2017-01-11 - 18010 - Ralph Lemons-Found no power at t-stat. Removed panel at Air Handler and found that the fuse was blown. Replaced fuse and now all is working good. - Ralph Lemons | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-12 | 38321 | TMPE-211836 | !! Send to HVAC shop. PRIORITY. The chillers are not supplying chilled water. Thanks. EMS team 42C3NC4 | 2017-02-06 - 18080 - Roque Garcia-Reset chillers and checked the air compressor. - Roque Garcia; 2017-05-11 - 18080 - Roque Garcia-Found air compressor controls faulty, reset - Roque Garcia | !! Send to HVAC shop. PRIORITY. The chillers are not supplying chilled water. Thanks. EMS team 42C3NC4 2017-02-06 - 18080 - Roque Garcia-Reset chillers and checked the air compressor. - Roque Garcia; 2017-05-11 - 18080 - Roque Garcia-Found air compressor controls faulty, reset - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-12 | 38404 | TMPE-211753 | Found pump seized, motor housing extremely hot! Isolated supply. | 2017-01-25 - 18230 - Jose Lopez-disconnect motor from pump,check motor and pump free pump install motor to pump re-Aline pump and put power working ok @ this time motor is going to need bearings - Jose Lopez | Found pump seized, motor housing extremely hot! Isolated supply. 2017-01-25 - 18230 - Jose Lopez-disconnect motor from pump,check motor and pump free pump install motor to pump re-Aline pump and put power working ok @ this time motor is going to need bearings - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-12 | 38485 | TMPE-211672 | BDA Roof !! Please install belt on exhaust fan 11 North side BIO A restroom not venting properly I shut off disconnect...thanks Jeffrey 4N00ABB | NA | BDA Roof !! Please install belt on exhaust fan 11 North side BIO A restroom not venting properly I shut off disconnect...thanks Jeffrey 4N00ABB NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-12 | 38488 | TMPE-211669 | Growth chamber not holding temp | 2017-01-12 - 18140 - Duane Rider-troubleshooting unit - Duane Rider; 2017-01-12 - 18140 - Duane Rider-leak check unit - Duane Rider; 2017-01-12 - 18140 - Duane Rider-Vacuum system and recharge - Duane Rider; 2017-03-15 - 18140 - Duane Rider-Unit working correctly - Duane Rider | Growth chamber not holding temp 2017-01-12 - 18140 - Duane Rider-troubleshooting unit - Duane Rider; 2017-01-12 - 18140 - Duane Rider-leak check unit - Duane Rider; 2017-01-12 - 18140 - Duane Rider-Vacuum system and recharge - Duane Rider; 2017-03-15 - 18140 - Duane Rider-Unit working correctly - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-12 | 38490 | TMPE-211667 | USB OUTSIDE OF 1650 There's a burning odor coming from outside of 1650 area. | 2017-01-20 - 18020 - Michael Kelley-A motor on the indoor fan blower burned up. Needs to be replaced - Michael Kelley | USB OUTSIDE OF 1650 There's a burning odor coming from outside of 1650 area. 2017-01-20 - 18020 - Michael Kelley-A motor on the indoor fan blower burned up. Needs to be replaced - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-12 | 170014 | RFMT-138317 | Please repair fan coil unit in Sonora 307 | 2017-01-13 - 18010 - Simon Fernandez-checked a/c unit found bad heating control,replaced, unit checked okay - Simon Fernandez | Please repair fan coil unit in Sonora 307 2017-01-13 - 18010 - Simon Fernandez-checked a/c unit found bad heating control,replaced, unit checked okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-12 | 212892 | RACC-115718 | Air conditioning does not work. Fan was turned on High and never went on all night 4O15OA7 | NA | Air conditioning does not work. Fan was turned on High and never went on all night 4O15OA7 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-13 | 38271 | TMPE-211886 | MU KITCHEN MU Catering Kitchen Dish Machine Hood vent system not turning on | NA | MU KITCHEN MU Catering Kitchen Dish Machine Hood vent system not turning on NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-13 | 212330 | RACC-116280 | AC vent by rooms A and B leaks water when AC is running. It also might need a filter change? 4NILJCB | NA | AC vent by rooms A and B leaks water when AC is running. It also might need a filter change? 4NILJCB NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-13 | 2677 | WEST-108572 | Air Compressor - Monthly Maintenance | 2017-01-12 - xPM-0100-M - Robert Gailey-checked oil and tire pressure. ran compressor - Robert Gailey | Air Compressor - Monthly Maintenance 2017-01-12 - xPM-0100-M - Robert Gailey-checked oil and tire pressure. ran compressor - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-15 | 41264 | TMPE-208893 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-16 | 169846 | RFMT-138485 | Temperature needs to be adjusted. Currently 80 degrees. It's too warm. Contacted Sal Marasco at 11:04am. | 2017-01-18 - 18010 - Simon Fernandez-removed and replaced heating actuator.rechecked a/c unit okay. - Simon Fernandez | Temperature needs to be adjusted. Currently 80 degrees. It's too warm. Contacted Sal Marasco at 11:04am. 2017-01-18 - 18010 - Simon Fernandez-removed and replaced heating actuator.rechecked a/c unit okay. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-16 | 169855 | RFMT-138476 | !! The A/C is not working. We would like it fixed. It has been this way since we moved in. 4O4DDAO | 2017-01-18 - 18010 - Thor Millsaps-Replaced heating actuator. System up and running. - Simon Fernandez | !! The A/C is not working. We would like it fixed. It has been this way since we moved in. 4O4DDAO 2017-01-18 - 18010 - Thor Millsaps-Replaced heating actuator. System up and running. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-16 | 169870 | RFMT-138461 | incredibly dusty vents- request to change air filters 4O057EG | 2017-01-18 - 18170 - Rene Arrieta-replace filter - Chester Duncan | incredibly dusty vents- request to change air filters 4O057EG 2017-01-18 - 18170 - Rene Arrieta-replace filter - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-16 | 169871 | RFMT-138460 | !! vent cover of AC is removed and missing 4O0ELEO | 2017-01-18 - 18010 - Chester Duncan-replace door - Chester Duncan | !! vent cover of AC is removed and missing 4O0ELEO 2017-01-18 - 18010 - Chester Duncan-replace door - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-16 | 252579 | DTPC-115959 | AC 1-2 for the 2nd floor IDF room is in alarm. | 2017-01-16 - 18010 - Ross Hossack-Reset thermostat and unit is running.Checked unit throughout the day and it has stayed running as it should. - Ross Hossack | AC 1-2 for the 2nd floor IDF room is in alarm. 2017-01-16 - 18010 - Ross Hossack-Reset thermostat and unit is running.Checked unit throughout the day and it has stayed running as it should. - Ross Hossack | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-16 | 37506 | TMPE-212651 | Naumann Hobbs Located unit, inspected and found bad batteries in a pack that was over 3 years old. Ordered parts. Removed seats and seat plate. Replaced batteries, repaired corroded wires, secured cables. Reassembled unit and tested charging system. total: 1364.89 | NA | Naumann Hobbs Located unit, inspected and found bad batteries in a pack that was over 3 years old. Ordered parts. Removed seats and seat plate. Replaced batteries, repaired corroded wires, secured cables. Reassembled unit and tested charging system. total: 1364.89 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-17 | 38008 | TMPE-212149 | UPDATE - JOE P&T DISPATCH CALLED FOR A STATUS. SAID IT'S STILL VERY COLD. In main area at PTS Operations offices the thermostat is showing 69 but temp is 76. Please see Joe in Dispatch. 4O190CB | 2017-02-06 - 18300 - Roque Garcia-Found two condenser units in need of repair. Reset and both needed fuses and freon. - Roque Garcia | UPDATE - JOE P&T DISPATCH CALLED FOR A STATUS. SAID IT'S STILL VERY COLD. In main area at PTS Operations offices the thermostat is showing 69 but temp is 76. Please see Joe in Dispatch. 4O190CB 2017-02-06 - 18300 - Roque Garcia-Found two condenser units in need of repair. Reset and both needed fuses and freon. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-17 | 38028 | TMPE-212129 | MU 99 Motor Y1051 for the chilled water process pump in EQ99 has developed excessive vibration. Please check. 42AI0GO | 2017-02-22 - 23100 - Derek Gittings-had motor off,looks like it is the pump.in working progress - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-working on pump and motor. - Derek Gittings; 2017-03-10 - 23100 - Derek Gittings-went to remove motor and pump,water shut off valve needs to be replaced. - Derek Gittings; 2017-04-14 - 23100 - Derek Gittings-replaced motor. - Derek Gittings | MU 99 Motor Y1051 for the chilled water process pump in EQ99 has developed excessive vibration. Please check. 42AI0GO 2017-02-22 - 23100 - Derek Gittings-had motor off,looks like it is the pump.in working progress - Derek Gittings; 2017-03-09 - 23100 - Derek Gittings-working on pump and motor. - Derek Gittings; 2017-03-10 - 23100 - Derek Gittings-went to remove motor and pump,water shut off valve needs to be replaced. - Derek Gittings; 2017-04-14 - 23100 - Derek Gittings-replaced motor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-01-17 | 169700 | RFMT-138631 | ASUHC-Agent: Lisa D. Description: Laundry room H-1 overflowing, washing machine broken. Who was dispatched: Sal Marasco Time of dispatch: 09:36pm ASUHC-Lisa D. 9:38pm Description: Casey O'Neil (480) 694-5939 called to report H-1092 (next to original laundry room) is experiencing heavy floodin. . . | 2017-01-18 - 23000 - Salvatore Marasco Jr-Moved washing machine away from wall, turned off supply water, called ASU Call Center to request Olympus come out to do water extraction in hallways and adjacent rooms. No plumber necessary, there were no broken pipes.May need to call vendor. Helped Olympus move equipment and opened model room for water to be extracted from there. Requested Olympus to place blowers in wet areas. - Salvatore Marasco Jr | ASUHC-Agent: Lisa D. Description: Laundry room H-1 overflowing, washing machine broken. Who was dispatched: Sal Marasco Time of dispatch: 09:36pm ASUHC-Lisa D. 9:38pm Description: Casey O'Neil (480) 694-5939 called to report H-1092 (next to original laundry room) is experiencing heavy floodin. . . 2017-01-18 - 23000 - Salvatore Marasco Jr-Moved washing machine away from wall, turned off supply water, called ASU Call Center to request Olympus come out to do water extraction in hallways and adjacent rooms. No plumber necessary, there were no broken pipes.May need to call vendor. Helped Olympus move equipment and opened model room for water to be extracted from there. Requested Olympus to place blowers in wet areas. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-17 | 169867 | RFMT-138464 | !! The air conditioning is broken Contact Name: Contact Phone Number: 7207578144 Contact Email: 4O0JMNB | 2017-01-17 - 18010 - John Romero-Resident would like for the room to be cooler. Advised resident on how system works. Everything is working like it should. - John Romero | !! The air conditioning is broken Contact Name: Contact Phone Number: 7207578144 Contact Email: 4O0JMNB 2017-01-17 - 18010 - John Romero-Resident would like for the room to be cooler. Advised resident on how system works. Everything is working like it should. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-17 | 252546 | DTPC-115992 | The air is blowing cold again in Mercado F 210 | 2017-01-20 - 18300 - Ralph Lemons-Took some temperature readings and it is blowing cold air. Analysis is low on refrigerant. Must call out HVAC company to put some R22 in it. - Ralph Lemons; 2017-03-30 - 18300 - Larry Smith-Unit was replaced this is working now. - Patricia Best | The air is blowing cold again in Mercado F 210 2017-01-20 - 18300 - Ralph Lemons-Took some temperature readings and it is blowing cold air. Analysis is low on refrigerant. Must call out HVAC company to put some R22 in it. - Ralph Lemons; 2017-03-30 - 18300 - Larry Smith-Unit was replaced this is working now. - Patricia Best | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-17 | 37549 | TMPE-212608 | !! Request for Estimate. Please initiate an estimate request for HVAC to determine if the REVCO -80\\xba C freezer in LSE S-61 marked as #15 (1st freezer on left side as you walk in the door) can be repaired or would be more cost effective to salvage and purchase new. Researchers will be waiting on the. . . | 2017-03-03 - 18180 - Zhi Yu-the unit is off upon arrived. We start unit the first stage is running, but the second stage compressor not coming on. We check all safety, the Hpc bad. We bypass HPC, 2 stage compressor LRA. Compressor lock-up. The cost of labor and material maybe exceed 1/2 the cost of new unit. Revco Technolagies ULT2586-5-A34 P07L-520413-PL We call the manufactory This unit from 2001, which about 17years old. It will be more cost efficient to replaced new unit in the long run. - Zhi Yu | !! Request for Estimate. Please initiate an estimate request for HVAC to determine if the REVCO -80\\xba C freezer in LSE S-61 marked as #15 (1st freezer on left side as you walk in the door) can be repaired or would be more cost effective to salvage and purchase new. Researchers will be waiting on the. . . 2017-03-03 - 18180 - Zhi Yu-the unit is off upon arrived. We start unit the first stage is running, but the second stage compressor not coming on. We check all safety, the Hpc bad. We bypass HPC, 2 stage compressor LRA. Compressor lock-up. The cost of labor and material maybe exceed 1/2 the cost of new unit. Revco Technolagies ULT2586-5-A34 P07L-520413-PL We call the manufactory This unit from 2001, which about 17years old. It will be more cost efficient to replaced new unit in the long run. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-01-18 | 37729 | TMPE-212428 | !! Chilled Water Pumps 1&2 - Y6172&6174 are off and won't start. Please check. 42AI0GO | 2017-01-23 - 23100 - Robert Dauscher-chilled water pump# 1 was able to be restarted, online and working properly. Chilled water pump #2 is drawing 100amps on one leg. And 70 amps on the other two legs. Need to megaohm the motor. - Robert Dauscher | !! Chilled Water Pumps 1&2 - Y6172&6174 are off and won't start. Please check. 42AI0GO 2017-01-23 - 23100 - Robert Dauscher-chilled water pump# 1 was able to be restarted, online and working properly. Chilled water pump #2 is drawing 100amps on one leg. And 70 amps on the other two legs. Need to megaohm the motor. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-18 | 37790 | TMPE-212367 | WHALL 9 !! There has been recent work on the sump pump in room 9 of West Hall, but with classes starting up now they have noticed some issues. From the Professor: "I've notice that the sump pump is leaking again, and I can't get the drain filter loose to clean anything that might be clogging it.. . . | 2017-01-23 - 23100 - Robert Dauscher-found pump motor had open winding. Pulled and replaced pump. had to adjust length of pipe to accommodate the height of the new pump. call complete - Robert Dauscher | WHALL 9 !! There has been recent work on the sump pump in room 9 of West Hall, but with classes starting up now they have noticed some issues. From the Professor: "I've notice that the sump pump is leaking again, and I can't get the drain filter loose to clean anything that might be clogging it.. . . 2017-01-23 - 23100 - Robert Dauscher-found pump motor had open winding. Pulled and replaced pump. had to adjust length of pipe to accommodate the height of the new pump. call complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-01-18 | 37812 | TMPE-212345 | Strange sound coming from AC vent in the office. 4N63726 | 2017-01-31 - 18010 - Jennifer Moyer-Sound is coming from air being drawn into the circulation pump. These coils do not have automatic regulating valves, it has a manual circuit setter that does not work. Problem should resolve itself once the pump is fixed. - Jennifer Moyer; 2017-02-01 - 18010 - Jennifer Moyer-Consulted with shop Lead, and the problem is the pipe and plumbing shop is aware. - Jennifer Moyer | Strange sound coming from AC vent in the office. 4N63726 2017-01-31 - 18010 - Jennifer Moyer-Sound is coming from air being drawn into the circulation pump. These coils do not have automatic regulating valves, it has a manual circuit setter that does not work. Problem should resolve itself once the pump is fixed. - Jennifer Moyer; 2017-02-01 - 18010 - Jennifer Moyer-Consulted with shop Lead, and the problem is the pipe and plumbing shop is aware. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-01-18 | 169620 | RFMT-138711 | !! The vent on the main door was ripped off and needs to be repaired for this residents room. 4O0ADI6 | 2017-01-20 - 18010 - Mike Guckian-reattached door vent. - Mike Guckian | !! The vent on the main door was ripped off and needs to be repaired for this residents room. 4O0ADI6 2017-01-20 - 18010 - Mike Guckian-reattached door vent. - Mike Guckian | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-18 | 169632 | RFMT-138699 | Maintenance came over today and suggested that we fill in a maintenance request because the air conditioner is probably broken. 4NG6FBE | 2017-01-19 - 18010 - Salvatore Marasco Jr-A.C unit is working fine in heat mode. In cool it seems to be working as well except that the central plant is not sending child water at this time. - Salvatore Marasco Jr | Maintenance came over today and suggested that we fill in a maintenance request because the air conditioner is probably broken. 4NG6FBE 2017-01-19 - 18010 - Salvatore Marasco Jr-A.C unit is working fine in heat mode. In cool it seems to be working as well except that the central plant is not sending child water at this time. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-01-18 | 169669 | RFMT-138662 | !! Our thermostat is only blowing hot air even when we turn it off. The ac doesn't work when we turn the ac on it continues to blow hot air. Contact Name: Contact Phone Number: 5039517678 Contact Email: 4O0BF4H | 2017-01-27 - 18010 - Simon Fernandez-rechecked a/c unit unit okay problem due to pressure differential. and bad valve. - Simon Fernandez | !! Our thermostat is only blowing hot air even when we turn it off. The ac doesn't work when we turn the ac on it continues to blow hot air. Contact Name: Contact Phone Number: 5039517678 Contact Email: 4O0BF4H 2017-01-27 - 18010 - Simon Fernandez-rechecked a/c unit unit okay problem due to pressure differential. and bad valve. - Simon Fernandez | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-01-18 | 231857 | POLY-116341 | !! The residents kitchen light switch needs to be replaced. The switch is wore out and will not stay switched up or down correctly. The resident would also like the air filter to be replaced as well. Thank you for your time. The resident also has pets so if you would be able to contact one of the re. . . | NA | !! The residents kitchen light switch needs to be replaced. The switch is wore out and will not stay switched up or down correctly. The resident would also like the air filter to be replaced as well. Thank you for your time. The resident also has pets so if you would be able to contact one of the re. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-18 | 37667 | TMPE-212490 | Fan motor is excessively noisy, please investigate asap, and notify on status. | 2017-01-19 - 18230 - Zhi has responded to this, the motor has noisy bearings. Not considered an emergency at this time. - Brian Qualls; 2017-01-23 - 18230 - Zhi Yu-Diagnosed bad bearing. We removed motor back to shop. We replaced new bearings and belt. bump test motor for 20min. reinstall motor and belt. system back to normal condition.. - Zhi Yu; 2017-01-23 - 18230 - Mitchell Andrews-Diagnosed bad bearing. We removed motor back to shop. We replaced new bearings and belt. bump test motor for 20min. reinstall motor and belt. system back to normal condition.. - Zhi Yu | Fan motor is excessively noisy, please investigate asap, and notify on status. 2017-01-19 - 18230 - Zhi has responded to this, the motor has noisy bearings. Not considered an emergency at this time. - Brian Qualls; 2017-01-23 - 18230 - Zhi Yu-Diagnosed bad bearing. We removed motor back to shop. We replaced new bearings and belt. bump test motor for 20min. reinstall motor and belt. system back to normal condition.. - Zhi Yu; 2017-01-23 - 18230 - Mitchell Andrews-Diagnosed bad bearing. We removed motor back to shop. We replaced new bearings and belt. bump test motor for 20min. reinstall motor and belt. system back to normal condition.. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-18 | 37670 | TMPE-212487 | SHESC 128M1 Work order for HVAC School of human evolution building room 128 M1 Exhaust fan #1943 needs to be replaced is making loud noise | 2017-01-24 - 18160 - Zhi Yu-Removed motor back to shop. - Zhi Yu; 2017-01-24 - 18160 - Zhi Yu-Pick-up Motor housing and assembly. Removed old bracket and install back to the new housing. - Zhi Yu; 2017-01-26 - 18160 - Zhi Yu-Install new Exhaust fan. vacuum the cabinet and wash grill. - Zhi Yu; 2017-01-26 - 18160 - Jennifer Moyer-Install new Exhaust fan. vacuum the cabinet and wash grill. - Zhi Yu | SHESC 128M1 Work order for HVAC School of human evolution building room 128 M1 Exhaust fan #1943 needs to be replaced is making loud noise 2017-01-24 - 18160 - Zhi Yu-Removed motor back to shop. - Zhi Yu; 2017-01-24 - 18160 - Zhi Yu-Pick-up Motor housing and assembly. Removed old bracket and install back to the new housing. - Zhi Yu; 2017-01-26 - 18160 - Zhi Yu-Install new Exhaust fan. vacuum the cabinet and wash grill. - Zhi Yu; 2017-01-26 - 18160 - Jennifer Moyer-Install new Exhaust fan. vacuum the cabinet and wash grill. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-18 | 37717 | TMPE-212440 | CPCOM B003 The #1 hot water pump is leaking. turn off and switch to #2, I will be doing work to repair #1. | 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-remove pump and motor remove flanges make 2 gaskets put flanges back re-connect pump/motor,open water check for leaks,start pump working ok. - Jose Lopez | CPCOM B003 The #1 hot water pump is leaking. turn off and switch to #2, I will be doing work to repair #1. 2017-02-01 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-01 - 23100 - Jose Lopez-remove pump and motor remove flanges make 2 gaskets put flanges back re-connect pump/motor,open water check for leaks,start pump working ok. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-19 | 150493 | RNLD-100808 | Please order Bathroom fan motors and grills for the Building. we used the last one. thanks 4NF4KMJ | 2017-05-15 - 15000 - Jesse Deanda-1/19 - Jesse talked with Joel Anderson, and he said he would order them, so Jesse gave it over to him. When the fans came in, we stored them in the Century Hall Utility Room. - Gayle Swenson | Please order Bathroom fan motors and grills for the Building. we used the last one. thanks 4NF4KMJ 2017-05-15 - 15000 - Jesse Deanda-1/19 - Jesse talked with Joel Anderson, and he said he would order them, so Jesse gave it over to him. When the fans came in, we stored them in the Century Hall Utility Room. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-19 | 169583 | RFMT-138748 | Heater isn't functional. Does not turn on. Thanks! Contact Name: Daniel Contact Phone Number: Contact Email: 4O235AA | 2017-01-20 - 18010 - Salvatore Marasco Jr-Checked out A.C. unit. Blower was functioning as well as the electric valve actuators but some of the ball isolation valves were not functional. Need A.C. techs. to address this unit. - Salvatore Marasco Jr; 2017-01-20 - 18010 - Res. Life HVAC copied - Gregory Stetka | Heater isn't functional. Does not turn on. Thanks! Contact Name: Daniel Contact Phone Number: Contact Email: 4O235AA 2017-01-20 - 18010 - Salvatore Marasco Jr-Checked out A.C. unit. Blower was functioning as well as the electric valve actuators but some of the ball isolation valves were not functional. Need A.C. techs. to address this unit. - Salvatore Marasco Jr; 2017-01-20 - 18010 - Res. Life HVAC copied - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-01-19 | 169594 | RFMT-138737 | Please repair fan coil units condensation line in C100C1 | 2017-01-20 - 18010 - Thor Millsaps-Cleaned condensate drain line. Removed p-trap and cleaned p-=trap as well. - Thor Millsaps | Please repair fan coil units condensation line in C100C1 2017-01-20 - 18010 - Thor Millsaps-Cleaned condensate drain line. Removed p-trap and cleaned p-=trap as well. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-19 | 169598 | RFMT-138733 | Fan to AC is blowing really hot air. We are sweating in this room. Please send someone, ASAP to fix. Dispatched Greg 4pm | 2017-01-19 - 18290 - Simon checked unit and found actuator failing. Adjusted valve - occupants o.k for the night. - Gregory Stetka; 2017-01-19 - 18290 - Contacted occupants and offered space heater - they said they are o.k. for the night. - Gregory Stetka; 2017-01-27 - 18290 - Thor Millsaps-Tried to replace heating actuator but water pressure too high. Water is being pushed past actuator. Set pump operation to run on vfd and pressure dropped from 105 psi to 40 psi. Actuator can now open and close normally. Possible comm malfunction between vfd, pump, and metasys panel. Recommend JCI or EMS troubleshoot. - Simon Fernandez | Fan to AC is blowing really hot air. We are sweating in this room. Please send someone, ASAP to fix. Dispatched Greg 4pm 2017-01-19 - 18290 - Simon checked unit and found actuator failing. Adjusted valve - occupants o.k for the night. - Gregory Stetka; 2017-01-19 - 18290 - Contacted occupants and offered space heater - they said they are o.k. for the night. - Gregory Stetka; 2017-01-27 - 18290 - Thor Millsaps-Tried to replace heating actuator but water pressure too high. Water is being pushed past actuator. Set pump operation to run on vfd and pressure dropped from 105 psi to 40 psi. Actuator can now open and close normally. Possible comm malfunction between vfd, pump, and metasys panel. Recommend JCI or EMS troubleshoot. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-01-19 | 169615 | RFMT-138716 | !! The AC in this room is not working, the AC works fine on the other side of the room but not this side. 4O024B0 | 2017-01-19 - 18010 - Scott Berndt-replaced the a/c filter and cleaned out a/c ...Found inside vent was blocked removed the debrus out... - Scott Berndt | !! The AC in this room is not working, the AC works fine on the other side of the room but not this side. 4O024B0 2017-01-19 - 18010 - Scott Berndt-replaced the a/c filter and cleaned out a/c ...Found inside vent was blocked removed the debrus out... - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-01-19 | 231831 | POLY-116367 | **Steve, I have made a copy of this work order adn will address the room numbers in TMA with Gayle when she returns.** The heaters are either not working or intermittently operating in these cells. Could we have someone look at them please? 42C43B2 2 items: can the room numbers in this . . . | 2017-03-20 - 18010 - Esli Arvizo-check units - found one with a bad motor - Steve Clark; 2017-03-20 - 18010 - Esli Arvizo-check units - found one with a bad motor 2/20- replaced motor - Steve Clark; 2017-03-20 - 18010 - Suresh Nair-check units - found one with a bad motor 2/20- replaced motor - Steve Clark | **Steve, I have made a copy of this work order adn will address the room numbers in TMA with Gayle when she returns.** The heaters are either not working or intermittently operating in these cells. Could we have someone look at them please? 42C43B2 2 items: can the room numbers in this . . . 2017-03-20 - 18010 - Esli Arvizo-check units - found one with a bad motor - Steve Clark; 2017-03-20 - 18010 - Esli Arvizo-check units - found one with a bad motor 2/20- replaced motor - Steve Clark; 2017-03-20 - 18010 - Suresh Nair-check units - found one with a bad motor 2/20- replaced motor - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-19 | 37372 | TMPE-212785 | Requesting Service from FACMAN Mechanical Dept... Please check minor leaking HWR pump Y # 3904 in Best C room 00S1. It appears to be leaking at the pumps shaft seal. Submitted by 42DINIB | 2017-02-02 - 23100 - Brian Qualls-Pump shaft seal does have a minor leak. We do not have info on this as it is a newer install. I have reassigned to Jose Lopez to take care of as weather warms up due to there being only 1 pump for heating, and we do not have a parts list. Also changing priority to routine. - Brian Qualls; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez | Requesting Service from FACMAN Mechanical Dept... Please check minor leaking HWR pump Y # 3904 in Best C room 00S1. It appears to be leaking at the pumps shaft seal. Submitted by 42DINIB 2017-02-02 - 23100 - Brian Qualls-Pump shaft seal does have a minor leak. We do not have info on this as it is a newer install. I have reassigned to Jose Lopez to take care of as weather warms up due to there being only 1 pump for heating, and we do not have a parts list. Also changing priority to routine. - Brian Qualls; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-19 | 37403 | TMPE-212754 | LSA 123 It is reported, "There is a constant low-volume noise that sounds metallic that seems to be coming from the ceiling. We would like to know if it could be looked to determine the source so it can then be addressed. Thank you!" Bob Booher in SOLS Facilities checked it out and it cannot be . . . | 2017-01-20 - 10010 - John Crocker-Checked Room. Noise Coming From Room 127. Can Not Lift Ceiling Tiles. Coming From AC Duct TRANSFER TO HVAC SHOP Materials: None .75 hr - John Crocker | LSA 123 It is reported, "There is a constant low-volume noise that sounds metallic that seems to be coming from the ceiling. We would like to know if it could be looked to determine the source so it can then be addressed. Thank you!" Bob Booher in SOLS Facilities checked it out and it cannot be . . . 2017-01-20 - 10010 - John Crocker-Checked Room. Noise Coming From Room 127. Can Not Lift Ceiling Tiles. Coming From AC Duct TRANSFER TO HVAC SHOP Materials: None .75 hr - John Crocker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-01-19 | 37417 | TMPE-212740 | AQUAT Condensate pump not working in main EQ room. assign to AC | 2017-03-22 - 23040 - Jennifer Moyer-Locate pump and evaluate next steps. - Jennifer Moyer | AQUAT Condensate pump not working in main EQ room. assign to AC 2017-03-22 - 23040 - Jennifer Moyer-Locate pump and evaluate next steps. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-19 | 37422 | TMPE-212735 | MOEUR L1-09B In the door that is just beyond this door, a hot water pump is leaking. | 2017-01-19 - 23100 - Called out to Brian - Amanda Thomas; 2017-01-23 - 23100 - Michael Kelley-Found HWP seals blown. Old WO TMPE-203742. Cleaned floor. Pulled Pump. Brought back to shop for repair. - Michael Kelley; 2017-01-23 - 23100 - Derek Gittings-Found HWP seals blown. Old WO TMPE-203742. Cleaned floor. Pulled Pump. Brought back to shop for repair. - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop Bead blasted parts - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop Bead blasted parts. Painted - Michael Kelley; 2017-02-01 - 23100 - Michael Kelley-got lip seal and bearing. Worked on pump installation. - Michael Kelley; 2017-02-02 - 23100 - Michael Kelley-put together pump. installed pump. Had problems with seal on outboard bearing. flange gasket leaked. informed Ashley at the front desk about issue. need to align pump as well. - Michael Kelley; 2017-02-02 - 23100 - Derek Gittings-put together pump. installed pump. Had problems with seal on outboard bearing. flange gasket leaked. informed Ashley at the front desk about issue. need to align pump as well. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-tied to get pump to seal. Still leaks. Pulled apart 3 times. Need new pump. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-tried to contact customer. Ashley Todd not at work. Pump is on Order. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-Made new gasket. Thicker. Same results. Leaks. Informed customer. Ran out of time to align. Set up drip pipes for pump leaks. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-aligned pump. Talk to Mike Cousins told him pump is working but has leaks. Pump on order according to Brian. Drip pans in place to catch leaks. RED DANGER tape put in place to protect people. Coupling guard is off - Michael Kelley; 2017-02-15 - 23100 - Derek Gittings-installed pump - Derek Gittings; 2017-02-17 - 23100 - Derek Gittings-rebuilt pump seals,bearings installed - Derek Gittings; 2017-03-03 - 23100 - Pump on order. see Brian. Drip pans added to control Hot Water leak at seal. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Received new pump. Delivered extra pump to basement eq room. The spare Hot water pump is just in case of leak. - Michael Kelley; 2017-04-03 - 23100 - Midhat Mukanovic-Received new pump. Delivered extra pump to basement eq room. The spare Hot water pump is just in case of leak. - Michael Kelley | MOEUR L1-09B In the door that is just beyond this door, a hot water pump is leaking. 2017-01-19 - 23100 - Called out to Brian - Amanda Thomas; 2017-01-23 - 23100 - Michael Kelley-Found HWP seals blown. Old WO TMPE-203742. Cleaned floor. Pulled Pump. Brought back to shop for repair. - Michael Kelley; 2017-01-23 - 23100 - Derek Gittings-Found HWP seals blown. Old WO TMPE-203742. Cleaned floor. Pulled Pump. Brought back to shop for repair. - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop Bead blasted parts - Michael Kelley; 2017-01-27 - 23100 - Michael Kelley-Repaired pump. in shop Bead blasted parts. Painted - Michael Kelley; 2017-02-01 - 23100 - Michael Kelley-got lip seal and bearing. Worked on pump installation. - Michael Kelley; 2017-02-02 - 23100 - Michael Kelley-put together pump. installed pump. Had problems with seal on outboard bearing. flange gasket leaked. informed Ashley at the front desk about issue. need to align pump as well. - Michael Kelley; 2017-02-02 - 23100 - Derek Gittings-put together pump. installed pump. Had problems with seal on outboard bearing. flange gasket leaked. informed Ashley at the front desk about issue. need to align pump as well. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-tied to get pump to seal. Still leaks. Pulled apart 3 times. Need new pump. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-tried to contact customer. Ashley Todd not at work. Pump is on Order. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-Made new gasket. Thicker. Same results. Leaks. Informed customer. Ran out of time to align. Set up drip pipes for pump leaks. - Michael Kelley; 2017-02-15 - 23100 - Michael Kelley-aligned pump. Talk to Mike Cousins told him pump is working but has leaks. Pump on order according to Brian. Drip pans in place to catch leaks. RED DANGER tape put in place to protect people. Coupling guard is off - Michael Kelley; 2017-02-15 - 23100 - Derek Gittings-installed pump - Derek Gittings; 2017-02-17 - 23100 - Derek Gittings-rebuilt pump seals,bearings installed - Derek Gittings; 2017-03-03 - 23100 - Pump on order. see Brian. Drip pans added to control Hot Water leak at seal. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Received new pump. Delivered extra pump to basement eq room. The spare Hot water pump is just in case of leak. - Michael Kelley; 2017-04-03 - 23100 - Midhat Mukanovic-Received new pump. Delivered extra pump to basement eq room. The spare Hot water pump is just in case of leak. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-19 | 37427 | TMPE-212730 | HVAC to EL Change breaker Change for single pull to 1 double pull Contact Jennifer Moyer is you have questions. 740-877-9915 MWO Psychology North 210: Name: Holly O'Rourke Phone number: 480-965-7420 Building: PSYN (Psychology North) Room number: 210 Request: The ventilation system in the . . . | 2017-01-28 - 15000 - Samuel Gladden-Trying to locate circuit for exhaust fan. - Samuel Gladden; 2017-02-02 - 15000 - Edward Howell-Circuit located and on. - Samuel Gladden | HVAC to EL Change breaker Change for single pull to 1 double pull Contact Jennifer Moyer is you have questions. 740-877-9915 MWO Psychology North 210: Name: Holly O'Rourke Phone number: 480-965-7420 Building: PSYN (Psychology North) Room number: 210 Request: The ventilation system in the . . . 2017-01-28 - 15000 - Samuel Gladden-Trying to locate circuit for exhaust fan. - Samuel Gladden; 2017-02-02 - 15000 - Edward Howell-Circuit located and on. - Samuel Gladden | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-19 | 37484 | TMPE-212673 | HC-Sofia In B22 the air handler is leaking. | 2017-05-08 - 18050 - Thomas Gibble-water coil is not leaking now. - Thomas Gibble | HC-Sofia In B22 the air handler is leaking. 2017-05-08 - 18050 - Thomas Gibble-water coil is not leaking now. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-19 | 37501 | TMPE-212656 | ADA Corrections - OCR Case 08-16-2198. Requirement #3B - Physical Science 'H' wing - add end panels to existing counter top to prevent cane users from bumping into them. Action - add end panels to all the other labs that have this same condition in this wing of the building. Getting room numbers. . . | 2017-04-05 - 25000 - Todd Green-In progress - Todd Green; 2017-04-06 - 25000 - Todd Green-in progress - Todd Green; 2017-04-21 - 25000 - Todd Green-In progress - Todd Green | ADA Corrections - OCR Case 08-16-2198. Requirement #3B - Physical Science 'H' wing - add end panels to existing counter top to prevent cane users from bumping into them. Action - add end panels to all the other labs that have this same condition in this wing of the building. Getting room numbers. . . 2017-04-05 - 25000 - Todd Green-In progress - Todd Green; 2017-04-06 - 25000 - Todd Green-in progress - Todd Green; 2017-04-21 - 25000 - Todd Green-In progress - Todd Green | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-19 | 37512 | TMPE-212645 | USE 154, 150 The ceiling fans in these two office do not seem to be working. The Department of Environmental Health and Safety did an indoor air quality test and they have asked us to contact FACMAN if the fans in those office\\u2019s do not turn on. So I am contacting your office to see if someone . . . | 2017-01-24 - 18010 - Zhi Yu-Arrived we check room 150 air are blowing from register. Room 154 also air blowing from register, is the end of the loop. The air gets little weaker. To identify is blowing I put piece of tape on the register. I went down to the EQ room see If I can increase the air flow. notice are in zones. Call EMS Mike. He said all the Zones are in pneumatic control. Have it transfer to EMS. - Zhi Yu | USE 154, 150 The ceiling fans in these two office do not seem to be working. The Department of Environmental Health and Safety did an indoor air quality test and they have asked us to contact FACMAN if the fans in those office\\u2019s do not turn on. So I am contacting your office to see if someone . . . 2017-01-24 - 18010 - Zhi Yu-Arrived we check room 150 air are blowing from register. Room 154 also air blowing from register, is the end of the loop. The air gets little weaker. To identify is blowing I put piece of tape on the register. I went down to the EQ room see If I can increase the air flow. notice are in zones. Call EMS Mike. He said all the Zones are in pneumatic control. Have it transfer to EMS. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 169567 | RFMT-138764 | !! The venting in the ceiling (I think where the air filter goes) above the sinks is dripping water. When I woke up this morning there was a large puddle on the floor of my bathroom area. It is now covered by a towel. 4NC7637 | 2017-01-20 - 23000 - Thomas Zambrano-chiller line leaking. repaired leak. - Thomas Zambrano | !! The venting in the ceiling (I think where the air filter goes) above the sinks is dripping water. When I woke up this morning there was a large puddle on the floor of my bathroom area. It is now covered by a towel. 4NC7637 2017-01-20 - 23000 - Thomas Zambrano-chiller line leaking. repaired leak. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-01-20 | 208533 | RAMA-100731 | Air unit does not turn on for air conditioner or heat. 4NKN0B3 | NA | Air unit does not turn on for air conditioner or heat. 4NKN0B3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 208536 | RAMA-100728 | !! Our AC unit in the kitchen is leaking whenever we use the heater or the air conditioning 4O21NFL | NA | !! Our AC unit in the kitchen is leaking whenever we use the heater or the air conditioning 4O21NFL NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 37201 | TMPE-212956 | ECF 130F Major leak pouring into this conference room. Thank you! | 2017-01-20 - 13050 - Rueben is responding per scot wilson - Amanda Thomas; 2017-01-23 - 13050 - Reuben Bilducia-cleaned and bulled air handler. - Jennifer Gorney | ECF 130F Major leak pouring into this conference room. Thank you! 2017-01-20 - 13050 - Rueben is responding per scot wilson - Amanda Thomas; 2017-01-23 - 13050 - Reuben Bilducia-cleaned and bulled air handler. - Jennifer Gorney | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-20 | 37204 | TMPE-212953 | PV WEST The sump pump that by the bottom of the ramp is not working. | 2017-03-16 - 23100 - Derek Gittings-has been repaied. - Derek Gittings | PV WEST The sump pump that by the bottom of the ramp is not working. 2017-03-16 - 23100 - Derek Gittings-has been repaied. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 37221 | TMPE-212936 | Pillow block bearings need replaced | 2017-02-22 - 18160 - Duane Rider-Removed fan replaced bearings - Duane Rider; 2017-02-22 - 18160 - Duane Rider-RE-installed fan - Duane Rider | Pillow block bearings need replaced 2017-02-22 - 18160 - Duane Rider-Removed fan replaced bearings - Duane Rider; 2017-02-22 - 18160 - Duane Rider-RE-installed fan - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-01-20 | 37250 | TMPE-212907 | broken grease line behind motor base.2nd notice | 2017-01-26 - 18160 - Zhi Yu-We located the Exhaust unit. The zeek hose crack. We putting material together. We contact EMS for shut down. - Zhi Yu | broken grease line behind motor base.2nd notice 2017-01-26 - 18160 - Zhi Yu-We located the Exhaust unit. The zeek hose crack. We putting material together. We contact EMS for shut down. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-20 | 37254 | TMPE-212903 | noisy shaft bearings,worn motor sheave,bad motor mount adjusting bolt..please repair.. | NA | noisy shaft bearings,worn motor sheave,bad motor mount adjusting bolt..please repair.. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-20 | 37260 | TMPE-212897 | RSS 1 for AC shop south end on the roof there is a HP 3 the T stat is dead assign to WES | 2017-02-02 - 18010 - Gail Jackson-Trouble shoot unit, found tstat off and 2 contacts burned out. Taped tstat and started working; needs replaced. - Gail Jackson; 2017-02-02 - 18010 - Thomas Gibble-Trouble shoot unit, found tstat off and 2 contacts burned out. Taped tstat and started working; needs replaced. Found 1 of 2 supply airs capped off; what the; will need to return with lift to remove cap and install "T" outlet will have sheet metal make 1 up - Gail Jackson [Modified: 2017-02-02 Gail Jackson]; 2017-02-02 - 18010 - Gail Jackson-Trip to warehouse and ARS Tempe for Tstat and contacts. - Gail Jackson; 2017-02-06 - 18010 - Gail Jackson-2 trips to ARS Tempe for Tstat, 1st trip would not work on 2 stage HP. Replaced 2 burned out contactors. 3 PH Blower contactor fried amp draw 5 amp within range; motor pulley is worn out. Assisted Carl in measuring for 12 inch supply Tee to replace 1 that is capped off. HP 3 is 1 of 3 units that Condenser Coil is Damaged from HAIL; needs repaired or unit replaced because of age and R22. - Gail Jackson; 2017-02-06 - 18010 - Gail Jackson-Run Test - Gail Jackson; 2017-02-14 - 18010 - Carl Karr-Fabricate and install 12" round tee. - Carl Karr; 2017-02-14 - 18010 - Gail Jackson-Fabricate and install 12" round tee. - Carl Karr; 2017-02-14 - 18010 - Thomas Gibble-Fabricate and install 12" round tee. - Carl Karr | RSS 1 for AC shop south end on the roof there is a HP 3 the T stat is dead assign to WES 2017-02-02 - 18010 - Gail Jackson-Trouble shoot unit, found tstat off and 2 contacts burned out. Taped tstat and started working; needs replaced. - Gail Jackson; 2017-02-02 - 18010 - Thomas Gibble-Trouble shoot unit, found tstat off and 2 contacts burned out. Taped tstat and started working; needs replaced. Found 1 of 2 supply airs capped off; what the; will need to return with lift to remove cap and install "T" outlet will have sheet metal make 1 up - Gail Jackson [Modified: 2017-02-02 Gail Jackson]; 2017-02-02 - 18010 - Gail Jackson-Trip to warehouse and ARS Tempe for Tstat and contacts. - Gail Jackson; 2017-02-06 - 18010 - Gail Jackson-2 trips to ARS Tempe for Tstat, 1st trip would not work on 2 stage HP. Replaced 2 burned out contactors. 3 PH Blower contactor fried amp draw 5 amp within range; motor pulley is worn out. Assisted Carl in measuring for 12 inch supply Tee to replace 1 that is capped off. HP 3 is 1 of 3 units that Condenser Coil is Damaged from HAIL; needs repaired or unit replaced because of age and R22. - Gail Jackson; 2017-02-06 - 18010 - Gail Jackson-Run Test - Gail Jackson; 2017-02-14 - 18010 - Carl Karr-Fabricate and install 12" round tee. - Carl Karr; 2017-02-14 - 18010 - Gail Jackson-Fabricate and install 12" round tee. - Carl Karr; 2017-02-14 - 18010 - Thomas Gibble-Fabricate and install 12" round tee. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-20 | 37297 | TMPE-212860 | (on) float needs to be lowered, inlet sewer line fills before pump is called on, this allows solids to collect and plug sewer line | 2017-05-08 - 23100 - Michael Kelley-checked floats. all appeared to be working. all were at proper level - Michael Kelley | (on) float needs to be lowered, inlet sewer line fills before pump is called on, this allows solids to collect and plug sewer line 2017-05-08 - 23100 - Michael Kelley-checked floats. all appeared to be working. all were at proper level - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 37299 | TMPE-212858 | LSA 127 TRANSFER BT to HVAC Coming from duct Noise is in room 127 ORIG REQUEST It is reported, "There is a constant low-volume noise that sounds metallic that seems to be coming from the ceiling. We would like to know if it could be looked to determine the source so it can then be addressed. Tha. . . | 2017-01-23 - 10010 - Robert Dauscher-Found noise. Appears to be ticking/tinging noise from steam water pipes buried in ceiling. (asbestos containing ceiling tiles, not able to move) found exposed steam pipes in room above this room. Transfer to plumbing to see if anything can be done for noise. - Robert Dauscher | LSA 127 TRANSFER BT to HVAC Coming from duct Noise is in room 127 ORIG REQUEST It is reported, "There is a constant low-volume noise that sounds metallic that seems to be coming from the ceiling. We would like to know if it could be looked to determine the source so it can then be addressed. Tha. . . 2017-01-23 - 10010 - Robert Dauscher-Found noise. Appears to be ticking/tinging noise from steam water pipes buried in ceiling. (asbestos containing ceiling tiles, not able to move) found exposed steam pipes in room above this room. Transfer to plumbing to see if anything can be done for noise. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-01-20 | 37320 | TMPE-212837 | USB 1650 building 150 room 1650. Blower motor burnt. Assign to ZHI YU | 2017-01-26 - 18010 - Zhi Yu-removed Blower motor from unit. Call Trane for parts. - Zhi Yu; 2017-01-30 - 18010 - Zhi Yu-We install new blower motor and cap. we check system pressure. unit back to normal condition. - Zhi Yu; 2017-01-30 - 18010 - Derek Gittings-We install new blower motor and cap. we check system pressure. unit back to normal condition. - Zhi Yu | USB 1650 building 150 room 1650. Blower motor burnt. Assign to ZHI YU 2017-01-26 - 18010 - Zhi Yu-removed Blower motor from unit. Call Trane for parts. - Zhi Yu; 2017-01-30 - 18010 - Zhi Yu-We install new blower motor and cap. we check system pressure. unit back to normal condition. - Zhi Yu; 2017-01-30 - 18010 - Derek Gittings-We install new blower motor and cap. we check system pressure. unit back to normal condition. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-20 | 37325 | TMPE-212832 | CDN 153 Can someone from HVAC please come visit the Design library? We are hearing loud noises from the heating/cooling system. It sounds like "waves" where their are bursts of really loud fans going on then off then on again. Thanks! 42B769J | 2017-02-06 - 18010 - Roque Garcia-The AHU #1 VFD was in alarm. I added the electricians to the WO so they could figure out the problem with the VFD. - Roque Garcia | CDN 153 Can someone from HVAC please come visit the Design library? We are hearing loud noises from the heating/cooling system. It sounds like "waves" where their are bursts of really loud fans going on then off then on again. Thanks! 42B769J 2017-02-06 - 18010 - Roque Garcia-The AHU #1 VFD was in alarm. I added the electricians to the WO so they could figure out the problem with the VFD. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-21 | 169440 | RFMT-138891 | MAJOR ISSUE: A/C Unit can be turned on and off, but it cannot cool air; it can only blow warm air no matter what setting it is set to. 4O146J7 | 2017-01-23 - 18010 - Gabriel Figueroa-Checked a/c and actuator not working. Let Thor know since he was here on other heating issues. He said he would take a look at it. Need a Work order put in for ac/tech - Gabriel Figueroa; 2017-01-23 - 18010 - Res. Life HVAC dept. copied - Gregory Stetka | MAJOR ISSUE: A/C Unit can be turned on and off, but it cannot cool air; it can only blow warm air no matter what setting it is set to. 4O146J7 2017-01-23 - 18010 - Gabriel Figueroa-Checked a/c and actuator not working. Let Thor know since he was here on other heating issues. He said he would take a look at it. Need a Work order put in for ac/tech - Gabriel Figueroa; 2017-01-23 - 18010 - Res. Life HVAC dept. copied - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-23 | 169434 | RFMT-138897 | !! resident sent in concern of air duct. please clean air duct/filers - HAV B4061. Thanks! Picture attached per resident. Attachment(s) 4NGA63J | 2017-01-23 - 18170 - Scott Berndt-cleaned vent and vacuum - Scott Berndt | !! resident sent in concern of air duct. please clean air duct/filers - HAV B4061. Thanks! Picture attached per resident. Attachment(s) 4NGA63J 2017-01-23 - 18170 - Scott Berndt-cleaned vent and vacuum - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-01-23 | 231754 | POLY-116444 | The heater in unit O, room 6 at Bell Hall is not working. Please send maintenance to repair as soon as possible. Contact Name: George Vasquez Contact Phone Number: (909) 973-3896 Contact Email: george.vasquez@asu.edu 4O4JA8I | NA | The heater in unit O, room 6 at Bell Hall is not working. Please send maintenance to repair as soon as possible. Contact Name: George Vasquez Contact Phone Number: (909) 973-3896 Contact Email: george.vasquez@asu.edu 4O4JA8I NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-23 | 36698 | TMPE-213459 | ECE E114 !!!A24 belt has blown on the exhaust fan. Also ac/thermostat is not working. Extremely urgent. No 'Y' number | 2017-01-23 - 18010 - Called out to Brian - Amanda Thomas; 2017-01-26 - 18010 - Mitchell Andrews-replaced belt a34 adjusted shive - Mitchell Andrews | ECE E114 !!!A24 belt has blown on the exhaust fan. Also ac/thermostat is not working. Extremely urgent. No 'Y' number 2017-01-23 - 18010 - Called out to Brian - Amanda Thomas; 2017-01-26 - 18010 - Mitchell Andrews-replaced belt a34 adjusted shive - Mitchell Andrews | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-23 | 36715 | TMPE-213442 | Bad swamp gas odor in SCOB 260. Not sure if there is a floor drain in that lab that is dried up. Please check. Thanks! Michael Contact Name: Contact Phone Number: 4805290206 Contact Email: 4O328HD | 2017-03-02 - 18020 - Shark Plumbing did cast iron repairs on certain parts of the vent and drain piping on the lower level of the building. And also HVAC resealed the sewage injector lid and repaired the exhaust duct to that room. - Anthony Begay; 2017-03-10 - 18020 - Anthony Begay-Spent time on resourcing where the smell was coming from and found several cracked cast iron and sewage injector lid was open and exhaust duct was blowing into the room instead of blowing out so the smell in the room wasn't being filtered out of the building. Work was completed by Shark plumbing and Fac Man. - Anthony Begay | Bad swamp gas odor in SCOB 260. Not sure if there is a floor drain in that lab that is dried up. Please check. Thanks! Michael Contact Name: Contact Phone Number: 4805290206 Contact Email: 4O328HD 2017-03-02 - 18020 - Shark Plumbing did cast iron repairs on certain parts of the vent and drain piping on the lower level of the building. And also HVAC resealed the sewage injector lid and repaired the exhaust duct to that room. - Anthony Begay; 2017-03-10 - 18020 - Anthony Begay-Spent time on resourcing where the smell was coming from and found several cracked cast iron and sewage injector lid was open and exhaust duct was blowing into the room instead of blowing out so the smell in the room wasn't being filtered out of the building. Work was completed by Shark plumbing and Fac Man. - Anthony Begay | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-01-23 | 36718 | TMPE-213439 | !! We have an alarm sounding in the lab indicating the exhaust air for the flammable gas cabinets is not working, can you send someone to investigate? Thanks, Fred 42AB8AC | 2017-01-23 - 30000 - CALLED TO CHERYL. - Monica Moraga; 2017-02-10 - 30000 - John Holloway-After troubleshooting, job was sent to HVAC for belt replacement - John Holloway; 2017-02-15 - 30000 - John Holloway-Cause of alarm was low exhaust from bad belts - John Holloway | !! We have an alarm sounding in the lab indicating the exhaust air for the flammable gas cabinets is not working, can you send someone to investigate? Thanks, Fred 42AB8AC 2017-01-23 - 30000 - CALLED TO CHERYL. - Monica Moraga; 2017-02-10 - 30000 - John Holloway-After troubleshooting, job was sent to HVAC for belt replacement - John Holloway; 2017-02-15 - 30000 - John Holloway-Cause of alarm was low exhaust from bad belts - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-23 | 36732 | TMPE-213425 | PSC C258 Leaky reheat valve on AC unit. Send to plumbers to replace valve and to EMS to wire in new valve. 42B213C | 2017-01-31 - 23180 - Kim Hainline-replaced control valve on fan coil. - Kim Hainline | PSC C258 Leaky reheat valve on AC unit. Send to plumbers to replace valve and to EMS to wire in new valve. 42B213C 2017-01-31 - 23180 - Kim Hainline-replaced control valve on fan coil. - Kim Hainline | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-01-23 | 36795 | TMPE-213362 | ECB B130A Good morning, Friday night with the rains we had water leak into office ECB-130B. Could we have the roof checked to plug up the water entry. Thank you 42B13D7 | 2017-01-23 - 13120 - Timothy Grabowski-missing roof vent caps on two deck vents located above A-130B . Will sweep water away from area and seal areas where air was spitting out of loose laps - Timothy Grabowski; 2017-01-24 - 13120 - Timothy Grabowski-located leak under electrical conduit running along the wall , material had stuck to the sleeper under conduit and when it was moved the material underneath was destroyed . Cleaned out area really good , applied acrylicaulk and cotton mesh over entire area . Also found some loose laps at this area , vent cap was missing , found cap re-installed - Timothy Grabowski | ECB B130A Good morning, Friday night with the rains we had water leak into office ECB-130B. Could we have the roof checked to plug up the water entry. Thank you 42B13D7 2017-01-23 - 13120 - Timothy Grabowski-missing roof vent caps on two deck vents located above A-130B . Will sweep water away from area and seal areas where air was spitting out of loose laps - Timothy Grabowski; 2017-01-24 - 13120 - Timothy Grabowski-located leak under electrical conduit running along the wall , material had stuck to the sleeper under conduit and when it was moved the material underneath was destroyed . Cleaned out area really good , applied acrylicaulk and cotton mesh over entire area . Also found some loose laps at this area , vent cap was missing , found cap re-installed - Timothy Grabowski | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-23 | 36891 | TMPE-213266 | ECF 130F - reinspect to make sure contractor made proper repairs. Major leak pouring into this conference room. Thank you! | 2017-01-23 - 13120 - Timothy Grabowski-went and assisted rueben in sealing entire area where leak occurred . Entire unit has to be removed and new metal cap reinstalled . - Timothy Grabowski; 2017-01-24 - 13120 - Reuben Bilducia-Made more temporary repairs to ductwork. - Reuben Bilducia; 2017-03-15 - 13120 - Reuben Bilducia-Completed contractor repaired temporarily also. - Reuben Bilducia | ECF 130F - reinspect to make sure contractor made proper repairs. Major leak pouring into this conference room. Thank you! 2017-01-23 - 13120 - Timothy Grabowski-went and assisted rueben in sealing entire area where leak occurred . Entire unit has to be removed and new metal cap reinstalled . - Timothy Grabowski; 2017-01-24 - 13120 - Reuben Bilducia-Made more temporary repairs to ductwork. - Reuben Bilducia; 2017-03-15 - 13120 - Reuben Bilducia-Completed contractor repaired temporarily also. - Reuben Bilducia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-01-23 | 37163 | TMPE-212994 | Decorative Fountain Maintenance-Weekly | 2017-01-27 - xPM-Fountain W - Gail Jackson-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson; 2017-01-27 - xPM-Fountain W - Thomas Gibble-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson; 2017-01-27 - xPM-Fountain W - Bhuna Nhieu-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson | Decorative Fountain Maintenance-Weekly 2017-01-27 - xPM-Fountain W - Gail Jackson-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson; 2017-01-27 - xPM-Fountain W - Thomas Gibble-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson; 2017-01-27 - xPM-Fountain W - Bhuna Nhieu-Found pump and lighting pit full of water, pumped out. Takes man hole lift to remove concrete cover; very heavy; USE CAUTION! All wiring boxes will need replaced, run test pump; it runs. Security guard took to LL and showed where water is continually running in sump; will need further investigation. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-24 | 150484 | RNLD-100817 | 1) A/C Unit filters need to be cleaned because both roommates have allergies. (mold) 4O0COAF | 2017-01-26 - 18170 - Allan Blair-1/25 - Steve, Darusman, and Allan cleaned the filters. (Residents were not home). - Gayle Swenson | 1) A/C Unit filters need to be cleaned because both roommates have allergies. (mold) 4O0COAF 2017-01-26 - 18170 - Allan Blair-1/25 - Steve, Darusman, and Allan cleaned the filters. (Residents were not home). - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-24 | 150485 | RNLD-100816 | !! Air Conditioning does not work. The unit blows air, but does not get to desired temperature. 4NNCF36 | 2017-01-26 - 18010 - Allan Blair-1/25 - Steve, Darusman and Allan verified the the compressor runs. Used stand alone unction to test. Compressor runs. Explained temperature is 71F to 79F (75F plus/minus 4F) - Gayle Swenson | !! Air Conditioning does not work. The unit blows air, but does not get to desired temperature. 4NNCF36 2017-01-26 - 18010 - Allan Blair-1/25 - Steve, Darusman and Allan verified the the compressor runs. Used stand alone unction to test. Compressor runs. Explained temperature is 71F to 79F (75F plus/minus 4F) - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-24 | 169320 | RFMT-139011 | !! Repeat Request. A/C Unit only blowing hot air. Switched levers to cool setting and only the heat is working and rooms are getting extremely hot. Contact Name: Contact Phone Number: 4804680450 Contact Email: rakevionwhite@gmail.com 4O400EF | 2017-01-25 - 18010 - Gabriel Figueroa-Same thing as other rooms . Checked and all is fine a/c guys figured out the issue - Gabriel Figueroa | !! Repeat Request. A/C Unit only blowing hot air. Switched levers to cool setting and only the heat is working and rooms are getting extremely hot. Contact Name: Contact Phone Number: 4804680450 Contact Email: rakevionwhite@gmail.com 4O400EF 2017-01-25 - 18010 - Gabriel Figueroa-Same thing as other rooms . Checked and all is fine a/c guys figured out the issue - Gabriel Figueroa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-24 | 212442 | RACC-116168 | The hot tub is broken 4NHM69A | 2017-01-26 - 10010 - jet motor is on order will take 2 weeks to arrive - Jim Deal | The hot tub is broken 4NHM69A 2017-01-26 - 10010 - jet motor is on order will take 2 weeks to arrive - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-24 | 2415 | WEST-108834 | Replace broken core. | 2017-01-24 - 11000 - Pete Holguin-replace new core in room ucb 301f had a bad core ok now - Pete Holguin | Replace broken core. 2017-01-24 - 11000 - Pete Holguin-replace new core in room ucb 301f had a bad core ok now - Pete Holguin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-01-24 | 36519 | TMPE-213638 | After troubleshooting, I determined that this call should go to HVAC as 1st call list indicates. Please create a MWO for the HVAC shop to troubleshoot their Liebert units that maintain temperatures to this room. The MWO that was sent to EMS is 212868. John !! Good morning, For Old Main room 139, . . . | 2017-01-26 - 18290 - Zhi Yu-We meet with James to get access to the server room. Arrived the Temp @ 74. - Zhi Yu; 2017-02-07 - 18290 - Thomas Gibble-check out unit and will bring coil cleaner machine. - Thomas Gibble; 2017-02-07 - 18290 - Gail Jackson-check out unit and will bring coil cleaner machine. - Thomas Gibble | After troubleshooting, I determined that this call should go to HVAC as 1st call list indicates. Please create a MWO for the HVAC shop to troubleshoot their Liebert units that maintain temperatures to this room. The MWO that was sent to EMS is 212868. John !! Good morning, For Old Main room 139, . . . 2017-01-26 - 18290 - Zhi Yu-We meet with James to get access to the server room. Arrived the Temp @ 74. - Zhi Yu; 2017-02-07 - 18290 - Thomas Gibble-check out unit and will bring coil cleaner machine. - Thomas Gibble; 2017-02-07 - 18290 - Gail Jackson-check out unit and will bring coil cleaner machine. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-24 | 36539 | TMPE-213618 | CDN 162 The AC is blowing dust and dirt very hard and loud, please service asap. Thank you. | 2017-01-24 - 18010 - Called out to Brian - Amanda Thomas; 2017-02-03 - 18010 - Robert Ecabert-I talked to Terri Hoffman who was the requestor on this trouble call at the time;she said the that she could hear the supply air diffuser blowing very hard last week but it blowing normal again and much quieter. She said the unit is running fine for now and we do not need to do anything at this time. If the problem reacures she will put in another trouble call. - Robert Ecabert | CDN 162 The AC is blowing dust and dirt very hard and loud, please service asap. Thank you. 2017-01-24 - 18010 - Called out to Brian - Amanda Thomas; 2017-02-03 - 18010 - Robert Ecabert-I talked to Terri Hoffman who was the requestor on this trouble call at the time;she said the that she could hear the supply air diffuser blowing very hard last week but it blowing normal again and much quieter. She said the unit is running fine for now and we do not need to do anything at this time. If the problem reacures she will put in another trouble call. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-24 | 36583 | TMPE-213574 | GWC ONER SAID TO CREATE A WO FOR EMS AS WELL. We have no compressed air in the basement and I'm assuming it's the whole building. I believe it's due to the power outage. Please send someone asap. | 2017-01-26 - 30000 - HVAC reset air compressor after power outage - Mike Cozens | GWC ONER SAID TO CREATE A WO FOR EMS AS WELL. We have no compressed air in the basement and I'm assuming it's the whole building. I believe it's due to the power outage. Please send someone asap. 2017-01-26 - 30000 - HVAC reset air compressor after power outage - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-24 | 36586 | TMPE-213571 | GWC We have no compressed air in the basement and I'm assuming it's the whole building. I believe it's due to the power outage. Please send someone asap. | 2017-01-24 - 18030 - CALLED TO ONER. - Monica Moraga; 2017-01-25 - 18030 - Jose Lopez-restart 2 compressors check pressures set points,oil they check ok - Jose Lopez | GWC We have no compressed air in the basement and I'm assuming it's the whole building. I believe it's due to the power outage. Please send someone asap. 2017-01-24 - 18030 - CALLED TO ONER. - Monica Moraga; 2017-01-25 - 18030 - Jose Lopez-restart 2 compressors check pressures set points,oil they check ok - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-25 | 169194 | RFMT-139137 | !! Our heat/AC is stuck at 40 degrees when turned on. Unit pops off the wall. Is very loud when turned on. 4NKB0LE | 2017-01-26 - 18010 - Salvatore Marasco Jr-Found knob to thermostat set on 90. Blower was was set at off position. Turned blower on heard a rattling noise, removed front cover and stopped rattling noise. Found that the valve actuator was not working. Called Bill Hetzel to send out work request to A.C. technicians to check and replace actuator. - Salvatore Marasco Jr; 2017-01-31 - 18010 - Copied Simon with Res. Life HVAC Shop - Gregory Stetka | !! Our heat/AC is stuck at 40 degrees when turned on. Unit pops off the wall. Is very loud when turned on. 4NKB0LE 2017-01-26 - 18010 - Salvatore Marasco Jr-Found knob to thermostat set on 90. Blower was was set at off position. Turned blower on heard a rattling noise, removed front cover and stopped rattling noise. Found that the valve actuator was not working. Called Bill Hetzel to send out work request to A.C. technicians to check and replace actuator. - Salvatore Marasco Jr; 2017-01-31 - 18010 - Copied Simon with Res. Life HVAC Shop - Gregory Stetka | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-01-25 | 169246 | RFMT-139085 | Residents in 110/112 reported smelling a "foul musty odor similar to a dead animal" when they turn the heat on in the room. Problem is only present when heat is turned on. Thanks, Carli 4NF4L2O | 2017-01-25 - 18020 - David Cates-Sprayed disinfect into the vents and inside the air intake of both rooms, and test ran without the smelling any unusual odors. Filters were already changed out 1/24/17 during door to doors inspections. - David Cates | Residents in 110/112 reported smelling a "foul musty odor similar to a dead animal" when they turn the heat on in the room. Problem is only present when heat is turned on. Thanks, Carli 4NF4L2O 2017-01-25 - 18020 - David Cates-Sprayed disinfect into the vents and inside the air intake of both rooms, and test ran without the smelling any unusual odors. Filters were already changed out 1/24/17 during door to doors inspections. - David Cates | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-25 | 169257 | RFMT-139074 | !! Repeat Request. There was an incident of a broken pipe and flooding prior to break. Since my return from break there is no air conditioning and there is an odor of mildew. I have not been able to stay in my dorm because of this problem. It was reported to the front dest in Sonora. This is my . . . | 2017-01-25 - 18010 - Thor Millsaps-Heating actuator needs to be replaced. Before actuator can be replaced, access needs to be cut in ceiling adjacent to fan coil near toilet. - Thor Millsaps | !! Repeat Request. There was an incident of a broken pipe and flooding prior to break. Since my return from break there is no air conditioning and there is an odor of mildew. I have not been able to stay in my dorm because of this problem. It was reported to the front dest in Sonora. This is my . . . 2017-01-25 - 18010 - Thor Millsaps-Heating actuator needs to be replaced. Before actuator can be replaced, access needs to be cut in ceiling adjacent to fan coil near toilet. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2017-01-25 | 212367 | RACC-116243 | Room turn with bathroom exhaust fan repair (don't charge to student) and quarter clean in the bathroom split four ways (charge). No working fan in the bathroom appeared to create a moisture problem (black spots) on the ceiling near the bathroom door. Please check for mildew/mold. Charge $10 to res. . . | NA | Room turn with bathroom exhaust fan repair (don't charge to student) and quarter clean in the bathroom split four ways (charge). No working fan in the bathroom appeared to create a moisture problem (black spots) on the ceiling near the bathroom door. Please check for mildew/mold. Charge $10 to res. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-25 | 36224 | TMPE-213933 | NEED WO FOR MIKE COZENS AS WELL ASUHC Lisa D high temp alarm on the first floor of the ASUPD building room 107 U1 also AC unit # 1 on west side is off Dispatched to Tom Gibble time of dispatch 1:23 am | 2017-01-26 - 30000 - Michael Cozens-I verified the alarm. The room temperature stayed in alarm, but was holding at 80 degrees. I requested HVAC tech check out room DX AC, who requested that I increase high alarm to 82. I adjusted alarm and bad fuse was later replaced. - Mike Cozens | NEED WO FOR MIKE COZENS AS WELL ASUHC Lisa D high temp alarm on the first floor of the ASUPD building room 107 U1 also AC unit # 1 on west side is off Dispatched to Tom Gibble time of dispatch 1:23 am 2017-01-26 - 30000 - Michael Cozens-I verified the alarm. The room temperature stayed in alarm, but was holding at 80 degrees. I requested HVAC tech check out room DX AC, who requested that I increase high alarm to 82. I adjusted alarm and bad fuse was later replaced. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-25 | 36265 | TMPE-213892 | LSE 644 Please initiate a work order to have a hasp and lock installed on the freezer door of the refrigerator/freezer in LSE 644 (just inside on the right as you enter). All charges for this request may be billed to PO #LM502001099. Thank you. 42BLHKH | 2017-02-02 - 11000 - Zhi Yu-will get the locks on order. - Zhi Yu; 2017-02-02 - 11000 - Zhi Yu-install 2 nasp locks on the refrigeration door. - Zhi Yu | LSE 644 Please initiate a work order to have a hasp and lock installed on the freezer door of the refrigerator/freezer in LSE 644 (just inside on the right as you enter). All charges for this request may be billed to PO #LM502001099. Thank you. 42BLHKH 2017-02-02 - 11000 - Zhi Yu-will get the locks on order. - Zhi Yu; 2017-02-02 - 11000 - Zhi Yu-install 2 nasp locks on the refrigeration door. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-01-25 | 36298 | TMPE-213859 | !! Researcher states fume hood fan is not working in ECF, room 119. See attachment for more details. Please inform John Lemanski when the repair is complete. Attachment(s) 42C6AFK | 2017-04-07 - 18190 - John Holloway-Identified exhaust fan checked Fume Hood - John Holloway | !! Researcher states fume hood fan is not working in ECF, room 119. See attachment for more details. Please inform John Lemanski when the repair is complete. Attachment(s) 42C6AFK 2017-04-07 - 18190 - John Holloway-Identified exhaust fan checked Fume Hood - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-25 | 36324 | TMPE-213833 | MSB !! It does not appear that our heat is working, cool air is blowing out of the units. 4MN74G5 | 2017-04-04 - 18300 - Roque Garcia-Repaired three units on the roof. Number 1 needed a blower motor and contactors. Number 2 needed defrost boards. Number 3 needed the breaker reset. Number 1 and 3 are wired off the same breaker. - Roque Garcia | MSB !! It does not appear that our heat is working, cool air is blowing out of the units. 4MN74G5 2017-04-04 - 18300 - Roque Garcia-Repaired three units on the roof. Number 1 needed a blower motor and contactors. Number 2 needed defrost boards. Number 3 needed the breaker reset. Number 1 and 3 are wired off the same breaker. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-01-25 | 36354 | TMPE-213803 | CPCOM 455E !! Good Morning, I have a professor in CPCOM 455E stating that the fan or a/c is too loud. I went by with another associate and it was in fact really loud to have to work in, is there anything you can do about the noise? Thank you, Mariana 42BKC9M | 2017-01-29 - 18010 - Robert Dauscher-Stopped by room. Heard what sounded like mechanical vibration close to 455A. Had EMS stop fan inspected belts. They appear to be in good condition. Pulled off job for emergency leak repair at another building. Need to return with Brian to determine which bearing is the cause of vibration. Very large blower, shaft diameter 4-5 inches. - Robert Dauscher; 2017-01-30 - 18010 - Robert Dauscher-took measurements for bearings and gave info to Steve to order parts. will need to schedule extended shutdown to replace both bearings in AH and 60HP motor... once again pulled off of job for emergency elsewhere on campus. - Robert Dauscher | CPCOM 455E !! Good Morning, I have a professor in CPCOM 455E stating that the fan or a/c is too loud. I went by with another associate and it was in fact really loud to have to work in, is there anything you can do about the noise? Thank you, Mariana 42BKC9M 2017-01-29 - 18010 - Robert Dauscher-Stopped by room. Heard what sounded like mechanical vibration close to 455A. Had EMS stop fan inspected belts. They appear to be in good condition. Pulled off job for emergency leak repair at another building. Need to return with Brian to determine which bearing is the cause of vibration. Very large blower, shaft diameter 4-5 inches. - Robert Dauscher; 2017-01-30 - 18010 - Robert Dauscher-took measurements for bearings and gave info to Steve to order parts. will need to schedule extended shutdown to replace both bearings in AH and 60HP motor... once again pulled off of job for emergency elsewhere on campus. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-01-25 | 36392 | TMPE-213765 | !! The 2 chillers in GWC-167 are blowing hot air. There are several computer clusters in the room. 42A89GH | 2017-01-25 - 18080 - CALLED TO STEVE P. - Monica Moraga; 2017-02-06 - 18080 - Roque Garcia-The chiller pumps were off due to the power outage. I spoke with Mike C. from BMS and i reset the VFD - Roque Garcia | !! The 2 chillers in GWC-167 are blowing hot air. There are several computer clusters in the room. 42A89GH 2017-01-25 - 18080 - CALLED TO STEVE P. - Monica Moraga; 2017-02-06 - 18080 - Roque Garcia-The chiller pumps were off due to the power outage. I spoke with Mike C. from BMS and i reset the VFD - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-25 | 36413 | TMPE-213744 | ECE E114 AC/thermostat is not working. No 'Y' number | 2017-02-17 - 18010 - Mitchell Andrews-replaced the tstat and fuses..unit is running on one stage it needs a compressor on the second stage - Mitchell Andrews | ECE E114 AC/thermostat is not working. No 'Y' number 2017-02-17 - 18010 - Mitchell Andrews-replaced the tstat and fuses..unit is running on one stage it needs a compressor on the second stage - Mitchell Andrews | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-25 | 36416 | TMPE-213741 | ASUHC Lisa D high temp alarm on the first floor of the ASUPD building room 107 U1 also AC unit # 1 on west side is off Dispatched to Tom Gibble time of dispatch 1:23 am | 2017-01-26 - 18010 - Thomas Gibble-re-set west air handler. and replaced fuse on the Mitsubishi city multi ac unit.room went to 65 f . - Thomas Gibble | ASUHC Lisa D high temp alarm on the first floor of the ASUPD building room 107 U1 also AC unit # 1 on west side is off Dispatched to Tom Gibble time of dispatch 1:23 am 2017-01-26 - 18010 - Thomas Gibble-re-set west air handler. and replaced fuse on the Mitsubishi city multi ac unit.room went to 65 f . - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-26 | 212302 | RACC-116308 | Fridge/ freezer unit not cooling as much as it should- problem getting worse over time. Additionally the freezer does not stay closed when the fridge door is closed. 4NF54CD | NA | Fridge/ freezer unit not cooling as much as it should- problem getting worse over time. Additionally the freezer does not stay closed when the fridge door is closed. 4NF54CD NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-26 | 33042 | TMPE-217115 | Naumann Hobbs Located unit, inspected and found bad key switch. Ordered part and returned to cart. Removed dash and kick plate. Replaced key switch and all locks. Reassembled unit and tested. Reinstalled rear tail light. 1 GEM 1018633 KEY SWITCH KIT 0906-00016 total: 379.51 | NA | Naumann Hobbs Located unit, inspected and found bad key switch. Ordered part and returned to cart. Removed dash and kick plate. Replaced key switch and all locks. Reassembled unit and tested. Reinstalled rear tail light. 1 GEM 1018633 KEY SWITCH KIT 0906-00016 total: 379.51 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-01-26 | 36063 | TMPE-214094 | 1/26/17 The outside drinking fountain on Preschool 2's side (#132) does not work. Bill to TL502001138 42A042B | 2017-02-02 - 23080 - Thomas Gibble-drinking fountain is part of a sink. The water is reg. water not cold. plumber came to fix the sink and fix the drinking part of the sink too. - Thomas Gibble; 2017-02-02 - 23080 - Gail Jackson-drinking fountain is part of a sink. The water is reg. water not cold. plumber came to fix the sink and fix the drinking part of the sink too. - Thomas Gibble | 1/26/17 The outside drinking fountain on Preschool 2's side (#132) does not work. Bill to TL502001138 42A042B 2017-02-02 - 23080 - Thomas Gibble-drinking fountain is part of a sink. The water is reg. water not cold. plumber came to fix the sink and fix the drinking part of the sink too. - Thomas Gibble; 2017-02-02 - 23080 - Gail Jackson-drinking fountain is part of a sink. The water is reg. water not cold. plumber came to fix the sink and fix the drinking part of the sink too. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-26 | 36102 | TMPE-214055 | HVAC-- Return Vent Clogged 4NLGDF0 | 2017-02-09 - 18010 - Jennifer Moyer-Disconnected return grill from duct work and cleared the blockage. Reattached grill. Other supply and return grills were inhibiting air supply, so I took care of it in that lab. Time includes locating requester, locating ladder for extra high ceilings, driving, and TMA entry. - Jennifer Moyer [Modified: 2017-02-09 Jennifer Moyer]; 2017-02-15 - 18010 - Jennifer Moyer-Locate room, assess job, locate ladder storage area, inform customer of repair to be scheduled tomorrow. - Jennifer Moyer | HVAC-- Return Vent Clogged 4NLGDF0 2017-02-09 - 18010 - Jennifer Moyer-Disconnected return grill from duct work and cleared the blockage. Reattached grill. Other supply and return grills were inhibiting air supply, so I took care of it in that lab. Time includes locating requester, locating ladder for extra high ceilings, driving, and TMA entry. - Jennifer Moyer [Modified: 2017-02-09 Jennifer Moyer]; 2017-02-15 - 18010 - Jennifer Moyer-Locate room, assess job, locate ladder storage area, inform customer of repair to be scheduled tomorrow. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 3
2017-01-26 | 36109 | TMPE-214048 | USB - 1801: EMS transfer to HVAC, controlled by local control roof top unit. Heaters in Paint Shop does not heat. Can thermostats also get replaced? Thanks! | 2017-01-27 - 18300 - Jennifer Moyer-Research/locate parts &amp; order. Due to arrive Tuesday. - Jennifer Moyer; 2017-01-27 - 18300 - Jennifer Moyer-Pick up Loto device and troubleshoot unit. - Jennifer Moyer; 2017-02-06 - 18300 - Jennifer Moyer-Install new fan control kit for discontinued part.Install two switches and re-wire. - Jennifer Moyer; 2017-02-14 - 18300 - Thermostat replacement not approved. The thermostat for this gas heater is is not broken or malfunctioning. - Jennifer Moyer | USB - 1801: EMS transfer to HVAC, controlled by local control roof top unit. Heaters in Paint Shop does not heat. Can thermostats also get replaced? Thanks! 2017-01-27 - 18300 - Jennifer Moyer-Research/locate parts &amp; order. Due to arrive Tuesday. - Jennifer Moyer; 2017-01-27 - 18300 - Jennifer Moyer-Pick up Loto device and troubleshoot unit. - Jennifer Moyer; 2017-02-06 - 18300 - Jennifer Moyer-Install new fan control kit for discontinued part.Install two switches and re-wire. - Jennifer Moyer; 2017-02-14 - 18300 - Thermostat replacement not approved. The thermostat for this gas heater is is not broken or malfunctioning. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5
2017-01-26 | 36129 | TMPE-214028 | SAN PABLO The circulating pump for the heat exchanger for domestic hot water, is not operating and we have no hot water to the building. | 2017-01-30 - 23100 - Derek Gittings-Derek and Zhi respond to this call. Located the pump in basement floor. This system is Spirax Sarco. Mod- OPMT80701H/001 s/n 803-714-2000. We know very little about the controller. its on error code The circulation pump out of range.. We can't reset the controller. - Zhi Yu; 2017-01-30 - 23100 - Zhi Yu-Derek and Zhi respond to this call. Located the pump in basement floor. This system is Spirax Sarco. Mod- OPMT80701H/001 s/n 803-714-2000. We know very little about the controller. its on error code The circulation pump out of range.. We can't reset the controller. - Zhi Yu; 2017-01-30 - 23100 - Derek Gittings-We contact Philip Douda from Spriax, want some picture email to him. - Zhi Yu; 2017-02-01 - 23100 - Derek Gittings-We contact Eric Echols from industrial automation services come out to assist us on the spirax sarco system. We go through the system diagnostic. The alarm code showing no output which water temperature probe malfunction. We remove sensor and check the wire splice touching each other in the terminal. we repair wiring and run auto tuning for 15min. System back to normal operation. - Zhi Yu; 2017-02-01 - 23100 - Zhi Yu-We contact Eric Echols from industrial automation services come out to assist us on the spirax sarco system. We go through the system diagnostic. The alarm code showing no output which water temperature probe malfunction. We remove sensor and check the wire splice touching each other in the terminal. we repair wiring and run auto tuning for 15min. System back to normal operation. - Zhi Yu | SAN PABLO The circulating pump for the heat exchanger for domestic hot water, is not operating and we have no hot water to the building. 2017-01-30 - 23100 - Derek Gittings-Derek and Zhi respond to this call. Located the pump in basement floor. This system is Spirax Sarco. Mod- OPMT80701H/001 s/n 803-714-2000. We know very little about the controller. its on error code The circulation pump out of range.. We can't reset the controller. - Zhi Yu; 2017-01-30 - 23100 - Zhi Yu-Derek and Zhi respond to this call. Located the pump in basement floor. This system is Spirax Sarco. Mod- OPMT80701H/001 s/n 803-714-2000. We know very little about the controller. its on error code The circulation pump out of range.. We can't reset the controller. - Zhi Yu; 2017-01-30 - 23100 - Derek Gittings-We contact Philip Douda from Spriax, want some picture email to him. - Zhi Yu; 2017-02-01 - 23100 - Derek Gittings-We contact Eric Echols from industrial automation services come out to assist us on the spirax sarco system. We go through the system diagnostic. The alarm code showing no output which water temperature probe malfunction. We remove sensor and check the wire splice touching each other in the terminal. we repair wiring and run auto tuning for 15min. System back to normal operation. - Zhi Yu; 2017-02-01 - 23100 - Zhi Yu-We contact Eric Echols from industrial automation services come out to assist us on the spirax sarco system. We go through the system diagnostic. The alarm code showing no output which water temperature probe malfunction. We remove sensor and check the wire splice touching each other in the terminal. we repair wiring and run auto tuning for 15min. System back to normal operation. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-01-26 | 36183 | TMPE-213974 | Air handler in ceiling making a very unusual noise that is very loud and cannot work in the office. Please address. Thank you very much. Jeff 4N291MC | 2017-02-03 - 18050 - Duane Rider-Troubleshooting unit, need magnetic motor starter - Duane Rider | Air handler in ceiling making a very unusual noise that is very loud and cannot work in the office. Please address. Thank you very much. Jeff 4N291MC 2017-02-03 - 18050 - Duane Rider-Troubleshooting unit, need magnetic motor starter - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-26 | 36213 | TMPE-213944 | MU 87 Please add the Electric Shop to HVAC work order# 212127. Inspect, repair, replace magnetic starter. Cutler-Hammer: Size 3, 120volt coil Also repair, replace HOA switch assembly. HVAC contact is Tom Gibble. Chilled water pump 2 is off, overload tripped, one fuse open in disconnect swi. . . | 2017-01-27 - 15000 - Gary Conover-Troubleshot starter and HOA switch Repaired same. Motor ohm'ed and determined good. Voltage at mag a little low amps a little high but within tolerances - Gary Conover; 2017-01-27 - 15000 - Gary Conover-Checked motor at 3:00Pm unit is running - Gary Conover | MU 87 Please add the Electric Shop to HVAC work order# 212127. Inspect, repair, replace magnetic starter. Cutler-Hammer: Size 3, 120volt coil Also repair, replace HOA switch assembly. HVAC contact is Tom Gibble. Chilled water pump 2 is off, overload tripped, one fuse open in disconnect swi. . . 2017-01-27 - 15000 - Gary Conover-Troubleshot starter and HOA switch Repaired same. Motor ohm'ed and determined good. Voltage at mag a little low amps a little high but within tolerances - Gary Conover; 2017-01-27 - 15000 - Gary Conover-Checked motor at 3:00Pm unit is running - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-01-27 | 150471 | RNLD-100830 | !! The AC unit in room 280 needs to be cleaned out. There is mildew growing on and in the vents. Please clean the unit out if possible. Thank you. 4NI91HM | 2017-01-30 - 18010 - Allan Blair-1/27 - Allan and Darusman removed vanes and filters, and washed and dried them both, an reinstalled them. the occupant was happy. - Gayle Swenson | !! The AC unit in room 280 needs to be cleaned out. There is mildew growing on and in the vents. Please clean the unit out if possible. Thank you. 4NI91HM 2017-01-30 - 18010 - Allan Blair-1/27 - Allan and Darusman removed vanes and filters, and washed and dried them both, an reinstalled them. the occupant was happy. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-27 | 169098 | RFMT-139233 | !! RL HVAC - Please fix the heat in unit-37. 4NEI9DN | 2017-01-27 - 18010 - Thor Millsaps-Found line voltage wired to incorrect wire on thermostat and also heat and cool wires were reversed. Corrected wiring on thermostat and system is operating properly (heating). - Simon Fernandez | !! RL HVAC - Please fix the heat in unit-37. 4NEI9DN 2017-01-27 - 18010 - Thor Millsaps-Found line voltage wired to incorrect wire on thermostat and also heat and cool wires were reversed. Corrected wiring on thermostat and system is operating properly (heating). - Simon Fernandez | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-27 | 169099 | RFMT-139232 | !! RL HVAC - This room has no heat (47), please fix. 4NEI9DN | 2017-01-27 - 18010 - Simon Fernandez-checked a/c unit found bad wiring,rewired t-stat unit checks okay - Simon Fernandez | !! RL HVAC - This room has no heat (47), please fix. 4NEI9DN 2017-01-27 - 18010 - Simon Fernandez-checked a/c unit found bad wiring,rewired t-stat unit checks okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-27 | 212252 | RACC-116358 | !! Air Conditioner is still not working after repair guys stopped if from leaking. 4O13H3I | NA | !! Air Conditioner is still not working after repair guys stopped if from leaking. 4O13H3I NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-27 | 2375 | WEST-108874 | Tammy called from Cafe West. Their freezer is not working. Spoke to Jim at CP. | 2017-01-27 - 18180 - Chad T Ball-Took a look at the freezer. Evaporator coil was completely frozen. Shut down condensing unit and left evap fans running to help defrost coil. After checking out unit I found that it will not properly initiate defrost cycle. Spoke with Tammy and advised her to call their service contractor for repairs. - Chad T Ball | Tammy called from Cafe West. Their freezer is not working. Spoke to Jim at CP. 2017-01-27 - 18180 - Chad T Ball-Took a look at the freezer. Evaporator coil was completely frozen. Shut down condensing unit and left evap fans running to help defrost coil. After checking out unit I found that it will not properly initiate defrost cycle. Spoke with Tammy and advised her to call their service contractor for repairs. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-27 | 252236 | DTPC-116302 | !! The heat in rooms 164,166 &168 is not working properly. A single heating unit controls these 3 graduate studios There is an extension ladder located underneath the metal stair case. Bob the building engineer is familiar with the situation. This need to be repaired ASAP. George Harris Super. . . | 2017-01-31 - 18300 - Ralph Lemons-The t-stat in the students room was turned down. I raised the temperature and all is working good. it is holding temperature. - Ralph Lemons | !! The heat in rooms 164,166 &168 is not working properly. A single heating unit controls these 3 graduate studios There is an extension ladder located underneath the metal stair case. Bob the building engineer is familiar with the situation. This need to be repaired ASAP. George Harris Super. . . 2017-01-31 - 18300 - Ralph Lemons-The t-stat in the students room was turned down. I raised the temperature and all is working good. it is holding temperature. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-27 | 252241 | DTPC-116297 | !! Thermostat 1-18 is dead. This unit controls heat for rooms 138,140,142 and 144. Students are complaining that they are cold in their studios so repair this problem ASAP. George Harris Supervisor Grant Street Studios 42AMFKL | 2017-01-28 - 18010 - Robert Bartels-Trouble shoot ac, found loose fuse inside air handler - Robert Bartels; 2017-01-28 - 18010 - Robert Bartels-trouble shoot ac, found loose fuse inside the air handler - Robert Bartels | !! Thermostat 1-18 is dead. This unit controls heat for rooms 138,140,142 and 144. Students are complaining that they are cold in their studios so repair this problem ASAP. George Harris Supervisor Grant Street Studios 42AMFKL 2017-01-28 - 18010 - Robert Bartels-Trouble shoot ac, found loose fuse inside air handler - Robert Bartels; 2017-01-28 - 18010 - Robert Bartels-trouble shoot ac, found loose fuse inside the air handler - Robert Bartels | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-27 | 35878 | TMPE-214279 | The air conditioner in our office is making a noise that sounds like water or gas is leaking out of the machine. I have not turned on the air conditioner in a while and did not want to check if it worked to avoid making the problem any worse. The noise is persistent and I noticed it Wednesday as wel. . . | 2017-02-24 - 18010 - Thomas Gibble-unit was running OK. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-unit was running OK. - Thomas Gibble | The air conditioner in our office is making a noise that sounds like water or gas is leaking out of the machine. I have not turned on the air conditioner in a while and did not want to check if it worked to avoid making the problem any worse. The noise is persistent and I noticed it Wednesday as wel. . . 2017-02-24 - 18010 - Thomas Gibble-unit was running OK. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-unit was running OK. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-27 | 35911 | TMPE-214246 | worn motor and shaft sheaves... ak28 x 3/4 1vL34 x 1/2 | 2017-02-09 - 18160 - Thomas Gibble-measured sheaves for ex fan - Thomas Gibble; 2017-02-09 - 18160 - Gail Jackson-measured sheaves for ex fan - Thomas Gibble; 2017-02-14 - 18160 - Thomas Gibble-changed both sheaves - Thomas Gibble; 2017-02-14 - 18160 - Gail Jackson-changed both sheaves - Thomas Gibble | worn motor and shaft sheaves... ak28 x 3/4 1vL34 x 1/2 2017-02-09 - 18160 - Thomas Gibble-measured sheaves for ex fan - Thomas Gibble; 2017-02-09 - 18160 - Gail Jackson-measured sheaves for ex fan - Thomas Gibble; 2017-02-14 - 18160 - Thomas Gibble-changed both sheaves - Thomas Gibble; 2017-02-14 - 18160 - Gail Jackson-changed both sheaves - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-27 | 35986 | TMPE-214171 | Repair Temperature Sensor FCU M-3 room M1-26. Thanks, | 2017-02-03 - 18300 - Duane Rider-troubleshoot unit, needs new sensor, replaced filters, clean unit - Duane Rider; 2017-02-10 - 18300 - Return air temperature to be used as zone temperature sensing. Sensor connection for RA to moved to AI-1 on controller-Guy. - Guy Boyd; 2017-02-17 - 18300 - Duane Rider-Closed - Duane Rider | Repair Temperature Sensor FCU M-3 room M1-26. Thanks, 2017-02-03 - 18300 - Duane Rider-troubleshoot unit, needs new sensor, replaced filters, clean unit - Duane Rider; 2017-02-10 - 18300 - Return air temperature to be used as zone temperature sensing. Sensor connection for RA to moved to AI-1 on controller-Guy. - Guy Boyd; 2017-02-17 - 18300 - Duane Rider-Closed - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-27 | 35991 | TMPE-214166 | PSH Please create a new work order for HVAC services for work done on 1/24/2017 at Bateman Physical Sciences H wing (057H). Air Handler # 4 located in 2nd floor EQ room. Install \\u201cSteril-Aire\\u201d UV emitter assembly. | 2017-01-27 - 18050 - Gail Jackson-Installed UV lights in A/H 4. Trip to ACE for parts. SAFETY HAZARD ANYONE WORKING WITH THESE LIGHTS NEEDS TO BE INFORMED OF DANGERS, Informed electricians who will wire up. - Gail Jackson; 2017-01-27 - 18050 - Thomas Gibble-Installed UV lights in A/H 4. Trip to ACE for parts. SAFETY HAZARD ANYONE WORKING WITH THESE LIGHTS NEEDS TO BE INFORMED OF DANGERS, Informed electricians who will wire up. - Gail Jackson | PSH Please create a new work order for HVAC services for work done on 1/24/2017 at Bateman Physical Sciences H wing (057H). Air Handler # 4 located in 2nd floor EQ room. Install \\u201cSteril-Aire\\u201d UV emitter assembly. 2017-01-27 - 18050 - Gail Jackson-Installed UV lights in A/H 4. Trip to ACE for parts. SAFETY HAZARD ANYONE WORKING WITH THESE LIGHTS NEEDS TO BE INFORMED OF DANGERS, Informed electricians who will wire up. - Gail Jackson; 2017-01-27 - 18050 - Thomas Gibble-Installed UV lights in A/H 4. Trip to ACE for parts. SAFETY HAZARD ANYONE WORKING WITH THESE LIGHTS NEEDS TO BE INFORMED OF DANGERS, Informed electricians who will wire up. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-29 | 34934 | TMPE-215223 | HC-Sofia G Fire alarm going off after some adjusted the thermostat. Dispatched to: Kevin Cunningham Time: 10:50 Kevin said he would check it out and call ASU PD with any further questions. | 2017-01-30 - 17000 - Kevin Cunningham-Called in on standby, student told PD that they turned on the wall mounted fancoil unit in 3rd floor elevator lobby and what they thought was smoke coming out of the vent. Upon inspection the filter was full of what appeared to be drywall dust. The unit did come on when I showed up and filled the space with dust (putting the building in alarm again, mimicking what the student had reported)I checked the unit for burned wires or motor, everything checked out. I shut unit off internally and let Dale Hess know that filter needed to be changed and unit needed to be vacuumed out prior to operation.Standby call, 1.5hrs actual, 3hr. min. 1/29/2017-1/30/2017. Kevin. PD reset the fire panel. - Kevin Cunningham; 2017-02-02 - 17000 - Kevin Cunningham-1.5 hrs. adjusted for 3 hr. min.-JG - Jennifer Gorney | HC-Sofia G Fire alarm going off after some adjusted the thermostat. Dispatched to: Kevin Cunningham Time: 10:50 Kevin said he would check it out and call ASU PD with any further questions. 2017-01-30 - 17000 - Kevin Cunningham-Called in on standby, student told PD that they turned on the wall mounted fancoil unit in 3rd floor elevator lobby and what they thought was smoke coming out of the vent. Upon inspection the filter was full of what appeared to be drywall dust. The unit did come on when I showed up and filled the space with dust (putting the building in alarm again, mimicking what the student had reported)I checked the unit for burned wires or motor, everything checked out. I shut unit off internally and let Dale Hess know that filter needed to be changed and unit needed to be vacuumed out prior to operation.Standby call, 1.5hrs actual, 3hr. min. 1/29/2017-1/30/2017. Kevin. PD reset the fire panel. - Kevin Cunningham; 2017-02-02 - 17000 - Kevin Cunningham-1.5 hrs. adjusted for 3 hr. min.-JG - Jennifer Gorney | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
2017-01-30 | 169011 | RFMT-139320 | !! Air conditioner and heater is making really loud noises every time it's turned on Contact Name: Contact Phone Number: 8083484877 Contact Email: 4NOD04M | 2017-01-31 - 18010 - Simon Fernandez-removed and replaced motor,rechecked operation okay - Simon Fernandez; 2017-01-31 - 18010 - Thor Millsaps-removed and replaced motor,rechecked operation okay - Simon Fernandez | !! Air conditioner and heater is making really loud noises every time it's turned on Contact Name: Contact Phone Number: 8083484877 Contact Email: 4NOD04M 2017-01-31 - 18010 - Simon Fernandez-removed and replaced motor,rechecked operation okay - Simon Fernandez; 2017-01-31 - 18010 - Thor Millsaps-removed and replaced motor,rechecked operation okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-01-30 | 231567 | POLY-116631 | Install Air Return Vent in Shop Door | 2017-02-01 - 13000 - Peter Lyberg-1/31 - Peter cut 2" off the bottom of the door for air flow. - Gayle Swenson | Install Air Return Vent in Shop Door 2017-02-01 - 13000 - Peter Lyberg-1/31 - Peter cut 2" off the bottom of the door for air flow. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-01-30 | 34836 | TMPE-215321 | Add AC shop: WE need to replace the domestic hot water circulation pump. PVE domestic hot water temperature at 100 degrees. Starting to get resident complaints. Please inspect and repair Submitted by 4N0JHK6 | 2017-01-30 - 23100 - Robert Dauscher-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher; 2017-01-30 - 23100 - Brian Qualls-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher; 2017-01-30 - 23100 - Jennifer Moyer-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher | Add AC shop: WE need to replace the domestic hot water circulation pump. PVE domestic hot water temperature at 100 degrees. Starting to get resident complaints. Please inspect and repair Submitted by 4N0JHK6 2017-01-30 - 23100 - Robert Dauscher-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher; 2017-01-30 - 23100 - Brian Qualls-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher; 2017-01-30 - 23100 - Jennifer Moyer-called by Steve at 1:15pm and told to pick up new pump for jobsite. On way back called by Brian and informed that Per John H. I could not leave without completing job. Was given NO information on pumps location. Was not given instruction on tasks needed to be performed to complete job. Was not given proper tools and supplies to perform task. Had to call Brian to bring needed parts and supplies. Since my van was out of service because of a dead battery...... With Brian and Jennifer's assistance we were able to complete the task. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-30 | 34892 | TMPE-215265 | PSF - F75: Bldg hot water pump #2, Y#364, has a broken coupling that needs to be repaired or replaced. Send to HVAC services 42B213C | 2017-02-01 - 23100 - Zhi Yu-We located the pump. We removed sleeve inspect coupling all torn-up. Not in stock at our shop, and have one in order. Will be in tomorrow. - Zhi Yu; 2017-02-01 - 23100 - Derek Gittings-We located the pump. We removed sleeve inspect coupling all torn-up. Not in stock at our shop, and have one in order. Will be in tomorrow. - Zhi Yu; 2017-02-14 - 23100 - Derek Gittings-replaced coupling and alined motot. - Derek Gittings | PSF - F75: Bldg hot water pump #2, Y#364, has a broken coupling that needs to be repaired or replaced. Send to HVAC services 42B213C 2017-02-01 - 23100 - Zhi Yu-We located the pump. We removed sleeve inspect coupling all torn-up. Not in stock at our shop, and have one in order. Will be in tomorrow. - Zhi Yu; 2017-02-01 - 23100 - Derek Gittings-We located the pump. We removed sleeve inspect coupling all torn-up. Not in stock at our shop, and have one in order. Will be in tomorrow. - Zhi Yu; 2017-02-14 - 23100 - Derek Gittings-replaced coupling and alined motot. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-01-30 | 34903 | TMPE-215254 | SPECIAL FUNDING - Replace coils for AHU 7. | 2017-03-22 - 18090 - Michael Kelley-checked to make sure AHU was running properly. Hot call for building. - Michael Kelley; 2017-03-22 - 18090 - Michael Kelley-Painted AHU insulation. Put in shut down request. - Michael Kelley; 2017-03-23 - 18090 - Michael Kelley-Rescheduled shut downs and hot work Permit - Michael Kelley; 2017-04-03 - 18090 - Michael Kelley-submitted parking requests for Comfort system. Addressed issue of hard pack insulation on Air Handlers. sent over report from greg. - Michael Kelley; 2017-04-28 - 18090 - Michael Kelley-opened door for contractor. Went over next job - Michael Kelley; 2017-04-28 - 18090 - Michael Kelley-sprayed pipes silver or red. Green was used to mark wear wear to cut insulation or possible Asbestos testing. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-contractor assist. Shutdown for AHU 7 5am for three days. Came in at 430 to assist Comfort systems. Insulation removal company did not show up tell 8am. Contacted Lucas with Asbestos program. Contractor did not recieve email with 5am start time. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-contractor assist. Crane day Assist with crane on job. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-shut down ended early. Assisted turning on the Airhandler. - Michael Kelley; 2017-05-10 - 18090 - Michael Kelley-Walked job with Steve, Found problem with drain pan. Pan Galvinized not stainless - Michael Kelley; 2017-05-18 - 18090 - Michael Kelley-checked job. done - Michael Kelley | SPECIAL FUNDING - Replace coils for AHU 7. 2017-03-22 - 18090 - Michael Kelley-checked to make sure AHU was running properly. Hot call for building. - Michael Kelley; 2017-03-22 - 18090 - Michael Kelley-Painted AHU insulation. Put in shut down request. - Michael Kelley; 2017-03-23 - 18090 - Michael Kelley-Rescheduled shut downs and hot work Permit - Michael Kelley; 2017-04-03 - 18090 - Michael Kelley-submitted parking requests for Comfort system. Addressed issue of hard pack insulation on Air Handlers. sent over report from greg. - Michael Kelley; 2017-04-28 - 18090 - Michael Kelley-opened door for contractor. Went over next job - Michael Kelley; 2017-04-28 - 18090 - Michael Kelley-sprayed pipes silver or red. Green was used to mark wear wear to cut insulation or possible Asbestos testing. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-contractor assist. Shutdown for AHU 7 5am for three days. Came in at 430 to assist Comfort systems. Insulation removal company did not show up tell 8am. Contacted Lucas with Asbestos program. Contractor did not recieve email with 5am start time. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-contractor assist. Crane day Assist with crane on job. - Michael Kelley; 2017-05-05 - 18090 - Michael Kelley-shut down ended early. Assisted turning on the Airhandler. - Michael Kelley; 2017-05-10 - 18090 - Michael Kelley-Walked job with Steve, Found problem with drain pan. Pan Galvinized not stainless - Michael Kelley; 2017-05-18 - 18090 - Michael Kelley-checked job. done - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-31 | 168932 | RFMT-139399 | Salvatore Marasco Jr reported-Found knob to thermostat set on 90. Blower was was set at off position. Turned blower on heard a rattling noise, removed front cover and stopped rattling noise. Found that the valve actuator was not working. Called Bill Hetzel to send out work request to A.C. technician. . . | 2017-02-01 - 18010 - Simon Fernandez-checked t-stat, fan sw.,and actuator,unit operating normally.explained to student about heating -cooling change over. - Simon Fernandez | Salvatore Marasco Jr reported-Found knob to thermostat set on 90. Blower was was set at off position. Turned blower on heard a rattling noise, removed front cover and stopped rattling noise. Found that the valve actuator was not working. Called Bill Hetzel to send out work request to A.C. technician. . . 2017-02-01 - 18010 - Simon Fernandez-checked t-stat, fan sw.,and actuator,unit operating normally.explained to student about heating -cooling change over. - Simon Fernandez | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-01-31 | 34664 | TMPE-215493 | Repair refrigerant leak at evap west rupture disk on Chiller 2. | 2017-05-15 - 30010 - not needed for fiscal year 2017. Will open a new work order for fiscal year 2018. - Lisa Anderson | Repair refrigerant leak at evap west rupture disk on Chiller 2. 2017-05-15 - 30010 - not needed for fiscal year 2017. Will open a new work order for fiscal year 2018. - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-31 | 34666 | TMPE-215491 | Repair refrigerant leaks on Chiller #7 at threaded plug on evaporator at sight glass (east) and pressure transmitter (2009 leak tag) | 2017-05-15 - 30010 - Not needed for fiscal year 2017. Will open a new work order for fiscal year 2018 - Lisa Anderson | Repair refrigerant leaks on Chiller #7 at threaded plug on evaporator at sight glass (east) and pressure transmitter (2009 leak tag) 2017-05-15 - 30010 - Not needed for fiscal year 2017. Will open a new work order for fiscal year 2018 - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-01-31 | 34741 | TMPE-215416 | LSD 2nd Flr It is reported, "The new evap cooler in the 2nd floor greenhouse does not have water running on the pads. West side. Please request repair. (It may just be turned off?) Please inspect and service accordingly at the earliest opportunity. Thank you. 42BLHKH | 2017-03-22 - 18150 - Roque Garcia-Checked the cooler and it checked out good. - Roque Garcia | LSD 2nd Flr It is reported, "The new evap cooler in the 2nd floor greenhouse does not have water running on the pads. West side. Please request repair. (It may just be turned off?) Please inspect and service accordingly at the earliest opportunity. Thank you. 42BLHKH 2017-03-22 - 18150 - Roque Garcia-Checked the cooler and it checked out good. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 168734 | RFMT-139597 | ASUHC-Agent: Ahmed Khalil Descrption: AC unit is spewing out strange chemical-like smell. Who was dispatched: Joe Swan Time: 10:15PM | 2017-02-02 - 18020 - Joe Swan-Could not detect any smell but did spray febreze air freshener - Joe Swan | ASUHC-Agent: Ahmed Khalil Descrption: AC unit is spewing out strange chemical-like smell. Who was dispatched: Joe Swan Time: 10:15PM 2017-02-02 - 18020 - Joe Swan-Could not detect any smell but did spray febreze air freshener - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
2017-02-01 | 2257 | WEST-108992 | HVAC-GENERAL-MA South | 2017-02-14 - 18010 - Chad T Ball-replaced air filters - Chad T Ball | HVAC-GENERAL-MA South 2017-02-14 - 18010 - Chad T Ball-replaced air filters - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 2258 | WEST-108991 | HVAC-GENERAL-MA North | 2017-02-14 - 18010 - Chad T Ball-replaced air filters - Chad T Ball | HVAC-GENERAL-MA North 2017-02-14 - 18010 - Chad T Ball-replaced air filters - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 2297 | WEST-108952 | Pump-SP-04-(EJECTOR) | 2017-02-03 - 23100 - Thomas Wienand-Unit scheduled for replacement no PM completed - Thomas Wienand | Pump-SP-04-(EJECTOR) 2017-02-03 - 23100 - Thomas Wienand-Unit scheduled for replacement no PM completed - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 2298 | WEST-108951 | Pump-SP-03-(EJECTOR) | 2017-02-03 - 23100 - Thomas Wienand-Unit removed for repairs but will be replaced. - Thomas Wienand | Pump-SP-03-(EJECTOR) 2017-02-03 - 23100 - Thomas Wienand-Unit removed for repairs but will be replaced. - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 2359 | WEST-108890 | Air Compressor-CAC-002 | 2017-02-15 - 18030 - Joseph McCormick-Greased and cleaned equipment. Checked air filter and belts. - Joseph McCormick | Air Compressor-CAC-002 2017-02-15 - 18030 - Joseph McCormick-Greased and cleaned equipment. Checked air filter and belts. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 2360 | WEST-108889 | Air Compressor-CAC-001 | 2017-02-14 - 18030 - Joseph McCormick-Tagged out. Valved off. Removed guard. Inspected belts and air filter. Wiped down equipment. Greased motor. Test ran. Drained moisture out of trap. - Joseph McCormick | Air Compressor-CAC-001 2017-02-14 - 18030 - Joseph McCormick-Tagged out. Valved off. Removed guard. Inspected belts and air filter. Wiped down equipment. Greased motor. Test ran. Drained moisture out of trap. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-02-01 | 251861 | DTPC-116677 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 251862 | DTPC-116676 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 251863 | DTPC-116675 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 251864 | DTPC-116674 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 251865 | DTPC-116673 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 251866 | DTPC-116672 | Pump | 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | Pump 2017-02-17 - 23100 - Thomas Klein-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein; 2017-02-17 - 23100 - Robert Bartels-Completed PM on pump and motor. Greased motor, checked all bolts blew down strainer etc. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 252011 | DTPC-116527 | Air Compressor | 2017-02-16 - 18030 - Steve Skibbe-annual pm preformed - Steve Skibbe; 2017-02-16 - 18030 - Robert Bartels-annual pm preformed - Steve Skibbe | Air Compressor 2017-02-16 - 18030 - Steve Skibbe-annual pm preformed - Steve Skibbe; 2017-02-16 - 18030 - Robert Bartels-annual pm preformed - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 252015 | DTPC-116523 | Pump | 2017-02-09 - 23100 - Steve Skibbe-annual pm preformed seals are not letting grease into the Bering on front of pump replaced front zerk as it was leaking at the cast . will address this later - Steve Skibbe | Pump 2017-02-09 - 23100 - Steve Skibbe-annual pm preformed seals are not letting grease into the Bering on front of pump replaced front zerk as it was leaking at the cast . will address this later - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 252085 | DTPC-116453 | Air Handler-Biannual | 2017-02-07 - xPM-0300.03-B - Ross Hossack-Completed PM.The bearings in the return fan motor are going out. - Ross Hossack; 2017-02-07 - xPM-0300.03-B - James Hermann-Completed PM. - Ross Hossack | Air Handler-Biannual 2017-02-07 - xPM-0300.03-B - Ross Hossack-Completed PM.The bearings in the return fan motor are going out. - Ross Hossack; 2017-02-07 - xPM-0300.03-B - James Hermann-Completed PM. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-02-01 | 252972 | DTPC-115566 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. These are the only two coolers that will be working. The other 12 coolers are becoming obsolete. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. These are the only two coolers that will be working. The other 12 coolers are becoming obsolete. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252973 | DTPC-115565 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. These are the only two coolers that will be working. The other 12 coolers are becoming obsolete. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. These are the only two coolers that will be working. The other 12 coolers are becoming obsolete. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252974 | DTPC-115564 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252975 | DTPC-115563 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252976 | DTPC-115562 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252977 | DTPC-115561 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252978 | DTPC-115560 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252979 | DTPC-115559 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252980 | DTPC-115558 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252981 | DTPC-115557 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252982 | DTPC-115556 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and cleaned the inside along with list of non working parts. This was performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252983 | DTPC-115555 | Evaporative Cooler-Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and did complete inspection on all pumps and pads. Dave Downing was the vendor who completed this. - Ralph Lemons | Evaporative Cooler-Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and did complete inspection on all pumps and pads. Dave Downing was the vendor who completed this. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-01 | 252984 | DTPC-115554 | Evaporative Cooler - Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and checked all parts. This cooler is going to be obsolete. All work performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler - Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and checked all parts. This cooler is going to be obsolete. All work performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 252985 | DTPC-115553 | Evaporative Cooler - Biannual | 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and checked all parts. This cooler is going to be obsolete. All work performed by Dave Downing and Assoc. - Ralph Lemons | Evaporative Cooler - Biannual 2017-01-11 - xPM-2000-B - Ralph Lemons-There was a winterizing performed at the end of October from Dave Downing and Associates. The next performance will be completed in February by Dave Downing. - Ralph Lemons; 2017-02-07 - xPM-2000-B - Ralph Lemons-Removed panels and checked all parts. This cooler is going to be obsolete. All work performed by Dave Downing and Assoc. - Ralph Lemons | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 31790 | TMPE-218367 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31791 | TMPE-218366 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31793 | TMPE-218364 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31794 | TMPE-218363 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31795 | TMPE-218362 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31796 | TMPE-218361 | Sidewalk condition and safety check-Monthly | 2017-02-16 - xPM-SWC-M - Karl Shisler-inspected around computing commons, and PE East found several spots that need addressed still need to inspect around Murdock and PE West, Armstrong and Ross Blakely - Karl Shisler | Sidewalk condition and safety check-Monthly 2017-02-16 - xPM-SWC-M - Karl Shisler-inspected around computing commons, and PE East found several spots that need addressed still need to inspect around Murdock and PE West, Armstrong and Ross Blakely - Karl Shisler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31797 | TMPE-218360 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31798 | TMPE-218359 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31799 | TMPE-218358 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31800 | TMPE-218357 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31801 | TMPE-218356 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31802 | TMPE-218355 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 31804 | TMPE-218353 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 34427 | TMPE-215730 | Please repair the circulating pump number 7848 in the basement of the EQ room at San Pablo | 2017-02-02 - 23100 - Brian Qualls-Pump bearings are going bad on this pump. It is able to be run if needed. Needs to be rebuilt. We do not have info on this machine. Changing priority to routine. - Brian Qualls; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-lock an tag pump/motor.remove pump/motor,replaced bearings,shaft seal,gasket,clean paint pump.install pump to motor.aline motor and pump rewire ,open water check for leaks.working well @ this time. - Jose Lopez | Please repair the circulating pump number 7848 in the basement of the EQ room at San Pablo 2017-02-02 - 23100 - Brian Qualls-Pump bearings are going bad on this pump. It is able to be run if needed. Needs to be rebuilt. We do not have info on this machine. Changing priority to routine. - Brian Qualls; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-20 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-02-27 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-03 - 23100 - Jose Lopez-lock an tag pump/motor.remove pump/motor,replaced bearings,shaft seal,gasket,clean paint pump.install pump to motor.aline motor and pump rewire ,open water check for leaks.working well @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6
2017-02-01 | 34436 | TMPE-215721 | For ems Robert Borucki Check operations of chill water and hot water heating pumps. 42A7J3M | 2017-04-20 - 18080 - Robert Borucki-Removed unused control relays from control panel. - Robert Borucki; 2017-04-27 - 18080 - Robert Borucki-Removed unused controls,installed new rib relays, and checked operation of equipment. - Robert Borucki | For ems Robert Borucki Check operations of chill water and hot water heating pumps. 42A7J3M 2017-04-20 - 18080 - Robert Borucki-Removed unused control relays from control panel. - Robert Borucki; 2017-04-27 - 18080 - Robert Borucki-Removed unused controls,installed new rib relays, and checked operation of equipment. - Robert Borucki | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-01 | 34471 | TMPE-215686 | Make up air unit is making noise. Possible belt or bearing. The unit is exposed because of a construction project we have going on at CP. I would like to have someone come out and take look. Room 121C Unit Number AF1 42CFMD8 | 2017-05-13 - 18010 - Robert Dauscher-checked unit. replaced and tightened belt - Robert Dauscher | Make up air unit is making noise. Possible belt or bearing. The unit is exposed because of a construction project we have going on at CP. I would like to have someone come out and take look. Room 121C Unit Number AF1 42CFMD8 2017-05-13 - 18010 - Robert Dauscher-checked unit. replaced and tightened belt - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 34479 | TMPE-215678 | a/h #11..y-6105 has a bad 4-bolt flange inboard bearing.9 located above the dock 0 | NA | a/h #11..y-6105 has a bad 4-bolt flange inboard bearing.9 located above the dock 0 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-01 | 34485 | TMPE-215672 | HVAC shop per Scot Wilson, Please come and check the venting of the hot water heater. We have had it shutdown two days in a row therefore Scot and the Uclub would like to know that it is operating properly. If there is a charge for this please use FC202000265. Thanks! 42B60NN | 2017-02-02 - 18010 - Robert Ecabert-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert; 2017-02-02 - 18010 - Robert Ecabert-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert; 2017-02-02 - 18010 - Carl Karr-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert | HVAC shop per Scot Wilson, Please come and check the venting of the hot water heater. We have had it shutdown two days in a row therefore Scot and the Uclub would like to know that it is operating properly. If there is a charge for this please use FC202000265. Thanks! 42B60NN 2017-02-02 - 18010 - Robert Ecabert-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert; 2017-02-02 - 18010 - Robert Ecabert-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert; 2017-02-02 - 18010 - Carl Karr-We were sent there on a trouble call saying hot water heater was tripping the breaker since the new flue pipe was installed. We were able to trouble shoot the electrical problem to a grounded in line water pump. We replaced the bad water pump with a new pump and it is running fine and the customer is happy. - Robert Ecabert | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-02-01 | 34562 | TMPE-215595 | !! Humidifier appears to have stopped functioning. Can someone from HVAC shop or familiar with the unit take a look as soon as possible. This has effect on animal holding rooms! For entrance please ring bell or call me (Mike, 480-227-3476) Thank you! -Mike Contact Name: Michael Comroe Cont. . . | 2017-02-03 - 18010 - Zhi Yu-Arrived at LSB. The Dri-Steem alarms code ( Excessive fill time Active. We diagnose NO RO Water pressure. We trace the pipe down to first floor and to LSA . We lose track. will need more help. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-We back on Monday. Doing little more digging. I going through ceiling to ceiling and EQ room from LSB to LSA before the tunnel. I Checking for any valve that's partial close, all valve are open. I call central plant what pressure reading do they have, Is about 40 - 45 psi. I also when down LSC down to the ( Dungeon) where there's new booster pump was install 1 1/2 years age. Ro Supply @ 25 psi.We add plumbing to join our investigate. - Zhi Yu [Modified: 2017-02-13 Zhi Yu]; 2017-02-13 - 18010 - Zhi Yu-We have Lou's the Plumbing join our investigate on the RO pressure. We go through our money foot step, from LSB to LSA. We check pressure in the subbasement where the RO come in. The first adjacent room is @23psi, Rooms further down hall pressure @23-25. Lou's take reading room above us @15-17 psi. There is no booster pump. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-Thursday morning got John's permission to take an actual RO reading in Central plant putout @ 40 psi. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-after the PSH Ro training. I went back to diagnose is anything we can do to get them humidity. I find out the penn valve and belimo actuator leaking through. I temporary bypass them and trying fill the tank. - Zhi Yu; 2017-02-14 - 18010 - Zhi Yu-Picking up material form United Refrigeration. and shut off unit to cold down. - Zhi Yu; 2017-02-16 - 18010 - Jennifer Moyer-Replace Penn valve, replace Belimo valve, clean and tune burners. Order hot surface igniters. - Jennifer Moyer; 2017-02-16 - 18010 - Zhi Yu-Replace Penn valve, replace Belimo valve, clean and tune burners. Order hot surface igniters. - Jennifer Moyer; 2017-02-24 - 18010 - Zhi Yu-follow up call unit operate normal condition. - Zhi Yu | !! Humidifier appears to have stopped functioning. Can someone from HVAC shop or familiar with the unit take a look as soon as possible. This has effect on animal holding rooms! For entrance please ring bell or call me (Mike, 480-227-3476) Thank you! -Mike Contact Name: Michael Comroe Cont. . . 2017-02-03 - 18010 - Zhi Yu-Arrived at LSB. The Dri-Steem alarms code ( Excessive fill time Active. We diagnose NO RO Water pressure. We trace the pipe down to first floor and to LSA . We lose track. will need more help. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-We back on Monday. Doing little more digging. I going through ceiling to ceiling and EQ room from LSB to LSA before the tunnel. I Checking for any valve that's partial close, all valve are open. I call central plant what pressure reading do they have, Is about 40 - 45 psi. I also when down LSC down to the ( Dungeon) where there's new booster pump was install 1 1/2 years age. Ro Supply @ 25 psi.We add plumbing to join our investigate. - Zhi Yu [Modified: 2017-02-13 Zhi Yu]; 2017-02-13 - 18010 - Zhi Yu-We have Lou's the Plumbing join our investigate on the RO pressure. We go through our money foot step, from LSB to LSA. We check pressure in the subbasement where the RO come in. The first adjacent room is @23psi, Rooms further down hall pressure @23-25. Lou's take reading room above us @15-17 psi. There is no booster pump. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-Thursday morning got John's permission to take an actual RO reading in Central plant putout @ 40 psi. - Zhi Yu; 2017-02-13 - 18010 - Zhi Yu-after the PSH Ro training. I went back to diagnose is anything we can do to get them humidity. I find out the penn valve and belimo actuator leaking through. I temporary bypass them and trying fill the tank. - Zhi Yu; 2017-02-14 - 18010 - Zhi Yu-Picking up material form United Refrigeration. and shut off unit to cold down. - Zhi Yu; 2017-02-16 - 18010 - Jennifer Moyer-Replace Penn valve, replace Belimo valve, clean and tune burners. Order hot surface igniters. - Jennifer Moyer; 2017-02-16 - 18010 - Zhi Yu-Replace Penn valve, replace Belimo valve, clean and tune burners. Order hot surface igniters. - Jennifer Moyer; 2017-02-24 - 18010 - Zhi Yu-follow up call unit operate normal condition. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 7
2017-02-01 | 35052 | TMPE-215105 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 35053 | TMPE-215104 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 35289 | TMPE-214868 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-01 | 35291 | TMPE-214866 | Air Compressor-Biannual | 2017-02-01 - xPM-0100-B - Matthew Smith-Changed the oil and the filters on pump 1. Checked connections and tightened any that were leaking. Found that pump 2 was low on oil topped off the oil sump. Cleaned the air compressor and changed the oil absorbing pads. - Matthew Smith | Air Compressor-Biannual 2017-02-01 - xPM-0100-B - Matthew Smith-Changed the oil and the filters on pump 1. Checked connections and tightened any that were leaking. Found that pump 2 was low on oil topped off the oil sump. Cleaned the air compressor and changed the oil absorbing pads. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-02-01 | 35572 | TMPE-214585 | Vehicle Inspection-Monthly | 2017-02-02 - xPM-VEH-M - Gail Jackson-Wash and clean vehicle inside and out. Vehicle was just returned from repair shop with with new fuel pump installed. They also inspect. - Gail Jackson | Vehicle Inspection-Monthly 2017-02-02 - xPM-VEH-M - Gail Jackson-Wash and clean vehicle inside and out. Vehicle was just returned from repair shop with with new fuel pump installed. They also inspect. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-02 | 165061 | RFMT-143270 | Proactive Activity Report | 2017-04-05 - 10010 - John Romero-R/R AC fan motor - Yvette Castro | Proactive Activity Report 2017-04-05 - 10010 - John Romero-R/R AC fan motor - Yvette Castro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-02 | 168719 | RFMT-139612 | RES LIFE / Scott: B3 elevator lobby, please clean wall pak and replace filter. | 2017-02-02 - 10010 - Scott Berndt-cleaned and replaced a/c filter ...vacuum and removed and cleaned in the vent... - Scott Berndt | RES LIFE / Scott: B3 elevator lobby, please clean wall pak and replace filter. 2017-02-02 - 10010 - Scott Berndt-cleaned and replaced a/c filter ...vacuum and removed and cleaned in the vent... - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-02 | 2152 | WEST-109097 | Replace the filter on this drinking fountain. | NA | Replace the filter on this drinking fountain. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-02 | 231390 | POLY-116808 | air filters bathtub is dripping Contact Name: Contact Phone Number: 7205394169 Contact Email: 4NE2L94 | NA | air filters bathtub is dripping Contact Name: Contact Phone Number: 7205394169 Contact Email: 4NE2L94 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-02 | 231403 | POLY-116795 | replace compressor #1 in h/p#2 4O216EO | 2017-02-15 - 18030 - Allan Blair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Suresh Nair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Darusman Amin-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Darusman Amin-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Allan Blair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Suresh Nair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Esli Arvizo-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-05-01 - 18030 - Esli Arvizo-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Suresh Nair-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Darusman Amin-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Darusman Amin-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark | replace compressor #1 in h/p#2 4O216EO 2017-02-15 - 18030 - Allan Blair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Suresh Nair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Darusman Amin-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Darusman Amin-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Allan Blair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Suresh Nair-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-02-15 - 18030 - Esli Arvizo-RECOVER CHARGE, REMOVE COMPRESSOR, INSTALL NEW COMPRESSOR AND LIQUID LINE FILTER DRYER, EVACUATED AND RECHARGED. FOUND OD FAN MOTOR AND 4-WAY VALVE COIL BAD. ORDRED NEW PARTS - Steve Clark; 2017-05-01 - 18030 - Esli Arvizo-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Suresh Nair-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Darusman Amin-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark; 2017-05-01 - 18030 - Darusman Amin-REPLACED TXV AND CHECKED UNIT OPERATION - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7
2017-02-02 | 231414 | POLY-116784 | Exterior wall lights need to be repaired. 42B97GA | 2017-02-09 - 15040 - Reynaldo Martinez-2/2 - Ray checked out the lighting issue, and will replace the rib relay tomorrow. Problem corrected by Steve and Ryan. Lighting schedule reprogrammed. No need to replaced the relay. - Gayle Swenson | Exterior wall lights need to be repaired. 42B97GA 2017-02-09 - 15040 - Reynaldo Martinez-2/2 - Ray checked out the lighting issue, and will replace the rib relay tomorrow. Problem corrected by Steve and Ryan. Lighting schedule reprogrammed. No need to replaced the relay. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-02 | 34212 | TMPE-215945 | HEPA filters in MBE lab (ERC 164) are not blowing air. When the fan switches are thrown, a relay can be heard in the ceiling, but the fans do not turn and no air flow can be felt. Contact Name: Stephen Schaefer Contact Phone Number: 520-591-9140 Contact Email: Stephen.T.Schaefer@asu.edu 4O10GI5 | 2017-02-07 - 18170 - Gail Jackson-Clean room; must suite up to enter. Starters turn on by 120v switches on S wall, but, fans do not run. Could not find Breaker for fans; added electricians to work order to trace wiring. Extreme Caution is required; must work of 10 ft ladder to access equipment, space is very tight for ladders. - Gail Jackson; 2017-02-07 - 18170 - Robert Dauscher-Clean room; must suite up to enter. Starters turn on by 120v switches on S wall, but, fans do not run. Could not find Breaker for fans; added electricians to work order to trace wiring. Extreme Caution is required; must work of 10 ft ladder to access equipment, space is very tight for ladders. - Gail Jackson; 2017-02-09 - 18170 - Gail Jackson-Continued search for 480 volt motor breakers for HEPA filter system, was aided in search by 2 electricians; could not find. Found starter for 1, but, could not access because of limited space and height. Joel said he would pull up electrical wiring drawings for that building and get back. - Gail Jackson; 2017-02-09 - 18170 - Thomas Gibble-Continued search for 480 volt motor breakers for HEPA filter system, was aided in search by 2 electricians; could not find. Found starter for 1, but, could not access because of limited space and height. Joel said he would pull up electrical wiring drawings for that building and get back. - Gail Jackson; 2017-04-07 - 18170 - Gail Jackson-Size up for new plenum. - Gail Jackson; 2017-04-07 - 18170 - Carl Karr-Size up for new plenum. - Gail Jackson; 2017-04-20 - 18170 - Gail Jackson-Electrical shop has parts ordered for these units, will install when comes in. - Gail Jackson | HEPA filters in MBE lab (ERC 164) are not blowing air. When the fan switches are thrown, a relay can be heard in the ceiling, but the fans do not turn and no air flow can be felt. Contact Name: Stephen Schaefer Contact Phone Number: 520-591-9140 Contact Email: Stephen.T.Schaefer@asu.edu 4O10GI5 2017-02-07 - 18170 - Gail Jackson-Clean room; must suite up to enter. Starters turn on by 120v switches on S wall, but, fans do not run. Could not find Breaker for fans; added electricians to work order to trace wiring. Extreme Caution is required; must work of 10 ft ladder to access equipment, space is very tight for ladders. - Gail Jackson; 2017-02-07 - 18170 - Robert Dauscher-Clean room; must suite up to enter. Starters turn on by 120v switches on S wall, but, fans do not run. Could not find Breaker for fans; added electricians to work order to trace wiring. Extreme Caution is required; must work of 10 ft ladder to access equipment, space is very tight for ladders. - Gail Jackson; 2017-02-09 - 18170 - Gail Jackson-Continued search for 480 volt motor breakers for HEPA filter system, was aided in search by 2 electricians; could not find. Found starter for 1, but, could not access because of limited space and height. Joel said he would pull up electrical wiring drawings for that building and get back. - Gail Jackson; 2017-02-09 - 18170 - Thomas Gibble-Continued search for 480 volt motor breakers for HEPA filter system, was aided in search by 2 electricians; could not find. Found starter for 1, but, could not access because of limited space and height. Joel said he would pull up electrical wiring drawings for that building and get back. - Gail Jackson; 2017-04-07 - 18170 - Gail Jackson-Size up for new plenum. - Gail Jackson; 2017-04-07 - 18170 - Carl Karr-Size up for new plenum. - Gail Jackson; 2017-04-20 - 18170 - Gail Jackson-Electrical shop has parts ordered for these units, will install when comes in. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-02-02 | 34284 | TMPE-215873 | Art warehouse - 130: They are using high powered torches in class today and the room is extremely warm - please cool it down a couple degrees. | 2017-02-09 - 18290 - Robert Ecabert-I have assessed the situation for what is needed to repair the air conditioning units at Arts ware house and I will fix the air conditioning units tomorrow. - Robert Ecabert; 2017-02-09 - 18290 - Robert Ecabert-I installed a new belt and adjusted the motor on air conditioning unit Y# 6784 and this unit works just fine but the customer did not know how to turn the air conditioning unit on in the cooling mode but she does now. On air conditioning unit Y#6788 the thermostat was falling off the wall so I remounted it securely to the wall and this air conditioning unit works fine and she now knows how to operate the thermostat. I also checked out Y#6786 that also serves this room 130 and I is working fine and she now knows how to operate the thermostat. - Robert Ecabert | Art warehouse - 130: They are using high powered torches in class today and the room is extremely warm - please cool it down a couple degrees. 2017-02-09 - 18290 - Robert Ecabert-I have assessed the situation for what is needed to repair the air conditioning units at Arts ware house and I will fix the air conditioning units tomorrow. - Robert Ecabert; 2017-02-09 - 18290 - Robert Ecabert-I installed a new belt and adjusted the motor on air conditioning unit Y# 6784 and this unit works just fine but the customer did not know how to turn the air conditioning unit on in the cooling mode but she does now. On air conditioning unit Y#6788 the thermostat was falling off the wall so I remounted it securely to the wall and this air conditioning unit works fine and she now knows how to operate the thermostat. I also checked out Y#6786 that also serves this room 130 and I is working fine and she now knows how to operate the thermostat. - Robert Ecabert | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-02 | 34381 | TMPE-215776 | One of the two heating units in APMA 132 doesn't work. There is a yoga class held there on Mondays and Wednesdays and they need to be able to heat up the room warmer than 70 degrees. Would it be possible to send someone out to fix this? Thank you. 4O25GF6 | 2017-05-13 - 18300 - Robert Dauscher-locate and address issue with gas valves being closed inside of all gas fired units on Building. Found induced motor bad on 1 unit. picked up from supply house to install next day - Robert Dauscher; 2017-05-13 - 18300 - Robert Dauscher-returned to install induced draft motor. found return air plugged on both systems. need to return at a later date with help to use lift and clean grills - Robert Dauscher; 2017-05-13 - 18300 - Robert Dauscher-used man lift to clean 4 return air grills. Wes J. Assisted per regulations. - Robert Dauscher; 2017-05-13 - 18300 - Gail Jackson-used man lift to clean 4 return air grills. Wes J. Assisted per regulations. - Robert Dauscher | One of the two heating units in APMA 132 doesn't work. There is a yoga class held there on Mondays and Wednesdays and they need to be able to heat up the room warmer than 70 degrees. Would it be possible to send someone out to fix this? Thank you. 4O25GF6 2017-05-13 - 18300 - Robert Dauscher-locate and address issue with gas valves being closed inside of all gas fired units on Building. Found induced motor bad on 1 unit. picked up from supply house to install next day - Robert Dauscher; 2017-05-13 - 18300 - Robert Dauscher-returned to install induced draft motor. found return air plugged on both systems. need to return at a later date with help to use lift and clean grills - Robert Dauscher; 2017-05-13 - 18300 - Robert Dauscher-used man lift to clean 4 return air grills. Wes J. Assisted per regulations. - Robert Dauscher; 2017-05-13 - 18300 - Gail Jackson-used man lift to clean 4 return air grills. Wes J. Assisted per regulations. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-02-03 | 168653 | RFMT-139678 | RES LIFE / Thor: Please check the operation of elevator room a/c. Received call from TK, a/c acting up. | 2017-02-10 - 18010 - Thor Millsaps-Thermostat batteries had died. Wired thermostat to use common + 24v from transformer for power. Removed batteries. Replaced condenser fan motor with Carrier OEM motor (1). 1/4 HP, 460v, 1100/900 rpm, cw rot - Thor Millsaps | RES LIFE / Thor: Please check the operation of elevator room a/c. Received call from TK, a/c acting up. 2017-02-10 - 18010 - Thor Millsaps-Thermostat batteries had died. Wired thermostat to use common + 24v from transformer for power. Removed batteries. Replaced condenser fan motor with Carrier OEM motor (1). 1/4 HP, 460v, 1100/900 rpm, cw rot - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-02-03 | 2142 | WEST-109107 | Monitor operations for the new glycol pump at SDFC. | 2017-02-03 - 23100 - Thomas Wienand-System Operational energy and flow total still not reading correctly - Thomas Wienand; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. BTU meter is showing 0gpm because of air bubbles. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. BTU meter is showing 0gpm because of air bubbles. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking solar heating system and venting air. BTU meter reading intermittently. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-13 - 23100 - Thomas Wienand-System appears to be working properly at this time - Thomas Wienand | Monitor operations for the new glycol pump at SDFC. 2017-02-03 - 23100 - Thomas Wienand-System Operational energy and flow total still not reading correctly - Thomas Wienand; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. BTU meter is showing 0gpm because of air bubbles. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. BTU meter is showing 0gpm because of air bubbles. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking solar heating system and venting air. BTU meter reading intermittently. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-09 - 23100 - Ronald Chaffee-Checking operation and venting system. - Ronald Chaffee; 2017-02-13 - 23100 - Thomas Wienand-System appears to be working properly at this time - Thomas Wienand | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-03 | 34184 | TMPE-215973 | ECC ROOF There's a cooler on the roof towards the middle that is leaking. Please send someone from HVAC. | 2017-05-10 - 18100 - Jennifer Moyer-Customer states that it is no longer leaking. - Jennifer Moyer | ECC ROOF There's a cooler on the roof towards the middle that is leaking. Please send someone from HVAC. 2017-05-10 - 18100 - Jennifer Moyer-Customer states that it is no longer leaking. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-03 | 34185 | TMPE-215972 | SWO HVAC to assist contractor and adjust air to RO tank on the roof of PSH PO# PL602003950 CPMG Project # 11688 Cost approved is NOT TO EXCEED $900.00 with out prior authorization. ~ DJP 4NB5JGJ | 2017-02-16 - 18010 - Michael Kelley-lock out tag out on RO cir pump on penthouse. Walked job with Onear, Steve, Contractor. Tried to understand problem. - Michael Kelley; 2017-03-03 - 18010 - Michael Kelley-assited contractor with tracing control problem for RO tank circulating pump - Michael Kelley; 2017-05-08 - 18010 - Michael Kelley-checked unit. union leeking. jopb complete - Michael Kelley | SWO HVAC to assist contractor and adjust air to RO tank on the roof of PSH PO# PL602003950 CPMG Project # 11688 Cost approved is NOT TO EXCEED $900.00 with out prior authorization. ~ DJP 4NB5JGJ 2017-02-16 - 18010 - Michael Kelley-lock out tag out on RO cir pump on penthouse. Walked job with Onear, Steve, Contractor. Tried to understand problem. - Michael Kelley; 2017-03-03 - 18010 - Michael Kelley-assited contractor with tracing control problem for RO tank circulating pump - Michael Kelley; 2017-05-08 - 18010 - Michael Kelley-checked unit. union leeking. jopb complete - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-02-03 | 34194 | TMPE-215963 | We are going to purchase a new air compressor. It will need new copper plumbing and electrical hookup. The unit will be in room 120. Please stop by room 101 and ask for Jim. I will need an estimate. Thank you, Jim 42C4IO9 154701 | 2017-02-03 - 18030 - Plumbing not needed as per James Maker: The ETS structure shop will be doing the plumbing not facilities othe PO will be only for the electrical hook up work from facilities. - Jeri Zappanti | We are going to purchase a new air compressor. It will need new copper plumbing and electrical hookup. The unit will be in room 120. Please stop by room 101 and ask for Jim. I will need an estimate. Thank you, Jim 42C4IO9 154701 2017-02-03 - 18030 - Plumbing not needed as per James Maker: The ETS structure shop will be doing the plumbing not facilities othe PO will be only for the electrical hook up work from facilities. - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-05 | 168612 | RFMT-139719 | !! Repeat Request. air conditioning cooling does not work. 4O0LMJ9 | 2017-02-06 - 18010 - Simon Fernandez-checked fan coil unit found coil clogged,flushed coil air supply at 60F.Also noticed isolation valves in the closed position all valves, notified central plant and Bill Hetzal. - Simon Fernandez; 2017-02-06 - 18010 - Thor Millsaps-c.a.r. - Simon Fernandez | !! Repeat Request. air conditioning cooling does not work. 4O0LMJ9 2017-02-06 - 18010 - Simon Fernandez-checked fan coil unit found coil clogged,flushed coil air supply at 60F.Also noticed isolation valves in the closed position all valves, notified central plant and Bill Hetzal. - Simon Fernandez; 2017-02-06 - 18010 - Thor Millsaps-c.a.r. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-02-05 | 231445 | POLY-116753 | Coils | 2017-05-02 - 18090 - building not occupied - t'stat set at 85c /60h - Steve Clark | Coils 2017-05-02 - 18090 - building not occupied - t'stat set at 85c /60h - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-05 | 33438 | TMPE-216719 | HC- Sofia G Walk in Cooler in memorial Union is running warm and needs to be looked at Dispatched to: Robert Dauscher Time: 4:48 | 2017-02-06 - 18100 - Robert Dauscher-responded to help desk call. received call at 4:51pm, just before end of shift. was informed that box had gone down at 11:30pm on Saturday night, and was just called in at 4:30pm Sunday. Due to Market management not returning calls. Checked unit found no operational errors...... Box temp at 37\\xb0 on arrival. Will recheck on Monday AM. - Robert Dauscher; 2017-02-06 - 18100 - Robert Dauscher-Returned in both AM and PM to verify proper operation. on Both visits found door to walk-in open on arrival. Box was 37\\xb0in AM, and 38\\xb0 in PM with lots of fresh product stocked in since AM. Box is working properly Possible loss of condenser water or a intermittent sticky defrost control.... are possible reasons for the conditions that were reported. - Robert Dauscher | HC- Sofia G Walk in Cooler in memorial Union is running warm and needs to be looked at Dispatched to: Robert Dauscher Time: 4:48 2017-02-06 - 18100 - Robert Dauscher-responded to help desk call. received call at 4:51pm, just before end of shift. was informed that box had gone down at 11:30pm on Saturday night, and was just called in at 4:30pm Sunday. Due to Market management not returning calls. Checked unit found no operational errors...... Box temp at 37\\xb0 on arrival. Will recheck on Monday AM. - Robert Dauscher; 2017-02-06 - 18100 - Robert Dauscher-Returned in both AM and PM to verify proper operation. on Both visits found door to walk-in open on arrival. Box was 37\\xb0in AM, and 38\\xb0 in PM with lots of fresh product stocked in since AM. Box is working properly Possible loss of condenser water or a intermittent sticky defrost control.... are possible reasons for the conditions that were reported. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-02-06 | 150441 | RNLD-100860 | STEVE - PLEASE CHECK ON THIS ASAP. THANKS. !! AC unit is not working, neither is the compressor for the AC unit Contact Name: Bailey Dunn Contact Phone Number: Contact Email: dunn_baliey@ymail.com 4NG6A72 | 2017-02-07 - 18010 - Steve Clark-2/6 - Steve gave this work order to George Vasquez to handle. - Gayle Swenson | STEVE - PLEASE CHECK ON THIS ASAP. THANKS. !! AC unit is not working, neither is the compressor for the AC unit Contact Name: Bailey Dunn Contact Phone Number: Contact Email: dunn_baliey@ymail.com 4NG6A72 2017-02-07 - 18010 - Steve Clark-2/6 - Steve gave this work order to George Vasquez to handle. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-06 | 168509 | RFMT-139822 | !! Air conditioner needs maintenance. Not giving the cooling effect it should give. Please check and repair it. Contact Name: Contact Phone Number: 6692121597 Contact Email: 4O4A4N4 | 2017-02-08 - 18010 - Thomas Zambrano-cooling is working ok. temp at vent was 60\\xb0. - Thomas Zambrano | !! Air conditioner needs maintenance. Not giving the cooling effect it should give. Please check and repair it. Contact Name: Contact Phone Number: 6692121597 Contact Email: 4O4A4N4 2017-02-08 - 18010 - Thomas Zambrano-cooling is working ok. temp at vent was 60\\xb0. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-06 | 2087 | WEST-109162 | Filter in this fountain needs to be replaced. | NA | Filter in this fountain needs to be replaced. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-06 | 211937 | RACC-116673 | Standard room turn with quarter clean in bathroom and bedroom. Charge resident Jannie Kozicki $35 (qtr clean bedroom and qtr clean bthrm split 4 ways). Room walk conducted by SAlevy and JPaskvan. 4NN7C8M | NA | Standard room turn with quarter clean in bathroom and bedroom. Charge resident Jannie Kozicki $35 (qtr clean bedroom and qtr clean bthrm split 4 ways). Room walk conducted by SAlevy and JPaskvan. 4NN7C8M NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-02-06 | 211957 | RACC-116653 | !! The chain broke and came out of my fan once again. so now I cant turn my fan on. And my air conditioning is broken.. my room is like a sweat box right now 4NI4IFO | 2017-02-08 - 10010 - A/C is working fine. replaced cord on fine - Jim Deal | !! The chain broke and came out of my fan once again. so now I cant turn my fan on. And my air conditioning is broken.. my room is like a sweat box right now 4NI4IFO 2017-02-08 - 10010 - A/C is working fine. replaced cord on fine - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-02-06 | 33358 | TMPE-216799 | !! A strong chemical smell is reported in LSE 218. Occupants would like it checked out ASAP, please. Thank you. 42BLHKH | 2017-02-06 - 18020 - Called to John Crocker - Jeri Zappanti; 2017-02-06 - 18020 - John Crocker-Checked Above Tiles, 3rd Floor Rooms. Nothing Leaking. Smell Coming Through Vents TRANSFER TO HVAC SHOP 1 hr - John Crocker | !! A strong chemical smell is reported in LSE 218. Occupants would like it checked out ASAP, please. Thank you. 42BLHKH 2017-02-06 - 18020 - Called to John Crocker - Jeri Zappanti; 2017-02-06 - 18020 - John Crocker-Checked Above Tiles, 3rd Floor Rooms. Nothing Leaking. Smell Coming Through Vents TRANSFER TO HVAC SHOP 1 hr - John Crocker | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3
2017-02-06 | 33372 | TMPE-216785 | !! Please initiate a work order for HVAC to reset the temperature on one of the chillers in LSC L2-45U1 at their earliest opportunity. Contact for this request (to identify which chiller) is Dave Lowry, Office: LSC L2-32, Telephone: 480.965.3210. Thank you. 42BLHKH | 2017-02-09 - 18080 - Robert Ecabert-Dave Lowry and i cleaned out the inline water filter for his closed loop chilled water that went to his chiller and we installed a new inline water filter and he said that is all he wants to do to the system for today. Dave said he will call me in the next few days if he wants to do any thing else to the system,like try to turn the temperature down on the chiller. de - Robert Ecabert; 2017-02-23 - 18080 - Robert Ecabert-The work order request for the water temperature to be turned down on a chiller. The problem is that the temperature in the is room is over 104 degrees and that is why the water temperature is so high. Also the exhaust fan for that room was not working,but I repaired it and it is working now. This room also has a spot cool for this room,but this spot cool has broken and does not work any longer. The spot cool acts like it is out of refrigerant or the valves are out of the compressor. In any case Dave Lowry does not want to spend any more money on this unit. Dave Lowry is going to buy a new spot cool to put in this room. - Robert Ecabert | !! Please initiate a work order for HVAC to reset the temperature on one of the chillers in LSC L2-45U1 at their earliest opportunity. Contact for this request (to identify which chiller) is Dave Lowry, Office: LSC L2-32, Telephone: 480.965.3210. Thank you. 42BLHKH 2017-02-09 - 18080 - Robert Ecabert-Dave Lowry and i cleaned out the inline water filter for his closed loop chilled water that went to his chiller and we installed a new inline water filter and he said that is all he wants to do to the system for today. Dave said he will call me in the next few days if he wants to do any thing else to the system,like try to turn the temperature down on the chiller. de - Robert Ecabert; 2017-02-23 - 18080 - Robert Ecabert-The work order request for the water temperature to be turned down on a chiller. The problem is that the temperature in the is room is over 104 degrees and that is why the water temperature is so high. Also the exhaust fan for that room was not working,but I repaired it and it is working now. This room also has a spot cool for this room,but this spot cool has broken and does not work any longer. The spot cool acts like it is out of refrigerant or the valves are out of the compressor. In any case Dave Lowry does not want to spend any more money on this unit. Dave Lowry is going to buy a new spot cool to put in this room. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 8
2017-02-07 | 168451 | RFMT-139880 | !! Air conditioner is on, but not blowing air and giving off a weird smell Contact Name: Contact Phone Number: 6029199164 Contact Email: 4NNN6DA | 2017-02-08 - 18020 - Chester Duncan-Replaced motor and cap run Cleaned squirrel cage - Chester Duncan | !! Air conditioner is on, but not blowing air and giving off a weird smell Contact Name: Contact Phone Number: 6029199164 Contact Email: 4NNN6DA 2017-02-08 - 18020 - Chester Duncan-Replaced motor and cap run Cleaned squirrel cage - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-07 | 2063 | WEST-109186 | Need the power disconnected from the door air compressor on the UCB west side lobby area so it can be used to replace the bad compressor on the east side. Please see Tim for details. | 2017-03-07 - 15000 - Joseph Danielek-tim had talked to me about this but never got back with me. going to close wo. - Joseph Danielek | Need the power disconnected from the door air compressor on the UCB west side lobby area so it can be used to replace the bad compressor on the east side. Please see Tim for details. 2017-03-07 - 15000 - Joseph Danielek-tim had talked to me about this but never got back with me. going to close wo. - Joseph Danielek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-07 | 33137 | TMPE-217020 | Also there is some A/C duct material that needs to be removed from the room. I have attached pictures. | 2017-02-16 - 18010 - Carl Karr-Contacted Jim M. He said he will have a student throw the items away,since we can not use them. - Carl Karr | Also there is some A/C duct material that needs to be removed from the room. I have attached pictures. 2017-02-16 - 18010 - Carl Karr-Contacted Jim M. He said he will have a student throw the items away,since we can not use them. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-02-07 | 33152 | TMPE-217005 | !! Walk in cooler in back stock is not holding its temperature. | 2017-02-15 - 18010 - Thomas Gibble-turn off one of the cond section to melt the ice on evaporator coil - Thomas Gibble; 2017-02-15 - 18010 - Gail Jackson-turn off one of the cond section to melt the ice on evaporator coil - Thomas Gibble; 2017-02-17 - 18010 - Thomas Gibble-de iced walk-in and checked unit - Thomas Gibble; 2017-02-17 - 18010 - Gail Jackson-de iced walk-in and checked unit - Thomas Gibble; 2017-03-01 - 18010 - Thomas Gibble-replaced refroze timer - Thomas Gibble; 2017-03-01 - 18010 - Gail Jackson-replaced refroze timer - Thomas Gibble | !! Walk in cooler in back stock is not holding its temperature. 2017-02-15 - 18010 - Thomas Gibble-turn off one of the cond section to melt the ice on evaporator coil - Thomas Gibble; 2017-02-15 - 18010 - Gail Jackson-turn off one of the cond section to melt the ice on evaporator coil - Thomas Gibble; 2017-02-17 - 18010 - Thomas Gibble-de iced walk-in and checked unit - Thomas Gibble; 2017-02-17 - 18010 - Gail Jackson-de iced walk-in and checked unit - Thomas Gibble; 2017-03-01 - 18010 - Thomas Gibble-replaced refroze timer - Thomas Gibble; 2017-03-01 - 18010 - Gail Jackson-replaced refroze timer - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-08 | 30171 | TMPE-219986 | Request for Estimate. Requesting an estimate for an ice machine to be installed. There is an existing water line that houses a water purifier, we are hoping to split into. The ice machine is a floor model and not a counter top. It is located just below the counter top water purifier however, Thank y. . . | 2017-02-27 - 18010 - Gail Jackson-Trip ENG G for parts list, trip to ACE hardware for parts, W Broadway for parts, ARS Tempe for parts and ware house for parts. - Gail Jackson; 2017-03-02 - 18010 - Gail Jackson-Install condensate pump / discharge line. Install H2O line from sink to machine. Replace drain line under sink. test run. - Gail Jackson; 2017-03-02 - 18010 - Thomas Gibble-Install condensate pump / discharge line. Install H2O line from sink to machine. Replace drain line under sink. test run. - Gail Jackson | Request for Estimate. Requesting an estimate for an ice machine to be installed. There is an existing water line that houses a water purifier, we are hoping to split into. The ice machine is a floor model and not a counter top. It is located just below the counter top water purifier however, Thank y. . . 2017-02-27 - 18010 - Gail Jackson-Trip ENG G for parts list, trip to ACE hardware for parts, W Broadway for parts, ARS Tempe for parts and ware house for parts. - Gail Jackson; 2017-03-02 - 18010 - Gail Jackson-Install condensate pump / discharge line. Install H2O line from sink to machine. Replace drain line under sink. test run. - Gail Jackson; 2017-03-02 - 18010 - Thomas Gibble-Install condensate pump / discharge line. Install H2O line from sink to machine. Replace drain line under sink. test run. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-08 | 32863 | TMPE-217294 | !! Particles fall from vents in offices PSD 21 and PSD 19. Could you please install filters in these two offices? Thanks for your help. Contact Name: Austin Echelmeier Contact Phone Number: 4807887595 Contact Email: aechelme@asu.edu 42BO0L7 | 2017-02-16 - 18170 - Jennifer Moyer-Building air handler filters are due for replacement. Brian has assigned work order# 179836 to filter crew to do on 2/17/17. BRIAN QUALLS - Brian Qualls | !! Particles fall from vents in offices PSD 21 and PSD 19. Could you please install filters in these two offices? Thanks for your help. Contact Name: Austin Echelmeier Contact Phone Number: 4807887595 Contact Email: aechelme@asu.edu 42BO0L7 2017-02-16 - 18170 - Jennifer Moyer-Building air handler filters are due for replacement. Brian has assigned work order# 179836 to filter crew to do on 2/17/17. BRIAN QUALLS - Brian Qualls | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 32873 | TMPE-217284 | MUSIC S1004 At the bottom of the stairs there's a transformer room that has condensate on the floor. | 2017-02-14 - 23040 - Gail Jackson-Vacuumed all plugged condensate lines, coil appears to be seeping. Cleaned condensate pan, very dirty. - Gail Jackson; 2017-02-14 - 23040 - Thomas Gibble-Vacuumed all plugged condensate lines, coil appears to be seeping. Cleaned condensate pan, very dirty. - Gail Jackson; 2017-02-14 - 23040 - Gail Jackson-Still leaking; adjusted level of fan coil and u trap. Flushed coil in server room; very dirty. Complete. - Gail Jackson; 2017-02-14 - 23040 - Thomas Gibble-Still leaking; adjusted level of fan coil and u trap. Flushed coil in server room; very dirty. Complete. - Gail Jackson | MUSIC S1004 At the bottom of the stairs there's a transformer room that has condensate on the floor. 2017-02-14 - 23040 - Gail Jackson-Vacuumed all plugged condensate lines, coil appears to be seeping. Cleaned condensate pan, very dirty. - Gail Jackson; 2017-02-14 - 23040 - Thomas Gibble-Vacuumed all plugged condensate lines, coil appears to be seeping. Cleaned condensate pan, very dirty. - Gail Jackson; 2017-02-14 - 23040 - Gail Jackson-Still leaking; adjusted level of fan coil and u trap. Flushed coil in server room; very dirty. Complete. - Gail Jackson; 2017-02-14 - 23040 - Thomas Gibble-Still leaking; adjusted level of fan coil and u trap. Flushed coil in server room; very dirty. Complete. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 32895 | TMPE-217262 | MU POD MARKET Please create a work order to service the ice maker inside the MU POD located in the MU on the first floor The light on the ice maker is yellow and needs serviced Charge ARAMARK GN7 | 2017-02-17 - 18210 - Gail Jackson-Found machine very dirty, explained to management and workers how to clean user friendly condenser filter. Disassemble and clean ice machine. Reinstall all parts, run cleaner, flush and test. Adjust settings. Empty all ice. - Gail Jackson; 2017-02-17 - 18210 - Thomas Gibble-Found machine very dirty, explained to management and workers how to clean user friendly condenser filter. Disassemble and clean ice machine. Reinstall all parts, run cleaner, flush and test. Adjust settings. Empty all ice. - Gail Jackson; 2017-02-21 - 18210 - Gail Jackson-Over Coke dispenser ice machine with H2O condenser; empty all ice from bin, clean all removable parts, run cleaner through machine and sanitize. Run test, water temp sensor needs replaced, got ok from store manager to replace, some type of issue with ordering parts, researched part and price, availability. - Gail Jackson; 2017-02-21 - 18210 - Thomas Gibble-Over Coke dispenser ice machine with H2O condenser; empty all ice from bin, clean all removable parts, run cleaner through machine and sanitize. Run test, water temp sensor needs replaced, got ok from store manager to replace, some type of issue with ordering parts, researched part and price, availability. - Gail Jackson; 2017-02-27 - 18210 - Gail Jackson-Trip to ARS Phoenix for parts and install, unit on left. Adjust bridge thickness unit on right, out on short freeze, this often happens because unit is clean. Complete. - Gail Jackson; 2017-02-27 - 18210 - Thomas Gibble-Trip to ARS Phoenix for parts and install, unit on left. Adjust bridge thickness unit on right, out on short freeze, this often happens because unit is clean. Complete. - Gail Jackson; 2017-02-27 - 18210 - Gail Jackson-Trip to ARS Phoenix for parts unit on left, install part. Adjust bridge thickness unit on right, out on short freeze, this often happens after unit is cleaned. run test Complete. - Gail Jackson; 2017-02-27 - 18210 - Thomas Gibble-Trip to ARS Phoenix for parts unit on left, install part. Adjust bridge thickness unit on right, out on short freeze, this often happens after unit is cleaned. run test Complete. - Gail Jackson | MU POD MARKET Please create a work order to service the ice maker inside the MU POD located in the MU on the first floor The light on the ice maker is yellow and needs serviced Charge ARAMARK GN7 2017-02-17 - 18210 - Gail Jackson-Found machine very dirty, explained to management and workers how to clean user friendly condenser filter. Disassemble and clean ice machine. Reinstall all parts, run cleaner, flush and test. Adjust settings. Empty all ice. - Gail Jackson; 2017-02-17 - 18210 - Thomas Gibble-Found machine very dirty, explained to management and workers how to clean user friendly condenser filter. Disassemble and clean ice machine. Reinstall all parts, run cleaner, flush and test. Adjust settings. Empty all ice. - Gail Jackson; 2017-02-21 - 18210 - Gail Jackson-Over Coke dispenser ice machine with H2O condenser; empty all ice from bin, clean all removable parts, run cleaner through machine and sanitize. Run test, water temp sensor needs replaced, got ok from store manager to replace, some type of issue with ordering parts, researched part and price, availability. - Gail Jackson; 2017-02-21 - 18210 - Thomas Gibble-Over Coke dispenser ice machine with H2O condenser; empty all ice from bin, clean all removable parts, run cleaner through machine and sanitize. Run test, water temp sensor needs replaced, got ok from store manager to replace, some type of issue with ordering parts, researched part and price, availability. - Gail Jackson; 2017-02-27 - 18210 - Gail Jackson-Trip to ARS Phoenix for parts and install, unit on left. Adjust bridge thickness unit on right, out on short freeze, this often happens because unit is clean. Complete. - Gail Jackson; 2017-02-27 - 18210 - Thomas Gibble-Trip to ARS Phoenix for parts and install, unit on left. Adjust bridge thickness unit on right, out on short freeze, this often happens because unit is clean. Complete. - Gail Jackson; 2017-02-27 - 18210 - Gail Jackson-Trip to ARS Phoenix for parts unit on left, install part. Adjust bridge thickness unit on right, out on short freeze, this often happens after unit is cleaned. run test Complete. - Gail Jackson; 2017-02-27 - 18210 - Thomas Gibble-Trip to ARS Phoenix for parts unit on left, install part. Adjust bridge thickness unit on right, out on short freeze, this often happens after unit is cleaned. run test Complete. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-08 | 32900 | TMPE-217257 | Drinking fountain chiller not working #REFERENCE 237457 | 2017-05-11 - 18010 - This water fountain is unchilled. - Jennifer Moyer; 2017-05-11 - 18010 - Water leak, transferred to plumbing and red tagged. - Jennifer Moyer | Drinking fountain chiller not working #REFERENCE 237457 2017-05-11 - 18010 - This water fountain is unchilled. - Jennifer Moyer; 2017-05-11 - 18010 - Water leak, transferred to plumbing and red tagged. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-08 | 32901 | TMPE-217256 | Drinking fountain chiller not working | 2017-02-16 - 18010 - Jennifer Moyer-Amp draw 4.2, water temperature 47.5, no GFCI observed ( reported ). Unit was unplugged. - Jennifer Moyer | Drinking fountain chiller not working 2017-02-16 - 18010 - Jennifer Moyer-Amp draw 4.2, water temperature 47.5, no GFCI observed ( reported ). Unit was unplugged. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-08 | 32909 | TMPE-217248 | There seem to be small white objects falling from the ceiling or vent above my desk in D-102. Often when I come into the office or get back from lunch I notice them on my desk and on the ground below my chair. If you could take a look at this it would be much appreciated - maybe the filter just need. . . | 2017-05-11 - 18170 - Jennifer Moyer-Investigated complaint and looked at rooms close by for similar problem. Checked air handler out, filters needed changed. Reported to management and filters were scheduled. - Jennifer Moyer | There seem to be small white objects falling from the ceiling or vent above my desk in D-102. Often when I come into the office or get back from lunch I notice them on my desk and on the ground below my chair. If you could take a look at this it would be much appreciated - maybe the filter just need. . . 2017-05-11 - 18170 - Jennifer Moyer-Investigated complaint and looked at rooms close by for similar problem. Checked air handler out, filters needed changed. Reported to management and filters were scheduled. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 32986 | TMPE-217171 | !! Please have the HVAC Shop repair/replace the exhaust fans in the Staff Locker Room (47) in WFA. This needs to be completed ASAP. Mildew is present in the showers. PO is YG202004950. Thank you. Contact Name: Michael Elliott Contact Phone Number: 602-680-8030 Contact Email: Mike.Elliott@asu.. . . | 2017-02-10 - 18160 - Robert Ecabert-Air handler was in the off position at the VFD. This is interlocked with the exhaust fan which serves locker room 47. It is now back in operation. I recommend that they clean the mildew on the walls,ceilings and floors and the grout. I also recommend that they paint the shower area with a mildew resistant paint. The exhaust from the shower area is working fine. Do not close out this work order yet because I ordered a new return grill for the shower room. - Robert Ecabert; 2017-03-03 - 18160 - Robert Ecabert-Replaced the exhaust air grill with a brand new one in the showers area. - Robert Ecabert | !! Please have the HVAC Shop repair/replace the exhaust fans in the Staff Locker Room (47) in WFA. This needs to be completed ASAP. Mildew is present in the showers. PO is YG202004950. Thank you. Contact Name: Michael Elliott Contact Phone Number: 602-680-8030 Contact Email: Mike.Elliott@asu.. . . 2017-02-10 - 18160 - Robert Ecabert-Air handler was in the off position at the VFD. This is interlocked with the exhaust fan which serves locker room 47. It is now back in operation. I recommend that they clean the mildew on the walls,ceilings and floors and the grout. I also recommend that they paint the shower area with a mildew resistant paint. The exhaust from the shower area is working fine. Do not close out this work order yet because I ordered a new return grill for the shower room. - Robert Ecabert; 2017-03-03 - 18160 - Robert Ecabert-Replaced the exhaust air grill with a brand new one in the showers area. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-02-08 | 33016 | TMPE-217141 | TRANSFER PL to HVAC HVAC to check on this issue, water is coming out of the duct work. We didn\\u2019t find the source of the water. Per email: 2/7/2017 6:08pm I approve Jim Emmons ORIG REQUEST ASUHC Agent: Spencer Leisy Description: Leak coming from the ceiling, behind Einsteins. Type of ceiling. . . | 2017-02-08 - 18010 - As per Jim Emmons's email 02/07/17 - 6:08 PM: Yes I approve Jim Emmons - Jeri Zappanti; 2017-02-17 - 18010 - Thomas Gibble-found no signs of water leaking - Thomas Gibble; 2017-02-17 - 18010 - Gail Jackson-found no signs of water leaking - Thomas Gibble | TRANSFER PL to HVAC HVAC to check on this issue, water is coming out of the duct work. We didn\\u2019t find the source of the water. Per email: 2/7/2017 6:08pm I approve Jim Emmons ORIG REQUEST ASUHC Agent: Spencer Leisy Description: Leak coming from the ceiling, behind Einsteins. Type of ceiling. . . 2017-02-08 - 18010 - As per Jim Emmons's email 02/07/17 - 6:08 PM: Yes I approve Jim Emmons - Jeri Zappanti; 2017-02-17 - 18010 - Thomas Gibble-found no signs of water leaking - Thomas Gibble; 2017-02-17 - 18010 - Gail Jackson-found no signs of water leaking - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-02-08 | 33480 | TMPE-216677 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 33481 | TMPE-216676 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 34019 | TMPE-216138 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-08 | 34022 | TMPE-216135 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-09 | 211836 | RACC-116774 | The thermostat is not turned on, not displaying anything and I cannot figure out how to turn it on. If there is a particular way to turn it on an email with instructions on how to would be all I need. The unit has not been on since winter break. 4NO5JGK | NA | The thermostat is not turned on, not displaying anything and I cannot figure out how to turn it on. If there is a particular way to turn it on an email with instructions on how to would be all I need. The unit has not been on since winter break. 4NO5JGK NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-09 | 211857 | RACC-116753 | AC broken again 4NOFGC3 | NA | AC broken again 4NOFGC3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-09 | 211868 | RACC-116742 | !! The air conditioner on the left side(when you walk in) is not working right. We have it set at 70 degrees and won't get below 75. There is a flashing battery icon, so I think the battery for the console is about to die. We are in building VAVL (Villas), room 3220, and the air conditioner is ne. . . | NA | !! The air conditioner on the left side(when you walk in) is not working right. We have it set at 70 degrees and won't get below 75. There is a flashing battery icon, so I think the battery for the console is about to die. We are in building VAVL (Villas), room 3220, and the air conditioner is ne. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-09 | 231260 | POLY-116938 | Replace furnace and condensing unit | NA | Replace furnace and condensing unit NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-09 | 231268 | POLY-116930 | !! Can we please get the air vents checked and our building/offices thoroughly inspected for mold? 42C3B05 | 2017-02-15 - 18010 - Steve Clark-CHECKED ON PROBLEM - Steve Clark; 2017-02-15 - 18010 - Steve Clark-CHECKED ON PROBLEM - Steve Clark; 2017-02-15 - 18010 - Allan Blair-REPLACED FILTERS, CLEANED AND TREATED INDOOR COIL, CLEARED AND FLUSHED OUT CONDENSATE DRAINS, ADDED CONDENSATED TABLETS TO EACH UNIT, HOESED OFF ROOF - Steve Clark; 2017-02-15 - 18010 - Darusman Amin-REPLACED FILTERS, CLEANED AND TREATED INDOOR COIL, CLEARED AND FLUSHED OUT CONDENSATE DRAINS, ADDED CONDENSATED TABLETS TO EACH UNIT, HOESED OFF ROOF - Steve Clark; 2017-02-17 - 18010 - Steve Clark-MET UP WITH EH&amp;S WHILE THEY PERFORMED A AIR ANYALIST- RESULTS WERE OK - EH&amp;S TO SEND REPORT TO THAT EFFECT - Steve Clark | !! Can we please get the air vents checked and our building/offices thoroughly inspected for mold? 42C3B05 2017-02-15 - 18010 - Steve Clark-CHECKED ON PROBLEM - Steve Clark; 2017-02-15 - 18010 - Steve Clark-CHECKED ON PROBLEM - Steve Clark; 2017-02-15 - 18010 - Allan Blair-REPLACED FILTERS, CLEANED AND TREATED INDOOR COIL, CLEARED AND FLUSHED OUT CONDENSATE DRAINS, ADDED CONDENSATED TABLETS TO EACH UNIT, HOESED OFF ROOF - Steve Clark; 2017-02-15 - 18010 - Darusman Amin-REPLACED FILTERS, CLEANED AND TREATED INDOOR COIL, CLEARED AND FLUSHED OUT CONDENSATE DRAINS, ADDED CONDENSATED TABLETS TO EACH UNIT, HOESED OFF ROOF - Steve Clark; 2017-02-17 - 18010 - Steve Clark-MET UP WITH EH&amp;S WHILE THEY PERFORMED A AIR ANYALIST- RESULTS WERE OK - EH&amp;S TO SEND REPORT TO THAT EFFECT - Steve Clark | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-09 | 31193 | TMPE-218964 | HHW Jennifer, I placed two 30# cylinders of R22 in will call at the Tempe ARS. Please pick them up and label the cylinders with PO# AC - Thank you Purchase qty. (2) 30lbs. cylinders R22 RFMT-139633 Please direct to Steven Palombo | 2017-03-07 - 18010 - Jennifer Moyer-Picked up refrigerant for shop. - Jennifer Moyer | HHW Jennifer, I placed two 30# cylinders of R22 in will call at the Tempe ARS. Please pick them up and label the cylinders with PO# AC - Thank you Purchase qty. (2) 30lbs. cylinders R22 RFMT-139633 Please direct to Steven Palombo 2017-03-07 - 18010 - Jennifer Moyer-Picked up refrigerant for shop. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-09 | 32664 | TMPE-217493 | PSA 15A: Order parts for Compressor Alarm PE Switch & Reversing Relays. Compressed air alarm. Send to EMS Mike Cozens 42B213C | 2017-02-17 - 30000 - Cheryl St. John-02.10.17 Created work order to order parts for PSA, created shop request, sent email to vendor for parts and posted labor. - Cheryl St. John; 2017-02-17 - 30000 - 02.17.17 Parts came in today, I gave them to appropriate tech. Closed work order. - Cheryl St. John | PSA 15A: Order parts for Compressor Alarm PE Switch & Reversing Relays. Compressed air alarm. Send to EMS Mike Cozens 42B213C 2017-02-17 - 30000 - Cheryl St. John-02.10.17 Created work order to order parts for PSA, created shop request, sent email to vendor for parts and posted labor. - Cheryl St. John; 2017-02-17 - 30000 - 02.17.17 Parts came in today, I gave them to appropriate tech. Closed work order. - Cheryl St. John | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-09 | 32693 | TMPE-217464 | It is reported, "LSE 541 Details: The green incubator on the left is leaking water. Also, a previous researcher said that it was overheating. Not sure if the overheating led to the leak, but I just noticed the leak today." Please initiate a work order for HVAC to inspect and service at their earlie. . . | 2017-03-16 - 18010 - Robert Ecabert-Found conviron box a little low on refrigerant, i leak checked the whole conviron but i could not locate a leak anywhere. I added 6ounces of refrigerant R-22 from refrigerant bottle JS160216-22 AC-1508533 and the unit has been running fine ever since i repaired it. - Robert Ecabert | It is reported, "LSE 541 Details: The green incubator on the left is leaking water. Also, a previous researcher said that it was overheating. Not sure if the overheating led to the leak, but I just noticed the leak today." Please initiate a work order for HVAC to inspect and service at their earlie. . . 2017-03-16 - 18010 - Robert Ecabert-Found conviron box a little low on refrigerant, i leak checked the whole conviron but i could not locate a leak anywhere. I added 6ounces of refrigerant R-22 from refrigerant bottle JS160216-22 AC-1508533 and the unit has been running fine ever since i repaired it. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-09 | 32712 | TMPE-217445 | There is a large air leak somewhere in the control air system. Its causing the control air compressor to cycle on and off every couple of minutes. | 2017-02-21 - 18010 - Michael Cozens-Searched for and repaired air leaks found. Compressor currently running just 33% of time. Will continue searching as time permits. - Mike Cozens | There is a large air leak somewhere in the control air system. Its causing the control air compressor to cycle on and off every couple of minutes. 2017-02-21 - 18010 - Michael Cozens-Searched for and repaired air leaks found. Compressor currently running just 33% of time. Will continue searching as time permits. - Mike Cozens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-09 | 32733 | TMPE-217424 | The coupling between the motor and the pump is broken. The unit has ceased to pull a vacuum. | NA | The coupling between the motor and the pump is broken. The unit has ceased to pull a vacuum. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-02-09 | 32773 | TMPE-217384 | MU DEVILS GREENS Please create a work order to have a tech service the ice machine that is located at Devils Greens This is located inside the MU Building on the first floor The ice maker is above the soda machine Charge to ARAMARK Gn7 | 2017-02-15 - 18210 - Thomas Gibble-cleaned ice machine sensors and cleaned air filters - Thomas Gibble; 2017-02-15 - 18210 - Gail Jackson-cleaned ice machine sensors and cleaned air filters - Thomas Gibble | MU DEVILS GREENS Please create a work order to have a tech service the ice machine that is located at Devils Greens This is located inside the MU Building on the first floor The ice maker is above the soda machine Charge to ARAMARK Gn7 2017-02-15 - 18210 - Thomas Gibble-cleaned ice machine sensors and cleaned air filters - Thomas Gibble; 2017-02-15 - 18210 - Gail Jackson-cleaned ice machine sensors and cleaned air filters - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-09 | 32785 | TMPE-217372 | Please open a work order for the HVAC Shop to assess the deli-cooler that is not working in LSE 348. (It has been shut down and emptied.) Charges up to $250.00 may be billed to PO LM502001099. Additional charges will warrant an estimate and alternate PO. Thank you. 42BLHKH | 2017-02-27 - 18100 - Zhi Yu-We diagnose the compressor LRA and smell burning. This unit is 17 years old and exceeded its life expand.. Will quote Her new unit. - Zhi Yu | Please open a work order for the HVAC Shop to assess the deli-cooler that is not working in LSE 348. (It has been shut down and emptied.) Charges up to $250.00 may be billed to PO LM502001099. Additional charges will warrant an estimate and alternate PO. Thank you. 42BLHKH 2017-02-27 - 18100 - Zhi Yu-We diagnose the compressor LRA and smell burning. This unit is 17 years old and exceeded its life expand.. Will quote Her new unit. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-10 | 2030 | WEST-109219 | The handicapped plates on the East and West side of the Student Services building\\u2014East side of the building -- either are broken again or are still not working. Tim will respond. | 2017-02-16 - 13070 - Tim Jowers-went over and found that the compressor was off line again checked the switch and reset it, unit ran all the way to over 110 lbs. psi.. used a screwdriver to bump the pressure switch. set off the pop off valve and dropped the presser to 75 lbs., unit ran up to 90 psi. and shut off. cycled the doors and unit ran up to pressure and shut off. - Tim Jowers | The handicapped plates on the East and West side of the Student Services building\\u2014East side of the building -- either are broken again or are still not working. Tim will respond. 2017-02-16 - 13070 - Tim Jowers-went over and found that the compressor was off line again checked the switch and reset it, unit ran all the way to over 110 lbs. psi.. used a screwdriver to bump the pressure switch. set off the pop off valve and dropped the presser to 75 lbs., unit ran up to 90 psi. and shut off. cycled the doors and unit ran up to pressure and shut off. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 5
2017-02-10 | 211763 | RACC-116847 | !! Bathroom Vent duct needs repair, the towel circular holder needs to be fixed and the toilet every time you press the flush the water comes out. Please fix that. 4NDF54G | NA | !! Bathroom Vent duct needs repair, the towel circular holder needs to be fixed and the toilet every time you press the flush the water comes out. Please fix that. 4NDF54G NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-02-10 | 231144 | POLY-117054 | BUILDING IS NO LONGER OCCUPIED - SHUT DOWN A/C SYSTEMS AND MAKE SURE EXHAUST FANS ARE OPERATIONAL 4O216EO | NA | BUILDING IS NO LONGER OCCUPIED - SHUT DOWN A/C SYSTEMS AND MAKE SURE EXHAUST FANS ARE OPERATIONAL 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-10 | 32487 | TMPE-217670 | The AC in the Rock House at Phx MUni is not cooling. Thermostat is set at 74, but the temperature is 80. The thermostat is located in James' office (room C102). PO is YG202004982. Thank you. This needs to be repaired by 2/16. Contact Name: James.Vujs Contact Phone Number: 623-570-3014 Contact . . . | 2017-03-21 - 18290 - Roque Garcia-Replaced motor, blade, and fuses checked and tested ok. - Roque Garcia | The AC in the Rock House at Phx MUni is not cooling. Thermostat is set at 74, but the temperature is 80. The thermostat is located in James' office (room C102). PO is YG202004982. Thank you. This needs to be repaired by 2/16. Contact Name: James.Vujs Contact Phone Number: 623-570-3014 Contact . . . 2017-03-21 - 18290 - Roque Garcia-Replaced motor, blade, and fuses checked and tested ok. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-10 | 32500 | TMPE-217657 | ERC B23 Located in the B/M pump room. The Hankinson refrigerated control air dryer has been disabled and bypassed and so is not removing moisture from the control air. Dryer needs to be repaired and put back in service ASAP. Send to HVAC Services. For further info contact Mike Cozens . . . | 2017-03-02 - 18040 - Brian Qualls-Dryer is not worth fixing,ordered new. Grainger part# 3YA46. Also, receptacle damaged. Will add Electric shop to replace. - Brian Qualls | ERC B23 Located in the B/M pump room. The Hankinson refrigerated control air dryer has been disabled and bypassed and so is not removing moisture from the control air. Dryer needs to be repaired and put back in service ASAP. Send to HVAC Services. For further info contact Mike Cozens . . . 2017-03-02 - 18040 - Brian Qualls-Dryer is not worth fixing,ordered new. Grainger part# 3YA46. Also, receptacle damaged. Will add Electric shop to replace. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-10 | 32567 | TMPE-217590 | ASUPD 207U1 The grill on the a/c unit is broken and rattling. | 2017-02-14 - 18010 - Carl Karr-Pick up 18x10 grille. Install at police station. - Carl Karr | ASUPD 207U1 The grill on the a/c unit is broken and rattling. 2017-02-14 - 18010 - Carl Karr-Pick up 18x10 grille. Install at police station. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-10 | 32577 | TMPE-217580 | ASUPD 107U1 On the west wall, the 1st split a/c unit is leaking pretty steady. Please have someone from HVAC check it out asap. | 2017-02-10 - 18010 - CALLED TO ONER. - Monica Moraga; 2017-02-14 - 18010 - Thomas Gibble-replaced cond pump - Thomas Gibble; 2017-02-14 - 18010 - Gail Jackson-replaced cond pump - Thomas Gibble | ASUPD 107U1 On the west wall, the 1st split a/c unit is leaking pretty steady. Please have someone from HVAC check it out asap. 2017-02-10 - 18010 - CALLED TO ONER. - Monica Moraga; 2017-02-14 - 18010 - Thomas Gibble-replaced cond pump - Thomas Gibble; 2017-02-14 - 18010 - Gail Jackson-replaced cond pump - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-10 | 32600 | TMPE-217557 | assessing pump 8532 in basement 22 | 2017-05-12 - 18010 - Jose Lopez-lock and tag unit.shut water off.there's a different work # for same task. - Jose Lopez | assessing pump 8532 in basement 22 2017-05-12 - 18010 - Jose Lopez-lock and tag unit.shut water off.there's a different work # for same task. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-02-11 | 168304 | RFMT-140027 | Air conditioning is not turning on. It is not blowing out cool air. 4NJOBCL | 2017-02-13 - 18010 - Salvatore Marasco Jr-Checked fan motor making sure that it was working normally, checked fan coil making sure there was no frost buildup. The Heat/Cool switch on the thermostat was not making good contact on the Cool side. By operating the switch from heat to cool and back again a few times seemed to allow for good contact allowing the blower motor to operate. If this occurs again, the A.C. techs. should change t-stat. - Salvatore Marasco Jr | Air conditioning is not turning on. It is not blowing out cool air. 4NJOBCL 2017-02-13 - 18010 - Salvatore Marasco Jr-Checked fan motor making sure that it was working normally, checked fan coil making sure there was no frost buildup. The Heat/Cool switch on the thermostat was not making good contact on the Cool side. By operating the switch from heat to cool and back again a few times seemed to allow for good contact allowing the blower motor to operate. If this occurs again, the A.C. techs. should change t-stat. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-02-11 | 231293 | POLY-116905 | Coils | 2017-02-17 - 18090 - Darusman Amin-checked belts, greased bearings, replaced filters in trane unit - Steve Clark; 2017-02-17 - 18090 - Allan Blair-checked belts, greased bearings, replaced filters in trane unit - Steve Clark | Coils 2017-02-17 - 18090 - Darusman Amin-checked belts, greased bearings, replaced filters in trane unit - Steve Clark; 2017-02-17 - 18090 - Allan Blair-checked belts, greased bearings, replaced filters in trane unit - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-12 | 168260 | RFMT-140071 | !! Change vents in room and in bathroom above shower Contact Name: Contact Phone Number: 6267103027 Contact Email: natalierosesirois@gmail.com 4NK919C | 2017-02-13 - 18130 - Salvatore Marasco Jr-Checked on vents in room C112. The occupant stated that she had not filed any work requests but maybe her suite mate in room 110 did, because the suite mate had told her that when they run the A.C. the room would smell. I checked next door, no one was in but I turned on the A.C. unit for a minute and sniffed around. I did not smell a bad odor. - Salvatore Marasco Jr | !! Change vents in room and in bathroom above shower Contact Name: Contact Phone Number: 6267103027 Contact Email: natalierosesirois@gmail.com 4NK919C 2017-02-13 - 18130 - Salvatore Marasco Jr-Checked on vents in room C112. The occupant stated that she had not filed any work requests but maybe her suite mate in room 110 did, because the suite mate had told her that when they run the A.C. the room would smell. I checked next door, no one was in but I turned on the A.C. unit for a minute and sniffed around. I did not smell a bad odor. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-12 | 168262 | RFMT-140069 | !! Air conditioning doesn't seem to be working. Seems to not be turning on in this room, but is working in the joined room. Contact Name: Contact Phone Number: 6618772721 Contact Email: 4NK7354 | 2017-02-14 - 18010 - Thor Millsaps-Inspected a/c unit. Operating properly in cooling mode. Supply air temp 55 degrees. Over 20 degree split. G108 shares a/c with adjoining room but there is no access between rooms. Thermostat is in adjoining room so G108 has no access to thermostat. Adjoining room is noticeably cooler than G108 which will make thermostat call for cooling less than required to keep G108 a similar temp. G108 likely has a higher heat load than adjoining room. I don't see a solution to this problem other than leaving fan set to "on" in order to circulate more air between rooms. - Thor Millsaps | !! Air conditioning doesn't seem to be working. Seems to not be turning on in this room, but is working in the joined room. Contact Name: Contact Phone Number: 6618772721 Contact Email: 4NK7354 2017-02-14 - 18010 - Thor Millsaps-Inspected a/c unit. Operating properly in cooling mode. Supply air temp 55 degrees. Over 20 degree split. G108 shares a/c with adjoining room but there is no access between rooms. Thermostat is in adjoining room so G108 has no access to thermostat. Adjoining room is noticeably cooler than G108 which will make thermostat call for cooling less than required to keep G108 a similar temp. G108 likely has a higher heat load than adjoining room. I don't see a solution to this problem other than leaving fan set to "on" in order to circulate more air between rooms. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-12 | 168273 | RFMT-140058 | Our heater is broken. Please fix. 4NOL41N | 2017-02-14 - 18010 - John Romero-the unit is working like it should. Adviser student how the system works. - John Romero | Our heater is broken. Please fix. 4NOL41N 2017-02-14 - 18010 - John Romero-the unit is working like it should. Adviser student how the system works. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-12 | 168281 | RFMT-140050 | HC- Sofia G Air conditioner is not cooling down and blowing heated air even though the thermostat is on low. Dispatched: Mike Guckian Time: 2:48 | 2017-02-13 - 18010 - Mike Guckian-replaced pop up valve. its cool now. - Mike Guckian | HC- Sofia G Air conditioner is not cooling down and blowing heated air even though the thermostat is on low. Dispatched: Mike Guckian Time: 2:48 2017-02-13 - 18010 - Mike Guckian-replaced pop up valve. its cool now. - Mike Guckian | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-02-13 | 168217 | RFMT-140114 | Air vent filter smells really bad. It's making our room smell like dust/ 4NC9C11 | 2017-02-14 - 18020 - Salvatore Marasco Jr-Checked air filter to make sure it was new, seeing that we had recently replaced all air filters in building, and they were new and clean. There was a puddle of water on the bathroom floor in front of shower, and the bathroom was humid. I explained to the occupant that the moisture gets pulled through the air vents and into all of the rooms in their unit. So if the bathroom (water closet) is not clean and it smells bad so will the rest of the unit when the a.c. blower is blowing. Try to keep it clean and dry, and it won't smell. - Salvatore Marasco Jr | Air vent filter smells really bad. It's making our room smell like dust/ 4NC9C11 2017-02-14 - 18020 - Salvatore Marasco Jr-Checked air filter to make sure it was new, seeing that we had recently replaced all air filters in building, and they were new and clean. There was a puddle of water on the bathroom floor in front of shower, and the bathroom was humid. I explained to the occupant that the moisture gets pulled through the air vents and into all of the rooms in their unit. So if the bathroom (water closet) is not clean and it smells bad so will the rest of the unit when the a.c. blower is blowing. Try to keep it clean and dry, and it won't smell. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-13 | 168229 | RFMT-140102 | Followed up on a/c unit condensate leak on to carpet and musty smell in Adelphi I J 110 & 112 room. | 2017-02-13 - 18010 - duplicate w.o. - Gregory Stetka | Followed up on a/c unit condensate leak on to carpet and musty smell in Adelphi I J 110 & 112 room. 2017-02-13 - 18010 - duplicate w.o. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-13 | 168230 | RFMT-140101 | Followed up on a/c unit condensate leak on to carpet and musty smell in Adelphi I J 110 & 112 room. | 2017-02-13 - 18010 - Salvatore Marasco Jr-Checked on rooms J112 and also J110, doing a follow up on a call from the night before, finding the carpets still wet in even larger areas around the A.C. air handlers. It appears that the a.c. unit may have froze up last night and the on-call GMM had shut the a.c. unit of to let it thaw. Requested Olympus to do water extraction again, as they did the night before, and also deodorize carpets and extract water from the inside of the air handler. I spoke with the Olympus workers personally and asked if they would clean the black "mildew" from the inside of air handler. They said they would. - Salvatore Marasco Jr; 2017-02-13 - 18010 - Res. Life HVAC shop - Simon was copied to repair condensate drain. - Gregory Stetka | Followed up on a/c unit condensate leak on to carpet and musty smell in Adelphi I J 110 & 112 room. 2017-02-13 - 18010 - Salvatore Marasco Jr-Checked on rooms J112 and also J110, doing a follow up on a call from the night before, finding the carpets still wet in even larger areas around the A.C. air handlers. It appears that the a.c. unit may have froze up last night and the on-call GMM had shut the a.c. unit of to let it thaw. Requested Olympus to do water extraction again, as they did the night before, and also deodorize carpets and extract water from the inside of the air handler. I spoke with the Olympus workers personally and asked if they would clean the black "mildew" from the inside of air handler. They said they would. - Salvatore Marasco Jr; 2017-02-13 - 18010 - Res. Life HVAC shop - Simon was copied to repair condensate drain. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-13 | 168245 | RFMT-140086 | RES LIFE / Scott: Water on floor of laundry room, please investigate. | 2017-02-13 - 23000 - Scott Berndt-condensation line leaking from the A/c...cleaned and vacuum out the line....replaced a/c filter in unit... - Scott Berndt | RES LIFE / Scott: Water on floor of laundry room, please investigate. 2017-02-13 - 23000 - Scott Berndt-condensation line leaking from the A/c...cleaned and vacuum out the line....replaced a/c filter in unit... - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-13 | 168257 | RFMT-140074 | !! AC is not working. It sounds like it is trying to, but nothing is coming out and then it smelled like burning. 4O237MK | 2017-02-14 - 18010 - Scott Berndt-wire was disconnected ...reconnected the wires - Scott Berndt | !! AC is not working. It sounds like it is trying to, but nothing is coming out and then it smelled like burning. 4O237MK 2017-02-14 - 18010 - Scott Berndt-wire was disconnected ...reconnected the wires - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-13 | 168294 | RFMT-140037 | Gabriel Figueroa-flushed out lines and no luck. switched t-stat between heat and cool and actuator not moving either way. need to have a/c techs come and replace actuator Hello, My name is Nicole Avila, and I supervise the tutoring center at Sonora in room H15 (between the elevators) is having . . . | 2017-02-13 - 18010 - Thor Millsaps-checked unit,rewired unit on the cooling side - Simon Fernandez | Gabriel Figueroa-flushed out lines and no luck. switched t-stat between heat and cool and actuator not moving either way. need to have a/c techs come and replace actuator Hello, My name is Nicole Avila, and I supervise the tutoring center at Sonora in room H15 (between the elevators) is having . . . 2017-02-13 - 18010 - Thor Millsaps-checked unit,rewired unit on the cooling side - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-13 | 2026 | WEST-109223 | Air Compressor - Monthly Maintenance | 2017-02-15 - xPM-0100-M - Robert Gailey-checked fluids, operated compressor - Robert Gailey | Air Compressor - Monthly Maintenance 2017-02-15 - xPM-0100-M - Robert Gailey-checked fluids, operated compressor - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-13 | 31881 | TMPE-218276 | PSF F12 !! This morning Feb. 13, I noticed that the air compressor tank pressure (room PSF12) was close to zero ,~15 psi. The motor was working. But the sound was unusual. So I turned the main power off. Could you please check/repair this compressor? We have a lot of samples for light stable i. . . | 2017-02-15 - 18030 - Brian Qualls-Found worn belts. Cross referenced 5L-680's to B-65's which the warehouse stocks.Replaced belts, topped off oil. Checked operation. - Brian Qualls | PSF F12 !! This morning Feb. 13, I noticed that the air compressor tank pressure (room PSF12) was close to zero ,~15 psi. The motor was working. But the sound was unusual. So I turned the main power off. Could you please check/repair this compressor? We have a lot of samples for light stable i. . . 2017-02-15 - 18030 - Brian Qualls-Found worn belts. Cross referenced 5L-680's to B-65's which the warehouse stocks.Replaced belts, topped off oil. Checked operation. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-13 | 31942 | TMPE-218215 | LSC L1-34 It is reported that the cadaver cooler in LSC L1-34 is not cooling. IMMEDIATE Service is needed please. Thank you, Judy | 2017-02-13 - 18100 - Called out to John - Amanda Thomas; 2017-03-02 - 18100 - Roque Garcia-Checked the unit and it was working. The faculty member in room 54 stated it had started to work so I monitored it to make sure. I found out there was a scheduled shutdown the morning in question. Unit was working ok. - Roque Garcia | LSC L1-34 It is reported that the cadaver cooler in LSC L1-34 is not cooling. IMMEDIATE Service is needed please. Thank you, Judy 2017-02-13 - 18100 - Called out to John - Amanda Thomas; 2017-03-02 - 18100 - Roque Garcia-Checked the unit and it was working. The faculty member in room 54 stated it had started to work so I monitored it to make sure. I found out there was a scheduled shutdown the morning in question. Unit was working ok. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-13 | 31972 | TMPE-218185 | LSC 482 The -20 freezer in LSC 482 is reported to be at 0 degrees. Immediate service is requested. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warrant an estimate and alternate PO. | 2017-02-13 - 18180 - CALLED TO STEVE P. - Monica Moraga; 2017-03-02 - 18180 - Roque Garcia-Found the freezer iced up and defrosted. Replaced the timer, defrost tstat, and cleaned drain. Checked and tested ok. - Roque Garcia | LSC 482 The -20 freezer in LSC 482 is reported to be at 0 degrees. Immediate service is requested. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warrant an estimate and alternate PO. 2017-02-13 - 18180 - CALLED TO STEVE P. - Monica Moraga; 2017-03-02 - 18180 - Roque Garcia-Found the freezer iced up and defrosted. Replaced the timer, defrost tstat, and cleaned drain. Checked and tested ok. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-13 | 31995 | TMPE-218162 | TOWERA 131A HVAC A/C not working. The fan and heat work, but unit won't blow cold. Contact Name: Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B | 2017-03-09 - 18290 - Mitchell Andrews-unit dint have any power to the condencing unit... found the breaker had been shut off - Mitchell Andrews | TOWERA 131A HVAC A/C not working. The fan and heat work, but unit won't blow cold. Contact Name: Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B 2017-03-09 - 18290 - Mitchell Andrews-unit dint have any power to the condencing unit... found the breaker had been shut off - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-14 | 168130 | RFMT-140201 | vent fell off wall outside of room G3512, it's leaning against wall. Attachment(s) 4NK3GNI | 2017-02-15 - 10010 - Scott Berndt-replaced the a/c vent back up.. - Scott Berndt | vent fell off wall outside of room G3512, it's leaning against wall. Attachment(s) 4NK3GNI 2017-02-15 - 10010 - Scott Berndt-replaced the a/c vent back up.. - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-14 | 168132 | RFMT-140199 | !! Please take a look at our air conditioning unit. It stopped working a few days ago. It just will not turn on. Thanks. Contact Name: Jacob Weiss Contact Phone Number: 7144945977 Contact Email: jrweiss4@asu.edu 4NNB99H | 2017-02-15 - 18010 - John Romero-Checked out unit,both valves are working and so is the motor.Cleaned out condensation pan and line. Unit is working at time. - John Romero | !! Please take a look at our air conditioning unit. It stopped working a few days ago. It just will not turn on. Thanks. Contact Name: Jacob Weiss Contact Phone Number: 7144945977 Contact Email: jrweiss4@asu.edu 4NNB99H 2017-02-15 - 18010 - John Romero-Checked out unit,both valves are working and so is the motor.Cleaned out condensation pan and line. Unit is working at time. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-02-14 | 31702 | TMPE-218455 | sewer pump #1 is running but does not pump water from pit - needs repair | 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-23 - 23100 - Jose Lopez-install new check valve/gate valve,adjust floats,unit working @ this time. - Jose Lopez | sewer pump #1 is running but does not pump water from pit - needs repair 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-23 - 23100 - Jose Lopez-install new check valve/gate valve,adjust floats,unit working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-02-14 | 31839 | TMPE-218318 | Noisy Motor | NA | Noisy Motor NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 168128 | RFMT-140203 | Repeat Request RFMT - 139984 We have just received a work order status of finished for the temperature being fixed in our room. It still seems a few noticeable degrees higher than other rooms on the same floor and same side of the hall. If it could drop a few more degrees that would be very helpful. . . | 2017-02-16 - 18010 - Simon Fernandez-checked a/c unit found system to be plugged,flushed coil,air supply at 60F - Simon Fernandez | Repeat Request RFMT - 139984 We have just received a work order status of finished for the temperature being fixed in our room. It still seems a few noticeable degrees higher than other rooms on the same floor and same side of the hall. If it could drop a few more degrees that would be very helpful. . . 2017-02-16 - 18010 - Simon Fernandez-checked a/c unit found system to be plugged,flushed coil,air supply at 60F - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 211657 | RACC-116953 | !! Repeat Request. I requested to have my A/C system fixed, and it was repaired for about three hours. I think the fan system itself is broken. The air in my room is quite stagnant now. 4NO5OLK | NA | !! Repeat Request. I requested to have my A/C system fixed, and it was repaired for about three hours. I think the fan system itself is broken. The air in my room is quite stagnant now. 4NO5OLK NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-02-15 | 211683 | RACC-116927 | !! Water issues - the air conditioner is leaking water in the main hallway in between the A room and B room. In addition, my room is leaking water from the rubbery hole thing in the ceiling above my shower. Thanks for your help! 4NH2C8M | NA | !! Water issues - the air conditioner is leaking water in the main hallway in between the A room and B room. In addition, my room is leaking water from the rubbery hole thing in the ceiling above my shower. Thanks for your help! 4NH2C8M NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-15 | 27333 | TMPE-222824 | Drinking Fountain-Annual | 2017-03-08 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | Drinking Fountain-Annual 2017-03-08 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 27334 | TMPE-222823 | Drinking Fountain-Annual | 2017-03-08 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | Drinking Fountain-Annual 2017-03-08 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 27335 | TMPE-222822 | Drinking Fountain-Annual | 2017-03-06 - xPM-1500-A - Paul Renfrey-Paul Renfrey-Checked operation, found Drip from underside of spout, pooling in ceramic &amp; running down drywall! Work Order required. Draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | Drinking Fountain-Annual 2017-03-06 - xPM-1500-A - Paul Renfrey-Paul Renfrey-Checked operation, found Drip from underside of spout, pooling in ceramic &amp; running down drywall! Work Order required. Draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-15 | 27336 | TMPE-222821 | Drinking Fountain-Annual | 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | Drinking Fountain-Annual 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 27337 | TMPE-222820 | Drinking Fountain-Annual | 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | Drinking Fountain-Annual 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 27338 | TMPE-222819 | Drinking Fountain-Annual | 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | Drinking Fountain-Annual 2017-03-06 - xPM-1500-A - Paul Renfrey-Checked operation, no leaks found, and draining freely. Fair condition. Not currently filtered, or chilled as remote chiller as been removed at some point. - Paul Renfrey [Modified: 2017-03-06 Paul Renfrey] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 251564 | DTPC-116974 | install new auto air bleed in ac water lines | 2017-02-15 - 18010 - Steve Skibbe-installed new one where leaker was 3rd floor roof - Steve Skibbe | install new auto air bleed in ac water lines 2017-02-15 - 18010 - Steve Skibbe-installed new one where leaker was 3rd floor roof - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 31511 | TMPE-218646 | EL transfer to AC: look at motor get with semeon and gary if have any questions VFD is in Default needs service | NA | EL transfer to AC: look at motor get with semeon and gary if have any questions VFD is in Default needs service NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 31519 | TMPE-218638 | Chilled water has been valved off for some unknown reason | 2017-02-21 - 18050 - Thomas Gibble-make-up air unit is out of order - Thomas Gibble; 2017-02-21 - 18050 - Gail Jackson-make-up air unit is out of order - Thomas Gibble | Chilled water has been valved off for some unknown reason 2017-02-21 - 18050 - Thomas Gibble-make-up air unit is out of order - Thomas Gibble; 2017-02-21 - 18050 - Gail Jackson-make-up air unit is out of order - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-02-15 | 31520 | TMPE-218637 | Sonora POD Market the reach in cooler where the grab & GO meal exchange Items are is temping at 54-42. Please have someone out there as soon as possible and please have them call me to let me know status. Jim Emmons approved via email 2/15/17 11:54am | 2017-02-23 - 18100 - Zhi Yu-Arrived Check temperature @38-36 deg. The condenser coil on both LF and RT unit. Both unit running in normal condition. We lower the setpoint by 2deg. will check back tomorrow. - Zhi Yu [Modified: 2017-03-13 Zhi Yu]; 2017-02-27 - 18100 - Zhi Yu-We back the unit staying at 45deg. We pull out the condenser unit and Check pressure appear very low. The TXV malfunction. will need to replace. - Zhi Yu; 2017-03-13 - 18100 - Zhi Yu-We Recover 70oz 404a. Stating replaced TXV and Filter drier. We pressure test for leak we nitrogen and vacuum the system to 500 micron. We also notice the Right unit short cycling. We pull out unit the Bad condenser fan motor and run cap. - Zhi Yu; 2017-03-13 - 18100 - Zhi Yu-pick up the 50watt motor and 35mfd From ARS. We replaced the motor and cap,both unit running Temp @38deg - Zhi Yu | Sonora POD Market the reach in cooler where the grab & GO meal exchange Items are is temping at 54-42. Please have someone out there as soon as possible and please have them call me to let me know status. Jim Emmons approved via email 2/15/17 11:54am 2017-02-23 - 18100 - Zhi Yu-Arrived Check temperature @38-36 deg. The condenser coil on both LF and RT unit. Both unit running in normal condition. We lower the setpoint by 2deg. will check back tomorrow. - Zhi Yu [Modified: 2017-03-13 Zhi Yu]; 2017-02-27 - 18100 - Zhi Yu-We back the unit staying at 45deg. We pull out the condenser unit and Check pressure appear very low. The TXV malfunction. will need to replace. - Zhi Yu; 2017-03-13 - 18100 - Zhi Yu-We Recover 70oz 404a. Stating replaced TXV and Filter drier. We pressure test for leak we nitrogen and vacuum the system to 500 micron. We also notice the Right unit short cycling. We pull out unit the Bad condenser fan motor and run cap. - Zhi Yu; 2017-03-13 - 18100 - Zhi Yu-pick up the 50watt motor and 35mfd From ARS. We replaced the motor and cap,both unit running Temp @38deg - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-02-15 | 31521 | TMPE-218636 | !! Occupants of Suite 312 in the Centerpoint building are complaining of physical symptoms such as sneezing when the A/C turns on in the afternoon, and they believe the air filters are to blame. Can we have the filters examined and changed if necessary. Thank you! 4MO5454 | 2017-02-17 - 18170 - Mitchell Andrews-checked all air filters in the area all were just changed and clean - Mitchell Andrews | !! Occupants of Suite 312 in the Centerpoint building are complaining of physical symptoms such as sneezing when the A/C turns on in the afternoon, and they believe the air filters are to blame. Can we have the filters examined and changed if necessary. Thank you! 4MO5454 2017-02-17 - 18170 - Mitchell Andrews-checked all air filters in the area all were just changed and clean - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 31530 | TMPE-218627 | Attached is the report from when EH&S conducted an indoor air quality (IAQ) investigation at Interdisciplinary A-wing. The IAQ investigation did not find an issue with the air quality; however, there was a odor present in A212. During the IAQ investigation, EHS was informed HRC would submit a work. . . | 2017-02-23 - 18050 - Zhi Yu-On February 20, 2017 going on the investigation on an fumes smell. We didn't smell any odor at the time. We notice there is 4 register facing east side of the building, that draw outside make-up air. In the morning Grounds mowing the lawn. The fumes get suck in build. Another issue there is an penetration hole 26"x28" maybe drawing damp air from subbasement EQ room. We ask Carl to make us an eblow to redirect basement air outside. - Zhi Yu [Modified: 2017-02-27 Zhi Yu]; 2017-02-27 - 18050 - Zhi Yu-Carl and Zhi install elbow in the first floor EQ room. Will follow -up. - Zhi Yu; 2017-02-27 - 18050 - Carl Karr-Carl and Zhi install elbow in the first floor EQ room. Will follow -up. - Zhi Yu; 2017-03-08 - 18050 - Zhi Yu-We have install the Elbow to direct damm air from sub-bass a week half ago. We follow up with Elisabeth Luquez and professor Garcia said, the air quality Significant improved.. - Zhi Yu | Attached is the report from when EH&S conducted an indoor air quality (IAQ) investigation at Interdisciplinary A-wing. The IAQ investigation did not find an issue with the air quality; however, there was a odor present in A212. During the IAQ investigation, EHS was informed HRC would submit a work. . . 2017-02-23 - 18050 - Zhi Yu-On February 20, 2017 going on the investigation on an fumes smell. We didn't smell any odor at the time. We notice there is 4 register facing east side of the building, that draw outside make-up air. In the morning Grounds mowing the lawn. The fumes get suck in build. Another issue there is an penetration hole 26"x28" maybe drawing damp air from subbasement EQ room. We ask Carl to make us an eblow to redirect basement air outside. - Zhi Yu [Modified: 2017-02-27 Zhi Yu]; 2017-02-27 - 18050 - Zhi Yu-Carl and Zhi install elbow in the first floor EQ room. Will follow -up. - Zhi Yu; 2017-02-27 - 18050 - Carl Karr-Carl and Zhi install elbow in the first floor EQ room. Will follow -up. - Zhi Yu; 2017-03-08 - 18050 - Zhi Yu-We have install the Elbow to direct damm air from sub-bass a week half ago. We follow up with Elisabeth Luquez and professor Garcia said, the air quality Significant improved.. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 31551 | TMPE-218606 | BT to HVAC- condensate leak coming from computer. **original request** !! For some reason it's raining in LSC L1-54A... Please inspect and service immediately. Thank you. 42BLHKH | 2017-02-19 - 23040 - Robert Dauscher-Had Oner turn call over to carpentry shop. Found NO AC Equipment in room. Found crack in cement with previous leak repair directly over location where water was dripping from light fixture - Robert Dauscher | BT to HVAC- condensate leak coming from computer. **original request** !! For some reason it's raining in LSC L1-54A... Please inspect and service immediately. Thank you. 42BLHKH 2017-02-19 - 23040 - Robert Dauscher-Had Oner turn call over to carpentry shop. Found NO AC Equipment in room. Found crack in cement with previous leak repair directly over location where water was dripping from light fixture - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-15 | 31570 | TMPE-218587 | BT transfer to AC: , need to find out why air duct is leaking, dripping, it is not leaking now water leak above drop ceiling, one tile got wet and fell down. Water leak needs to be addressed before ceiling is fixed. 4NF8HJA | NA | BT transfer to AC: , need to find out why air duct is leaking, dripping, it is not leaking now water leak above drop ceiling, one tile got wet and fell down. Water leak needs to be addressed before ceiling is fixed. 4NF8HJA NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-02-15 | 32077 | TMPE-218080 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-15 | 32331 | TMPE-217826 | Vacuum Pump-Biannual | 2017-02-24 - xPM-3200.01-B - Matthew Smith-Found the motor windings going to ground. Submitted a WO for the replacement of the motor. the oil and filters are good. - Matthew Smith | Vacuum Pump-Biannual 2017-02-24 - xPM-3200.01-B - Matthew Smith-Found the motor windings going to ground. Submitted a WO for the replacement of the motor. the oil and filters are good. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-15 | 32351 | TMPE-217806 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 32392 | TMPE-217765 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 32393 | TMPE-217764 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 32394 | TMPE-217763 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-15 | 32396 | TMPE-217761 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-16 | 150412 | RNLD-100889 | !! The air filter in room 281 needs to be cleaned out. The vent itself has black particles that are growing on the blades, if you can clean those off that would be great. We have people moving into that room this weekend. 4NI91HM | 2017-02-21 - 18170 - Allan Blair-2/17 - Darusman and Allan cleaned the filters and vanes. - Gayle Swenson | !! The air filter in room 281 needs to be cleaned out. The vent itself has black particles that are growing on the blades, if you can clean those off that would be great. We have people moving into that room this weekend. 4NI91HM 2017-02-21 - 18170 - Allan Blair-2/17 - Darusman and Allan cleaned the filters and vanes. - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-16 | 167998 | RFMT-140333 | problems with the air conditioning 4NM3CLJ | 2017-02-17 - 18010 - Thor Millsaps-Replaced Belimo actuator on chilled water valve. System up and running. - Simon Fernandez | problems with the air conditioning 4NM3CLJ 2017-02-17 - 18010 - Thor Millsaps-Replaced Belimo actuator on chilled water valve. System up and running. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-02-16 | 168007 | RFMT-140324 | My ac doesn't work. 4NK0094 | 2017-02-17 - 18010 - Simon Fernandez-ball valves bad. shut off heating side,cooling side opened, unit okay - Simon Fernandez | My ac doesn't work. 4NK0094 2017-02-17 - 18010 - Simon Fernandez-ball valves bad. shut off heating side,cooling side opened, unit okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-02-16 | 168059 | RFMT-140272 | !! The air conditioning does not work. We can't turn the air on at all anymore, it is just broken. It is very hot in the rooms! 4ND42DH | 2017-02-17 - 18010 - Thor Millsaps-Replaced 1/4 HP 825 RPM condenser fan motor and capacitor. Fan motor partnot in TMA system. System up and running. - Simon Fernandez | !! The air conditioning does not work. We can't turn the air on at all anymore, it is just broken. It is very hot in the rooms! 4ND42DH 2017-02-17 - 18010 - Thor Millsaps-Replaced 1/4 HP 825 RPM condenser fan motor and capacitor. Fan motor partnot in TMA system. System up and running. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2017-02-16 | 231083 | POLY-117115 | The AC is not working in this room, we pushed the button to turn it on but nothing happened. 4NGNANM | 2017-02-17 - 18010 - Steve Clark-ROOM IS SET FOR 75C/69H. ROOM GOT UP TO 75.5DEG FOR MABOUT 1/2 HR B4 COOLING DOWN. SET COOLING FOR 74/69 - Steve Clark | The AC is not working in this room, we pushed the button to turn it on but nothing happened. 4NGNANM 2017-02-17 - 18010 - Steve Clark-ROOM IS SET FOR 75C/69H. ROOM GOT UP TO 75.5DEG FOR MABOUT 1/2 HR B4 COOLING DOWN. SET COOLING FOR 74/69 - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 231102 | POLY-117096 | BILLED 1. Boys urinal in bathroom located in Phase 2 keeps running-recurring issue 2. Wire box in same bathroom coming off wall 42AENHG BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) | NA | BILLED 1. Boys urinal in bathroom located in Phase 2 keeps running-recurring issue 2. Wire box in same bathroom coming off wall 42AENHG BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 30336 | TMPE-219821 | Replace water filter in Frigidaire refrigerator, model # FFHS2611LW. New water filter is on site (See Lori Stevens). We tried to replace it but the existing filter is difficult to remove. See attached page for directions. Attachment(s) 4N902JM PO# Bf502000788 EST-155367 | 2017-03-07 - 18240 - Thomas Gibble-replaced the water filter again. the filter they got from anamzon was no good. I went to parts store to pick one up and put it in. - Thomas Gibble | Replace water filter in Frigidaire refrigerator, model # FFHS2611LW. New water filter is on site (See Lori Stevens). We tried to replace it but the existing filter is difficult to remove. See attached page for directions. Attachment(s) 4N902JM PO# Bf502000788 EST-155367 2017-03-07 - 18240 - Thomas Gibble-replaced the water filter again. the filter they got from anamzon was no good. I went to parts store to pick one up and put it in. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 31217 | TMPE-218940 | Please repair the ice maker 056E-FICE-01006 that was found during the preventive maintenance. Please send this to Judy Swartz Judy.D.Swartz@asu.edu Please use PO #LM502001099 for this request. Sincerely Judy | 2017-05-11 - 18210 - Gail Jackson-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson; 2017-05-11 - 18210 - Gail Jackson-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson; 2017-05-11 - 18210 - Thomas Gibble-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson | Please repair the ice maker 056E-FICE-01006 that was found during the preventive maintenance. Please send this to Judy Swartz Judy.D.Swartz@asu.edu Please use PO #LM502001099 for this request. Sincerely Judy 2017-05-11 - 18210 - Gail Jackson-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson; 2017-05-11 - 18210 - Gail Jackson-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson; 2017-05-11 - 18210 - Thomas Gibble-Transport to shop; bearings, evap barrel, auger motor and auger wore out. Cost for parts and labor exceeds value of unit,Judy Swartz says to be scraped. - Gail Jackson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-16 | 31292 | TMPE-218865 | Sump pumps not working properly need repair possible float or control issue | 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-07 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-11 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in porogress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez | Sump pumps not working properly need repair possible float or control issue 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-10 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-07 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-11 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in porogress - Jose Lopez; 2017-05-12 - 23100 - Jose Lopez-work in progress - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 31301 | TMPE-218856 | !! Requesting immediate assistance. I need to have the ceiling vents closed right away for SSV bldg. room 276-C and 276-D. The air flow is so strong we have papers blowing off desks and it is extremely disruptive to our Executive Director and also our Director while they are working and hosting mee. . . | 2017-02-19 - 18010 - Robert Dauscher-Found airflow so great that papers were blowing off desk without being weighted down. Contacted EMS Tech and worked with them to adjust airflow into these two rooms back to an acceptable level - Robert Dauscher | !! Requesting immediate assistance. I need to have the ceiling vents closed right away for SSV bldg. room 276-C and 276-D. The air flow is so strong we have papers blowing off desks and it is extremely disruptive to our Executive Director and also our Director while they are working and hosting mee. . . 2017-02-19 - 18010 - Robert Dauscher-Found airflow so great that papers were blowing off desk without being weighted down. Contacted EMS Tech and worked with them to adjust airflow into these two rooms back to an acceptable level - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 31380 | TMPE-218777 | Central Plant--Please work with Purtec on replacing membrane filters in ro unit 4. See Mike Torres for information. 4NNI9H6 | NA | Central Plant--Please work with Purtec on replacing membrane filters in ro unit 4. See Mike Torres for information. 4NNI9H6 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-16 | 31416 | TMPE-218741 | One of the RO pumps that feed the roof tank is blinking yellow. We are not sure if this is an issue, but we thought we would bring this to your attention if the pump needs reset or repaired. PSH- H47U1- one of the two Grundfos Pumps installed by ASU. 4NB5JGJ | 2017-02-21 - 23100 - Thomas Gibble-#2 pump was off. re-started pump - Thomas Gibble; 2017-02-21 - 23100 - Gail Jackson-#2 pump was off. re-started pump - Thomas Gibble | One of the RO pumps that feed the roof tank is blinking yellow. We are not sure if this is an issue, but we thought we would bring this to your attention if the pump needs reset or repaired. PSH- H47U1- one of the two Grundfos Pumps installed by ASU. 4NB5JGJ 2017-02-21 - 23100 - Thomas Gibble-#2 pump was off. re-started pump - Thomas Gibble; 2017-02-21 - 23100 - Gail Jackson-#2 pump was off. re-started pump - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-17 | 167970 | RFMT-140361 | Bathroom fan not working. You hear electrical noise when turned on, but the fan doesn't actually turn on. Contact Name: Damian Echavarria Contact Phone Number: 9094713795 Contact Email: dbechava@asu.edu 4NOEA84 | 2017-02-20 - 18010 - Joe Swan-replaced fan motor - Joe Swan | Bathroom fan not working. You hear electrical noise when turned on, but the fan doesn't actually turn on. Contact Name: Damian Echavarria Contact Phone Number: 9094713795 Contact Email: dbechava@asu.edu 4NOEA84 2017-02-20 - 18010 - Joe Swan-replaced fan motor - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-17 | 1896 | WEST-109353 | The garbage disposer by the Sushi station is not working. | 2017-02-21 - 23090 - Tim Jowers-found that the disposal was not working, making a humming sound when turned on. asked Joe to come over and test the fuses. all were good.opened up the switch and found that the contacts were burnt and dirty. cleaned the contacts and adjusted the contact pressure.ran the unit and cleaned it out. - Tim Jowers; 2017-02-21 - 23090 - Joseph Danielek-worked on the disposal, found the fuses were good and the problem was with the switch. - Tim Jowers | The garbage disposer by the Sushi station is not working. 2017-02-21 - 23090 - Tim Jowers-found that the disposal was not working, making a humming sound when turned on. asked Joe to come over and test the fuses. all were good.opened up the switch and found that the contacts were burnt and dirty. cleaned the contacts and adjusted the contact pressure.ran the unit and cleaned it out. - Tim Jowers; 2017-02-21 - 23090 - Joseph Danielek-worked on the disposal, found the fuses were good and the problem was with the switch. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-17 | 1909 | WEST-109340 | Noisy operation of the inducer fan. | 2017-02-17 - 18010 - Chad T Ball-Motor was noisy when running. Found bushings on fan motor loose. Went to ARS to get replacement motor. Replaced defective motor and re-installed inducer fan assembly. - Chad T Ball | Noisy operation of the inducer fan. 2017-02-17 - 18010 - Chad T Ball-Motor was noisy when running. Found bushings on fan motor loose. Went to ARS to get replacement motor. Replaced defective motor and re-installed inducer fan assembly. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-17 | 231066 | POLY-117132 | REPAIR OF CHILLER 4O216EO | 2017-05-02 - 18080 - Suresh Nair-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Allan Blair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Allan Blair-installed new switch and brought chiller up to working order - Steve Clark | REPAIR OF CHILLER 4O216EO 2017-05-02 - 18080 - Suresh Nair-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-evaluate chiller for repairs - found bad low pressure switch - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Esli Arvizo-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Suresh Nair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Allan Blair-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Darusman Amin-installed new switch and brought chiller up to working order - Steve Clark; 2017-05-02 - 18080 - Allan Blair-installed new switch and brought chiller up to working order - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-17 | 251515 | DTPC-117023 | AHU 3A & AHU3B Bearings going out on both Return Fan Motors. | 2017-03-08 - 18230 - Ross Hossack-Steve and I retrieved the platform lift from the Mercado and then proceeded to remove the old motor to install the new one and the seals on the platform lift blew out so we are now ordering a new platform lift.When it comes in we will resume replacing the motors. - Ross Hossack; 2017-03-08 - 18230 - Steve Skibbe-Steve and I retrieved the platform lift from the Mercado and then proceeded to remove the old motor to install the new one and the seals on the platform lift blew out so we are now ordering a new platform lift.When it comes in we will resume replacing the motors. - Ross Hossack; 2017-03-10 - 18230 - Ross Hossack-Replaced return fan motor in AHU3B. - Ross Hossack; 2017-03-14 - 18230 - Ross Hossack-Removed motor with bad bearings and installed new motor. - Ross Hossack; 2017-03-14 - 18230 - Keith Griffin-Removed motor with bad bearings and installed new motor. - Ross Hossack | AHU 3A & AHU3B Bearings going out on both Return Fan Motors. 2017-03-08 - 18230 - Ross Hossack-Steve and I retrieved the platform lift from the Mercado and then proceeded to remove the old motor to install the new one and the seals on the platform lift blew out so we are now ordering a new platform lift.When it comes in we will resume replacing the motors. - Ross Hossack; 2017-03-08 - 18230 - Steve Skibbe-Steve and I retrieved the platform lift from the Mercado and then proceeded to remove the old motor to install the new one and the seals on the platform lift blew out so we are now ordering a new platform lift.When it comes in we will resume replacing the motors. - Ross Hossack; 2017-03-10 - 18230 - Ross Hossack-Replaced return fan motor in AHU3B. - Ross Hossack; 2017-03-14 - 18230 - Ross Hossack-Removed motor with bad bearings and installed new motor. - Ross Hossack; 2017-03-14 - 18230 - Keith Griffin-Removed motor with bad bearings and installed new motor. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-17 | 30546 | TMPE-219611 | Naumann Hobbs Located unit and tested. Found batteries bad, passenger seat torn. Ordered parts & returned to cart. Removed rear trunk and rear fender. Replaced all 6 batteries. Removed passenger seat, ordered new & replaced. Reassembled unit, tested operations & charging system. total: 2399.29 | NA | Naumann Hobbs Located unit and tested. Found batteries bad, passenger seat torn. Ordered parts & returned to cart. Removed rear trunk and rear fender. Replaced all 6 batteries. Removed passenger seat, ordered new & replaced. Reassembled unit, tested operations & charging system. total: 2399.29 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-17 | 30741 | TMPE-219416 | !! HVAC - Fan making a racket In Gammage, below the stage, in Room B11 (door says dimmer room) there's a really important fan unit. (keeps the dimmers cool.) The switch to the fan is behind the door (to the right as you enter.) Sounds like the fan blade is hitting something. You have to manually t. . . | 2017-02-23 - 18010 - Mitchell Andrews-replaced the blower wheels on the duel shaft - Mitchell Andrews | !! HVAC - Fan making a racket In Gammage, below the stage, in Room B11 (door says dimmer room) there's a really important fan unit. (keeps the dimmers cool.) The switch to the fan is behind the door (to the right as you enter.) Sounds like the fan blade is hitting something. You have to manually t. . . 2017-02-23 - 18010 - Mitchell Andrews-replaced the blower wheels on the duel shaft - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-17 | 31166 | TMPE-218991 | ATTENTION: HVAC - There is a constant buzzing noise in BA 189C. Can you please send someone to look at it? 42B20BB | 2017-02-24 - 18010 - Zhi Yu-Arrived At BA room 189c. no buzzing noise present. Above the ceiling there's no mechanical moving part, 2 florescent light. We notify the customer the ballast can be bad. We ask the customer if she hear the buzzing noise try to turn off the light switch see if the noise goes away. We ask Nick from EMS to assist on ramping zone see we can duplicate the buzzing noise. Will follow up in a week. - Zhi Yu [Modified: 2017-02-27 Zhi Yu]; 2017-03-27 - 18010 - Zhi Yu-follow-up call no noise at arrival. left my contact number. - Zhi Yu | ATTENTION: HVAC - There is a constant buzzing noise in BA 189C. Can you please send someone to look at it? 42B20BB 2017-02-24 - 18010 - Zhi Yu-Arrived At BA room 189c. no buzzing noise present. Above the ceiling there's no mechanical moving part, 2 florescent light. We notify the customer the ballast can be bad. We ask the customer if she hear the buzzing noise try to turn off the light switch see if the noise goes away. We ask Nick from EMS to assist on ramping zone see we can duplicate the buzzing noise. Will follow up in a week. - Zhi Yu [Modified: 2017-02-27 Zhi Yu]; 2017-03-27 - 18010 - Zhi Yu-follow-up call no noise at arrival. left my contact number. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-17 | 31180 | TMPE-218977 | BT to HVAC-the flex ducts have big holes causing air to blow very loudly into H244 and H246!!! The ceiling is marked with orange tape indicating where the holes are. Please make this priority. Very loud. !!Vent in classroom is making a loud noise, very disruptive for professor as she teaches. | 2017-02-17 - 18010 - Called out to Oner - Amanda Thomas; 2017-02-20 - 18010 - Carl Karr-Located leak. Moved ceiling tiles to lessen noise. - Carl Karr; 2017-03-10 - 18010 - Carl Karr-Contractor assist. - Carl Karr; 2017-04-27 - 18010 - Carl Karr-Job complete. - Carl Karr | BT to HVAC-the flex ducts have big holes causing air to blow very loudly into H244 and H246!!! The ceiling is marked with orange tape indicating where the holes are. Please make this priority. Very loud. !!Vent in classroom is making a loud noise, very disruptive for professor as she teaches. 2017-02-17 - 18010 - Called out to Oner - Amanda Thomas; 2017-02-20 - 18010 - Carl Karr-Located leak. Moved ceiling tiles to lessen noise. - Carl Karr; 2017-03-10 - 18010 - Carl Karr-Contractor assist. - Carl Karr; 2017-04-27 - 18010 - Carl Karr-Job complete. - Carl Karr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-02-17 | 31211 | TMPE-218946 | Can we please have an electrician sent to Devils greens to replace the cord on their line cooler. It has been damaged by the wheels and is creating a safety issue. Approved by Sara Royce GN7 account via email 2/16/17 9:05pm. | 2017-04-28 - 15000 - Edward Howell-Replaced with cord cap to a safe connection. - Edward Howell | Can we please have an electrician sent to Devils greens to replace the cord on their line cooler. It has been damaged by the wheels and is creating a safety issue. Approved by Sara Royce GN7 account via email 2/16/17 9:05pm. 2017-04-28 - 15000 - Edward Howell-Replaced with cord cap to a safe connection. - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-19 | 167909 | RFMT-140422 | !! Repeat Request. ac not working 4O0LMJ9 | 2017-02-20 - 18010 - Thomas Zambrano-chiller and boiler valves off? called Thor. Dont know the prognosis. - Thomas Zambrano | !! Repeat Request. ac not working 4O0LMJ9 2017-02-20 - 18010 - Thomas Zambrano-chiller and boiler valves off? called Thor. Dont know the prognosis. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-02-20 | 167830 | RFMT-140501 | Extremely bad smell comes from vents still when heater comes on 4NJNOI0 | 2017-02-21 - 18020 - Simon Fernandez-checked a/c unit student stated filter was changed and no more issues with smell - Simon Fernandez | Extremely bad smell comes from vents still when heater comes on 4NJNOI0 2017-02-21 - 18020 - Simon Fernandez-checked a/c unit student stated filter was changed and no more issues with smell - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30566 | TMPE-219591 | MU POD Please create a work order to PM the 2 air screens in the MU POD The compressors are dirty The MU POD is located in the MU building on the first floor | 2017-02-23 - 18100 - Michael Kelley-Contacted Jim Emmons 480-965-2052. Check out cooler units. Dirty coils. Talk to Market Supervisor for a better time to PM the cooler. Will return on Friday in AM. Need to clean coil, drip pan... - Michael Kelley; 2017-02-24 - 18100 - Michael Kelley-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley; 2017-02-24 - 18100 - Michael Kelley-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley; 2017-02-24 - 18100 - Midhat Mukanovic-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley | MU POD Please create a work order to PM the 2 air screens in the MU POD The compressors are dirty The MU POD is located in the MU building on the first floor 2017-02-23 - 18100 - Michael Kelley-Contacted Jim Emmons 480-965-2052. Check out cooler units. Dirty coils. Talk to Market Supervisor for a better time to PM the cooler. Will return on Friday in AM. Need to clean coil, drip pan... - Michael Kelley; 2017-02-24 - 18100 - Michael Kelley-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley; 2017-02-24 - 18100 - Michael Kelley-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley; 2017-02-24 - 18100 - Midhat Mukanovic-cleaned coils, drain line, tighten contacts, vacuumed condensation from drain line. found bad evap fan motor. $98.96 called Structural Concepts 1800-433-9489 model- C07178R serial- 860814GK161589 part # 62995 called and left message for Jim Emmons 480-9652052 Left message about problem. We need a separate WO for the repair. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-02-20 | 30588 | TMPE-219569 | INTDSA A207B Transfer HVAC to EL. Jennifer is needing assistance in locating a breaker for an exhaust fan on the roof of music. ORIG REQUEST !! This is urgent! Please also reference Work Order TMPE-191633 from September, 2016. The Mitsubishi Electric Mr. Slim air conditioning unit in A207B is. . . | 2017-02-23 - 15000 - Edward Howell-Spoke with Jennifer and she mentioned that she did not need assist anymore. - Edward Howell | INTDSA A207B Transfer HVAC to EL. Jennifer is needing assistance in locating a breaker for an exhaust fan on the roof of music. ORIG REQUEST !! This is urgent! Please also reference Work Order TMPE-191633 from September, 2016. The Mitsubishi Electric Mr. Slim air conditioning unit in A207B is. . . 2017-02-23 - 15000 - Edward Howell-Spoke with Jennifer and she mentioned that she did not need assist anymore. - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-20 | 30608 | TMPE-219549 | !!Rooms are too hot- please adjust: 151 & 142 | 2017-02-27 - 18290 - Jennifer Moyer-Central plant listed as "first call" on room 142. Placed call for cooler temp. from central plant. It appears the customer may want temperature lowered for equipment in the room. Will continue to monitor. - Jennifer Moyer; 2017-04-26 - 18290 - A customer or another customer created an additional work order that was assigned to one of my co-workers who provided a portable a/c unit. Since the problem was solved, I will "finish" this work order. - Jennifer Moyer | !!Rooms are too hot- please adjust: 151 & 142 2017-02-27 - 18290 - Jennifer Moyer-Central plant listed as "first call" on room 142. Placed call for cooler temp. from central plant. It appears the customer may want temperature lowered for equipment in the room. Will continue to monitor. - Jennifer Moyer; 2017-04-26 - 18290 - A customer or another customer created an additional work order that was assigned to one of my co-workers who provided a portable a/c unit. Since the problem was solved, I will "finish" this work order. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30629 | TMPE-219528 | USB assign to AC shop condensing unit #9 is frozen, photo attached | 2017-03-07 - 23040 - Gail Jackson-Check HP90 UTO employees had turned unit back on. Went to roof, rocked out again, shut unit off at disconnect. Called Central Plant left message for Cheryl for new Tstat. Trouble shoot unit; needs new board and temp sensors will not go into defrost. - Gail Jackson; 2017-03-09 - 23040 - Gail Jackson-Trip to Trane Parts for new Defrost board and sensors. - Gail Jackson; 2017-03-09 - 23040 - Gail Jackson-Install DF board and 2 temperature sensors. RUN TEST COMPLETE. Thermostat needs replaced; it registrars all over the place. This was HP 90 not 9 as on work order. Found old #109 in heat, called Central Plant and had Mike attempt to adjust temp, he could not, switched stat over to manual and runs fine. EMS needs to check address as #107 on stat has been marked out. - Gail Jackson | USB assign to AC shop condensing unit #9 is frozen, photo attached 2017-03-07 - 23040 - Gail Jackson-Check HP90 UTO employees had turned unit back on. Went to roof, rocked out again, shut unit off at disconnect. Called Central Plant left message for Cheryl for new Tstat. Trouble shoot unit; needs new board and temp sensors will not go into defrost. - Gail Jackson; 2017-03-09 - 23040 - Gail Jackson-Trip to Trane Parts for new Defrost board and sensors. - Gail Jackson; 2017-03-09 - 23040 - Gail Jackson-Install DF board and 2 temperature sensors. RUN TEST COMPLETE. Thermostat needs replaced; it registrars all over the place. This was HP 90 not 9 as on work order. Found old #109 in heat, called Central Plant and had Mike attempt to adjust temp, he could not, switched stat over to manual and runs fine. EMS needs to check address as #107 on stat has been marked out. - Gail Jackson | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30641 | TMPE-219516 | INTDSA A207B !! This is urgent! Please also reference Work Order TMPE-191633 from September, 2016. The Mitsubishi Electric Mr. Slim air conditioning unit in A207B is not functioning. The control screen on the unit is flashing the word "Check" and some other numbers, but will not turn on. It i. . . | 2017-02-20 - 18010 - Called out to John - Amanda Thomas; 2017-02-20 - 18010 - Jennifer Moyer-Called to work with Co-worker on unit. Supervision added me to the work order. Troubleshooting and repair not completed before 3pm, so portable a/c was installed and set at 76 degrees to keep room cool for the night as instructed.1st portable unit delivered, did not work, so I had to get another portable for the room. Unit 1007 installed. Called to another work order, same building. - Jennifer Moyer; 2017-02-22 - 18010 - Zhi Yu-After the steam trap class. Jennifer and I Continue the diagnose on the Code P6. Call the Tech support and waited for 1 1/2 hr. Jen removed the Evap cover to ohm out sensor and find the flare nut cracked cause Freon leak. We carry all needed EQ up to the roof. We Recover 2lbs of R410a. We Cutout flare nut and look for replacement. - Zhi Yu; 2017-02-22 - 18010 - Jennifer Moyer-After the steam trap class. Jennifer and I Continue the diagnose on the Code P6. Call the Tech support and waited for 1 1/2 hr. Jen removed the Evap cover to ohm out sensor and find the flare nut cracked cause Freon leak. We carry all needed EQ up to the roof. We Recover 2lbs of R410a. We Cutout flare nut and look for replacement. - Zhi Yu; 2017-02-22 - 18010 - Zhi Yu-Install New Flare nut. and pressure test for leaks. We vacuum unit to 490 micron and charge R409a. We test run the unit while retreating all the EQ up to roof. The unit running like Champion. The problem is proper tie up. - Zhi Yu; 2017-02-22 - 18010 - Michael Kelley-Install New Flare nut. and pressure test for leaks. We vacuum unit to 490 micron and charge R409a. We test run the unit while retreating all the EQ up to roof. The unit running like Champion. The problem is proper tie up. - Zhi Yu | INTDSA A207B !! This is urgent! Please also reference Work Order TMPE-191633 from September, 2016. The Mitsubishi Electric Mr. Slim air conditioning unit in A207B is not functioning. The control screen on the unit is flashing the word "Check" and some other numbers, but will not turn on. It i. . . 2017-02-20 - 18010 - Called out to John - Amanda Thomas; 2017-02-20 - 18010 - Jennifer Moyer-Called to work with Co-worker on unit. Supervision added me to the work order. Troubleshooting and repair not completed before 3pm, so portable a/c was installed and set at 76 degrees to keep room cool for the night as instructed.1st portable unit delivered, did not work, so I had to get another portable for the room. Unit 1007 installed. Called to another work order, same building. - Jennifer Moyer; 2017-02-22 - 18010 - Zhi Yu-After the steam trap class. Jennifer and I Continue the diagnose on the Code P6. Call the Tech support and waited for 1 1/2 hr. Jen removed the Evap cover to ohm out sensor and find the flare nut cracked cause Freon leak. We carry all needed EQ up to the roof. We Recover 2lbs of R410a. We Cutout flare nut and look for replacement. - Zhi Yu; 2017-02-22 - 18010 - Jennifer Moyer-After the steam trap class. Jennifer and I Continue the diagnose on the Code P6. Call the Tech support and waited for 1 1/2 hr. Jen removed the Evap cover to ohm out sensor and find the flare nut cracked cause Freon leak. We carry all needed EQ up to the roof. We Recover 2lbs of R410a. We Cutout flare nut and look for replacement. - Zhi Yu; 2017-02-22 - 18010 - Zhi Yu-Install New Flare nut. and pressure test for leaks. We vacuum unit to 490 micron and charge R409a. We test run the unit while retreating all the EQ up to roof. The unit running like Champion. The problem is proper tie up. - Zhi Yu; 2017-02-22 - 18010 - Michael Kelley-Install New Flare nut. and pressure test for leaks. We vacuum unit to 490 micron and charge R409a. We test run the unit while retreating all the EQ up to roof. The unit running like Champion. The problem is proper tie up. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30697 | TMPE-219460 | AH 9, Y# 5707, located in B/M pump room has dirty filters. Send to HVAC services for filter change out 42B213C | 2017-02-21 - 18170 - Jose Mazon-filters change completed.. - Jose Mazon | AH 9, Y# 5707, located in B/M pump room has dirty filters. Send to HVAC services for filter change out 42B213C 2017-02-21 - 18170 - Jose Mazon-filters change completed.. - Jose Mazon | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30713 | TMPE-219444 | CDN 162 There is a vent that blows so loud and hard, regardless of the temperature. The air that is blown has a lot of dust in it and is making people sick who are directly under it. It comes and goes roughly every 10 minutes. Please address urgently. Thank you. | 2017-02-24 - 18010 - Thomas Gibble-transfer to EMS . they found VFD on air handler is broke. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-transfer to EMS . they found VFD on air handler is broke. - Thomas Gibble | CDN 162 There is a vent that blows so loud and hard, regardless of the temperature. The air that is blown has a lot of dust in it and is making people sick who are directly under it. It comes and goes roughly every 10 minutes. Please address urgently. Thank you. 2017-02-24 - 18010 - Thomas Gibble-transfer to EMS . they found VFD on air handler is broke. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-transfer to EMS . they found VFD on air handler is broke. - Thomas Gibble | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2017-02-20 | 30715 | TMPE-219442 | TRANSFER TO HVAC Please transfer MWO 217667 to HVAC shop so they can troubleshoot an Environmental Chamber in room 525 LSE. !! Since the air handlers went down this morning, the environmental chamber in LSE 525 isn't coming down to temp. This may need to be reset but it isn't getting colder as . . . | 2017-02-22 - 18140 - Robert Ecabert-Reset condensing unit that was tripped off since Monday, the unit is cooling fine now. Some body must have shut the air handler down or some body must have done something to the pump in order for the growth chamber to trip off. - Robert Ecabert | TRANSFER TO HVAC Please transfer MWO 217667 to HVAC shop so they can troubleshoot an Environmental Chamber in room 525 LSE. !! Since the air handlers went down this morning, the environmental chamber in LSE 525 isn't coming down to temp. This may need to be reset but it isn't getting colder as . . . 2017-02-22 - 18140 - Robert Ecabert-Reset condensing unit that was tripped off since Monday, the unit is cooling fine now. Some body must have shut the air handler down or some body must have done something to the pump in order for the growth chamber to trip off. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-20 | 30716 | TMPE-219441 | The thermostat in that office makes a loud noise after 4:00 pm 42AC6MK | 2017-02-24 - 18010 - Thomas Gibble-t-stat working OK. person in room works to 6 pm. the bld shuts up units at 5 pm. we give her EMC phone number. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-t-stat working OK. person in room works to 6 pm. the bld shuts up units at 5 pm. we give her EMC phone number. - Thomas Gibble | The thermostat in that office makes a loud noise after 4:00 pm 42AC6MK 2017-02-24 - 18010 - Thomas Gibble-t-stat working OK. person in room works to 6 pm. the bld shuts up units at 5 pm. we give her EMC phone number. - Thomas Gibble; 2017-02-24 - 18010 - Gail Jackson-t-stat working OK. person in room works to 6 pm. the bld shuts up units at 5 pm. we give her EMC phone number. - Thomas Gibble | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-21 | 150404 | RNLD-100897 | !! The AC compressor doesn't work. Contact Name: Bailey Dunn Contact Phone Number: 6613309121 Contact Email: dunn_bailey@ymail.com 4NEAL36 | 2017-02-21 - 18030 - Allan Blair-2/21 - 3rd visit for the same call - Allan found the unit tested out properly (again). This time student was there and was informed of how it operates. - Gayle Swenson | !! The AC compressor doesn't work. Contact Name: Bailey Dunn Contact Phone Number: 6613309121 Contact Email: dunn_bailey@ymail.com 4NEAL36 2017-02-21 - 18030 - Allan Blair-2/21 - 3rd visit for the same call - Allan found the unit tested out properly (again). This time student was there and was informed of how it operates. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-21 | 167739 | RFMT-140592 | !! GMM - Please clean and install a new filter in this air handler of this unit (620). 4NEI9DN | 2017-02-22 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | !! GMM - Please clean and install a new filter in this air handler of this unit (620). 4NEI9DN 2017-02-22 - 18170 - Thomas Zambrano-replaced filter. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-21 | 167746 | RFMT-140585 | !! The heater is broken and when i turn it on it blows cold air 4NJNOI0 | 2017-02-21 - 18010 - Thor Millsaps-reset unit to operate in heat mode - Simon Fernandez | !! The heater is broken and when i turn it on it blows cold air 4NJNOI0 2017-02-21 - 18010 - Thor Millsaps-reset unit to operate in heat mode - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-21 | 167752 | RFMT-140579 | Tues. - Please recheck pool chlorine level and make adjustments as needed. | 2017-02-21 - 24000 - Salvatore Marasco Jr--Lowered water to level below missing tiles so contractor could replace missing tiles. -Ran filter backwash to help dilute water and lower chlorine level. -Adjusted auto fill valve so that when water returns to the full level it would be at a good level for flow into the skimmers. -Turned on water aerator to help remove and lower chlorine level. -Opened air bleed valve on top of filter to run a constant flow of water through the 1/4 inch tube and out to the field next to pump house. - Salvatore Marasco Jr | Tues. - Please recheck pool chlorine level and make adjustments as needed. 2017-02-21 - 24000 - Salvatore Marasco Jr--Lowered water to level below missing tiles so contractor could replace missing tiles. -Ran filter backwash to help dilute water and lower chlorine level. -Adjusted auto fill valve so that when water returns to the full level it would be at a good level for flow into the skimmers. -Turned on water aerator to help remove and lower chlorine level. -Opened air bleed valve on top of filter to run a constant flow of water through the 1/4 inch tube and out to the field next to pump house. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-02-21 | 211501 | RACC-117109 | !! I am in VDSD room 1031, bedroom B. The lightbulb in my ceiling fan has probably blown and is no longer working. 4NF2N8D | NA | !! I am in VDSD room 1031, bedroom B. The lightbulb in my ceiling fan has probably blown and is no longer working. 4NF2N8D NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-21 | 251410 | DTPC-117128 | !! I am in UCENT 857 adn my office is 80 degrees - this is too hot to work in. I need an A/C unit turned on. 42C7C1M | 2017-02-23 - 18290 - Steve Skibbe-took drago up to 863 to bid motor replacement - Steve Skibbe; 2017-02-23 - 18290 - Steve Skibbe-investigated no fan no accessibility to access and possible acm insulated duct below asked Greg w to investigate acm - Steve Skibbe; 2017-02-23 - 18290 - Larry Smith-investigated no fan no accessibility to access and possible acm insulated duct below asked Greg w to investigate acm - Steve Skibbe; 2017-03-01 - 18290 - Steve Skibbe-took emcore up to bid this today - Steve Skibbe; 2017-03-02 - 18290 - Steve Skibbe-greg w sampled possible acm - Steve Skibbe; 2017-03-02 - 18290 - Robert Bartels-greg w sampled possible acm - Steve Skibbe; 2017-03-23 - 18290 - Steve Skibbe-set up demo guy to remove duct preventing access set up the mechanic to replace fans for wens day next week - Steve Skibbe; 2017-03-29 - 18290 - Steve Skibbe-motors changed this job is complete - Steve Skibbe | !! I am in UCENT 857 adn my office is 80 degrees - this is too hot to work in. I need an A/C unit turned on. 42C7C1M 2017-02-23 - 18290 - Steve Skibbe-took drago up to 863 to bid motor replacement - Steve Skibbe; 2017-02-23 - 18290 - Steve Skibbe-investigated no fan no accessibility to access and possible acm insulated duct below asked Greg w to investigate acm - Steve Skibbe; 2017-02-23 - 18290 - Larry Smith-investigated no fan no accessibility to access and possible acm insulated duct below asked Greg w to investigate acm - Steve Skibbe; 2017-03-01 - 18290 - Steve Skibbe-took emcore up to bid this today - Steve Skibbe; 2017-03-02 - 18290 - Steve Skibbe-greg w sampled possible acm - Steve Skibbe; 2017-03-02 - 18290 - Robert Bartels-greg w sampled possible acm - Steve Skibbe; 2017-03-23 - 18290 - Steve Skibbe-set up demo guy to remove duct preventing access set up the mechanic to replace fans for wens day next week - Steve Skibbe; 2017-03-29 - 18290 - Steve Skibbe-motors changed this job is complete - Steve Skibbe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2017-02-21 | 30378 | TMPE-219779 | USB The Ice machine in the mechanical area is broken. Please assign to Wesley Jackson | 2017-02-24 - 18210 - Gail Jackson-cleaned water censers, adjusted/repaired bridge censer, trip to warehouse for cleaner, adjusted and run test COMPLETE - Gail Jackson; 2017-02-24 - 18210 - Thomas Gibble-cleaned water censers, adjusted/repaired bridge censer, trip to warehouse for cleaner, adjusted and run test COMPLETE - Gail Jackson | USB The Ice machine in the mechanical area is broken. Please assign to Wesley Jackson 2017-02-24 - 18210 - Gail Jackson-cleaned water censers, adjusted/repaired bridge censer, trip to warehouse for cleaner, adjusted and run test COMPLETE - Gail Jackson; 2017-02-24 - 18210 - Thomas Gibble-cleaned water censers, adjusted/repaired bridge censer, trip to warehouse for cleaner, adjusted and run test COMPLETE - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-21 | 30393 | TMPE-219764 | The AC in the Box Office at Phx Muni is not cooling. Thermostat is set at 74 but the temp is 80. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF | 2017-03-20 - 18290 - Roque Garcia-Replaced the condenser fan motor and blade. It was an emergency call due to baseball having a double header. - Roque Garcia | The AC in the Box Office at Phx Muni is not cooling. Thermostat is set at 74 but the temp is 80. PO is YG202004982. Thank you. Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: James.Vujs@asu.edu 42BDEDF 2017-03-20 - 18290 - Roque Garcia-Replaced the condenser fan motor and blade. It was an emergency call due to baseball having a double header. - Roque Garcia | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-21 | 30441 | TMPE-219716 | Shelby Prockish 02/21/2017 13:34 - HC Shelby- Description of issue: Men's restroom 1st floor, blower for toilet - belt is loud and possibly coming off - and ductwork has fallen off around the vent. Time of Dispatch: Normal hours no dispatch. Dispatched to: N/A | 2017-02-23 - 18010 - Michael Kelley-discovered fan in ceiling. The fan did nothing more than move the air in a ceiling. It served no purpose. Unplugged unit. Contacted Customer. they were happy with no sound. - Michael Kelley | Shelby Prockish 02/21/2017 13:34 - HC Shelby- Description of issue: Men's restroom 1st floor, blower for toilet - belt is loud and possibly coming off - and ductwork has fallen off around the vent. Time of Dispatch: Normal hours no dispatch. Dispatched to: N/A 2017-02-23 - 18010 - Michael Kelley-discovered fan in ceiling. The fan did nothing more than move the air in a ceiling. It served no purpose. Unplugged unit. Contacted Customer. they were happy with no sound. - Michael Kelley | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-02-21 | 30468 | TMPE-219689 | WGTF EMS WO#2219689, HVAC 222362. !! Repeat Request. Previous WO 217457 shows finished in the system. However, the AC continues to blow hot air in the Gymnastics facility. Please repair ASAP. PO is YG202004934. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Conta. . . | 2017-03-03 - 18290 - Cheryl St. John-03.03.17 In the Metasys system, checked HP1, HP2, &amp; HP3 found HP1 off line, HP2 &amp; HP3 calling for cooling with compressors on, both had hot zone temperatures. Sent Bonnie, Steve P. and Ish an email transferring call to HVAC to check out the heat pumps. Created work order for HVAC. Posted labor and finished work order. - Cheryl St. John | WGTF EMS WO#2219689, HVAC 222362. !! Repeat Request. Previous WO 217457 shows finished in the system. However, the AC continues to blow hot air in the Gymnastics facility. Please repair ASAP. PO is YG202004934. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Conta. . . 2017-03-03 - 18290 - Cheryl St. John-03.03.17 In the Metasys system, checked HP1, HP2, &amp; HP3 found HP1 off line, HP2 &amp; HP3 calling for cooling with compressors on, both had hot zone temperatures. Sent Bonnie, Steve P. and Ish an email transferring call to HVAC to check out the heat pumps. Created work order for HVAC. Posted labor and finished work order. - Cheryl St. John | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-21 | 30472 | TMPE-219685 | MU Subway walk in Freezer iced over and not holding temp. Thank you. | 2017-02-21 - 18180 - Called out to Steve - Amanda Thomas; 2017-03-20 - 18180 - Roque Garcia-Found the freezer coil iced up and I asked Subway personal to leave unit off. I returned the next morning and restarted. - Roque Garcia | MU Subway walk in Freezer iced over and not holding temp. Thank you. 2017-02-21 - 18180 - Called out to Steve - Amanda Thomas; 2017-03-20 - 18180 - Roque Garcia-Found the freezer coil iced up and I asked Subway personal to leave unit off. I returned the next morning and restarted. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-21 | 30475 | TMPE-219682 | Pump is turned off at electrical disconnect no tags. Old W/O# for pump leaking 150843 | 2017-03-03 - 23100 - Derek Gittings-still working on pump,have to replac lines. - Derek Gittings; 2017-03-28 - 23100 - Derek Gittings-repaid pump. - Derek Gittings | Pump is turned off at electrical disconnect no tags. Old W/O# for pump leaking 150843 2017-03-03 - 23100 - Derek Gittings-still working on pump,have to replac lines. - Derek Gittings; 2017-03-28 - 23100 - Derek Gittings-repaid pump. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-22 | 167679 | RFMT-140652 | !! I met with residents of B 202/204 today who indicated that they've had reoccurring problems with their A/C unit that continues to freeze and then condensation leaks in the vent area under the A/C unit. There are concerns about mold growing in the space under the A/C unit. Thanks, Carli 4NF4L2O | 2017-03-10 - 18010 - Simon Fernandez-cleaned condensate drain lines and replaced - Simon Fernandez | !! I met with residents of B 202/204 today who indicated that they've had reoccurring problems with their A/C unit that continues to freeze and then condensation leaks in the vent area under the A/C unit. There are concerns about mold growing in the space under the A/C unit. Thanks, Carli 4NF4L2O 2017-03-10 - 18010 - Simon Fernandez-cleaned condensate drain lines and replaced - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-22 | 167680 | RFMT-140651 | !! The cool air has stopped blowing, and I believe the AC USB broken. 4NJKA28 | 2017-02-27 - 18010 - Thor Millsaps-checked a/c unit found return air vent blocked unit okay - Simon Fernandez | !! The cool air has stopped blowing, and I believe the AC USB broken. 4NJKA28 2017-02-27 - 18010 - Thor Millsaps-checked a/c unit found return air vent blocked unit okay - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3
2017-02-22 | 30218 | TMPE-219939 | UNCTRB 3rd Flr Area: SW side of the 3rd Flr. W of rear exit. The customer has expressed a great concern regarding the air quality in a particular area. Many dust pellets floating around the air, also the people sitting in this immediate area are complaining of breathing trouble and general irr. . . | 2017-03-07 - 18010 - Jennifer Moyer-Requester provided an air quality report dated 2/24/17 that states "No current potential pollutant source was identified that may impact IAQ or adversely affect the occupants in the University Center B Building Third Floor Offices". However, she has two HVAC work orders that have not been addressed. As customer service is a priority, I am looking into her concerns. - Jennifer Moyer; 2017-04-12 - 18010 - Jennifer Moyer-Located a damper difuser to solve a problem in room 338. I passed on her other concerns to management. - Jennifer Moyer; 2017-05-17 - 18010 - Jennifer Moyer-Installed air diverter. - Jennifer Moyer | UNCTRB 3rd Flr Area: SW side of the 3rd Flr. W of rear exit. The customer has expressed a great concern regarding the air quality in a particular area. Many dust pellets floating around the air, also the people sitting in this immediate area are complaining of breathing trouble and general irr. . . 2017-03-07 - 18010 - Jennifer Moyer-Requester provided an air quality report dated 2/24/17 that states "No current potential pollutant source was identified that may impact IAQ or adversely affect the occupants in the University Center B Building Third Floor Offices". However, she has two HVAC work orders that have not been addressed. As customer service is a priority, I am looking into her concerns. - Jennifer Moyer; 2017-04-12 - 18010 - Jennifer Moyer-Located a damper difuser to solve a problem in room 338. I passed on her other concerns to management. - Jennifer Moyer; 2017-05-17 - 18010 - Jennifer Moyer-Installed air diverter. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-22 | 30241 | TMPE-219916 | !! It is reported, "growth chamber Green Conviron #2, Y1203 (no. 2, 1203) in LSE 645 stopped working since yesterday." Please inspect and service accordingly at the earliest opportunity. If billable, all charges may be billed to PO #LM502001099. Thank you. 42BLHKH | 2017-03-06 - 18140 - Sent email status request - Amanda Thomas; 2017-03-08 - 18140 - Robert Ecabert-I am in the process of troubleshooting this unit to see why the hot gas solenoid valve and the liquid line solenoid valve are not getting any power. - Robert Ecabert; 2017-03-08 - 18140 - Robert Ecabert-I found the electrical connections that go to the hot gas valve and the liquid line solenoid valve were loose, i tightened the electrical connections and installed a new axial fan and the unit is running fine now. - Robert Ecabert | !! It is reported, "growth chamber Green Conviron #2, Y1203 (no. 2, 1203) in LSE 645 stopped working since yesterday." Please inspect and service accordingly at the earliest opportunity. If billable, all charges may be billed to PO #LM502001099. Thank you. 42BLHKH 2017-03-06 - 18140 - Sent email status request - Amanda Thomas; 2017-03-08 - 18140 - Robert Ecabert-I am in the process of troubleshooting this unit to see why the hot gas solenoid valve and the liquid line solenoid valve are not getting any power. - Robert Ecabert; 2017-03-08 - 18140 - Robert Ecabert-I found the electrical connections that go to the hot gas valve and the liquid line solenoid valve were loose, i tightened the electrical connections and installed a new axial fan and the unit is running fine now. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-02-22 | 30246 | TMPE-219911 | MHALL 224 The a/c is blowing but it is warm air. Could you please have it checked asap. | 2017-03-22 - 18290 - Roque Garcia-Replaced the cond motor checked and tested ok - Roque Garcia | MHALL 224 The a/c is blowing but it is warm air. Could you please have it checked asap. 2017-03-22 - 18290 - Roque Garcia-Replaced the cond motor checked and tested ok - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-22 | 30289 | TMPE-219868 | HAV Dining Hall Hello, I have a cooler at hassy dining hall in the deli that is not working. Can you send someone to work on it. Thanks | 2017-03-21 - 18100 - Roque Garcia-Found both units off. I spoke with Zhi he replaced the evap. on the right side unit. I turned it back on 2/6/2017 and returned 2/7/2017 to check and take temperatures. Both units were working ok. - Roque Garcia | HAV Dining Hall Hello, I have a cooler at hassy dining hall in the deli that is not working. Can you send someone to work on it. Thanks 2017-03-21 - 18100 - Roque Garcia-Found both units off. I spoke with Zhi he replaced the evap. on the right side unit. I turned it back on 2/6/2017 and returned 2/7/2017 to check and take temperatures. Both units were working ok. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-22 | 30299 | TMPE-219858 | MWO - NFA AH#7 VFD Located in RM224U1 EMS is calling for AH#7 to run, there is power to the VFD however, the unit is not running. The FA Circuit has been checked and is not the issue. Can you please send someone out to check the VFD. | 2017-02-23 - 15100 - Semeon Haile-transferred to HVAC shop broken belt - Semeon Haile | MWO - NFA AH#7 VFD Located in RM224U1 EMS is calling for AH#7 to run, there is power to the VFD however, the unit is not running. The FA Circuit has been checked and is not the issue. Can you please send someone out to check the VFD. 2017-02-23 - 15100 - Semeon Haile-transferred to HVAC shop broken belt - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-22 | 30344 | TMPE-219813 | It is reported, ": LSE 539 Details: The walk-in growth chamber LSE 539 is overheating. It is set for 30 degrees and is currently at 36.7 degrees. Please have it looked at ASAP." Thank you. 42BLHKH | 2017-02-23 - 18140 - Robert Ecabert-This walk in growth chamber tripped off the other day when they shut down the air handlers to change the air filters on the roof air handlers. Anna Keilty who has this walk in reset this unit herself and the unit has been working fine ever since according to Anna Keilty. - Robert Ecabert | It is reported, ": LSE 539 Details: The walk-in growth chamber LSE 539 is overheating. It is set for 30 degrees and is currently at 36.7 degrees. Please have it looked at ASAP." Thank you. 42BLHKH 2017-02-23 - 18140 - Robert Ecabert-This walk in growth chamber tripped off the other day when they shut down the air handlers to change the air filters on the roof air handlers. Anna Keilty who has this walk in reset this unit herself and the unit has been working fine ever since according to Anna Keilty. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-22 | 30358 | TMPE-219799 | work order for the HVAC shop Building 048 Nelson Fine Arts Center. Per Gail Jackson - Pump housing are floods whenever it rains and causes electrical problems. Check location for a sump pump | 2017-03-09 - 23100 - Gail Jackson-Trip to ACE for parts, install parts, install sump pump, run test. No voltage at light terminal; need electrician to trace out. - Gail Jackson; 2017-03-09 - 23100 - Thomas Gibble-Trip to ACE for parts, install parts, install sump pump, run test. No voltage at light terminal; need electrician to trace out. - Gail Jackson; 2017-03-23 - 23100 - Gail Jackson-Finish wiring lights , fountain pump and sump pump. Fountain pump will need to run 24/7 during monsoon to keep water out of electrical chamber, sump is on same circuit as fountain. Wired lights and filled with water. RUN TEST COMPLETE. - Gail Jackson; 2017-03-23 - 23100 - Thomas Gibble-Finish wiring lights , fountain pump and sump pump. Fountain pump will need to run 24/7 during monsoon to keep water out of electrical chamber, sump is on same circuit as fountain. Wired lights and filled with water. RUN TEST COMPLETE. - Gail Jackson | work order for the HVAC shop Building 048 Nelson Fine Arts Center. Per Gail Jackson - Pump housing are floods whenever it rains and causes electrical problems. Check location for a sump pump 2017-03-09 - 23100 - Gail Jackson-Trip to ACE for parts, install parts, install sump pump, run test. No voltage at light terminal; need electrician to trace out. - Gail Jackson; 2017-03-09 - 23100 - Thomas Gibble-Trip to ACE for parts, install parts, install sump pump, run test. No voltage at light terminal; need electrician to trace out. - Gail Jackson; 2017-03-23 - 23100 - Gail Jackson-Finish wiring lights , fountain pump and sump pump. Fountain pump will need to run 24/7 during monsoon to keep water out of electrical chamber, sump is on same circuit as fountain. Wired lights and filled with water. RUN TEST COMPLETE. - Gail Jackson; 2017-03-23 - 23100 - Thomas Gibble-Finish wiring lights , fountain pump and sump pump. Fountain pump will need to run 24/7 during monsoon to keep water out of electrical chamber, sump is on same circuit as fountain. Wired lights and filled with water. RUN TEST COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-02-22 | 30359 | TMPE-219798 | Building NO.084 Music for work done on exterior decorative water fountain. Per Gail Jackson - Install new pump and motor assembly. | 2017-02-24 - 23100 - Thomas Gibble-replaced pump for fountain and picked up parts at ace. - Thomas Gibble; 2017-02-24 - 23100 - Gail Jackson-replaced pump for fountain and picked up parts at ace. - Thomas Gibble | Building NO.084 Music for work done on exterior decorative water fountain. Per Gail Jackson - Install new pump and motor assembly. 2017-02-24 - 23100 - Thomas Gibble-replaced pump for fountain and picked up parts at ace. - Thomas Gibble; 2017-02-24 - 23100 - Gail Jackson-replaced pump for fountain and picked up parts at ace. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-23 | 167616 | RFMT-140715 | A/C is broken. Has been for a couple of weeks. 4O0BFBB | 2017-02-27 - 18010 - Simon Fernandez-checked a/c unit found bad t-stat removed replaced t-stat ,unit okay - Simon Fernandez | A/C is broken. Has been for a couple of weeks. 4O0BFBB 2017-02-27 - 18010 - Simon Fernandez-checked a/c unit found bad t-stat removed replaced t-stat ,unit okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-23 | 1813 | WEST-109436 | The VWR glass door refrigerator's fan is making a noise. Do we have a HVAC/refrigeration tech that could take a look at this? Contact Name: Peter Jurutka Contact Phone Number: (602)543-6087 Contact Email: peter.jurutka@asu.edu Attachment(s) | 2017-02-24 - 18240 - Reassigned to Chad to check and provide estimate. TMW 0750 2/24/17 - Thomas Wienand; 2017-02-24 - 18240 - Chad T Ball-Found the refrigerator had a severely iced over evaporator coil. Referred to Service contractor for that equipment. - Chad T Ball | The VWR glass door refrigerator's fan is making a noise. Do we have a HVAC/refrigeration tech that could take a look at this? Contact Name: Peter Jurutka Contact Phone Number: (602)543-6087 Contact Email: peter.jurutka@asu.edu Attachment(s) 2017-02-24 - 18240 - Reassigned to Chad to check and provide estimate. TMW 0750 2/24/17 - Thomas Wienand; 2017-02-24 - 18240 - Chad T Ball-Found the refrigerator had a severely iced over evaporator coil. Referred to Service contractor for that equipment. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-23 | 211454 | RACC-117156 | microwave plate does not turn 4NI4EOB | 2017-02-28 - 10010 - replaced turn table motor Aaron - Jim Deal | microwave plate does not turn 4NI4EOB 2017-02-28 - 10010 - replaced turn table motor Aaron - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-23 | 30088 | TMPE-220069 | Central Plant - replace two broken belts on air compressor #1. | 2017-02-23 - 30010 - Louis Ballejos-Replaced 2 broken belts, properly adjusted belt tension. Cleaned air compressor. - Lisa Anderson | Central Plant - replace two broken belts on air compressor #1. 2017-02-23 - 30010 - Louis Ballejos-Replaced 2 broken belts, properly adjusted belt tension. Cleaned air compressor. - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-02-23 | 30120 | TMPE-220037 | Please check the circuit breaker on the west side of San Pablo for the roof vent fan it keep blowing circuits. | 2017-03-03 - 15010 - Gary Conover-Job complete - Gary Conover | Please check the circuit breaker on the west side of San Pablo for the roof vent fan it keep blowing circuits. 2017-03-03 - 15010 - Gary Conover-Job complete - Gary Conover | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-23 | 30121 | TMPE-220036 | Please check the A/C on the west side of the roof of San Pablo it keeps blowing fuses and EQ rooms are getting hot. | NA | Please check the A/C on the west side of the roof of San Pablo it keeps blowing fuses and EQ rooms are getting hot. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-23 | 30133 | TMPE-220024 | MU Jamba Juice The ice machine in Jamba juice in the memorial union building is not working pLEASE HANDLE APPROPIATELY COULD POSE A SAFETY RISK | 2017-02-27 - 18210 - Gail Jackson-Unit was not making ice, reset, made ice. Will check back in A.M. for new codes. - Gail Jackson; 2017-03-01 - 18210 - Gail Jackson-Found machine auger motor running but no compressor. Contactor FRIED. Trip to ARS Tempe for defrost time clock and contactor; they did not have. Called around trip to RSD for contactor. Installed parts and cleaned ice machinE; repaired/ replaced drain line in back which was broke off run test COMPLETE. - Gail Jackson; 2017-03-01 - 18210 - Thomas Gibble-Found machine auger motor running but no compressor. Contactor FRIED. Trip to ARS Tempe for defrost time clock and contactor; they did not have. Called around trip to RSD for contactor. Installed parts and cleaned ice machinE; repaired/ replaced drain line in back which was broke off run test COMPLETE. - Gail Jackson | MU Jamba Juice The ice machine in Jamba juice in the memorial union building is not working pLEASE HANDLE APPROPIATELY COULD POSE A SAFETY RISK 2017-02-27 - 18210 - Gail Jackson-Unit was not making ice, reset, made ice. Will check back in A.M. for new codes. - Gail Jackson; 2017-03-01 - 18210 - Gail Jackson-Found machine auger motor running but no compressor. Contactor FRIED. Trip to ARS Tempe for defrost time clock and contactor; they did not have. Called around trip to RSD for contactor. Installed parts and cleaned ice machinE; repaired/ replaced drain line in back which was broke off run test COMPLETE. - Gail Jackson; 2017-03-01 - 18210 - Thomas Gibble-Found machine auger motor running but no compressor. Contactor FRIED. Trip to ARS Tempe for defrost time clock and contactor; they did not have. Called around trip to RSD for contactor. Installed parts and cleaned ice machinE; repaired/ replaced drain line in back which was broke off run test COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 6
2017-02-23 | 30181 | TMPE-219976 | roof repair | 2017-02-24 - 13120 - Christopher Dovales-water testing to locate leaks on cooler and curbs - Christopher Dovales; 2017-02-24 - 13120 - Christopher Dovales-cleaning out old sealant on cooler and curb placed metal flashing under cooler and sealed flash in metal pan curb joints - Christopher Dovales; 2017-02-24 - 13120 - Christopher Dovales-water tested cooler no leaks - Christopher Dovales; 2017-02-28 - 13120 - Christopher Dovales-cleaning out old sealant and flashed joints holes on metal curb pan - Christopher Dovales; 2017-03-01 - 13120 - Christopher Dovales-checking on roof leaks no leaks - Christopher Dovales; 2017-03-28 - 13120 - Christopher Dovales-Cleaning out old sealant off metal curb pan joints - Christopher Dovales; 2017-03-30 - 13120 - Christopher Dovales-Cleaning off old sealant on metal pan curb joints - Christopher Dovales; 2017-03-31 - 13120 - Christopher Dovales-Cleaned and flashed in joints on metal pan on AC curb - Christopher Dovales; 2017-04-03 - 13120 - Christopher Dovales-picked up my trash repairs are completed - Christopher Dovales | roof repair 2017-02-24 - 13120 - Christopher Dovales-water testing to locate leaks on cooler and curbs - Christopher Dovales; 2017-02-24 - 13120 - Christopher Dovales-cleaning out old sealant on cooler and curb placed metal flashing under cooler and sealed flash in metal pan curb joints - Christopher Dovales; 2017-02-24 - 13120 - Christopher Dovales-water tested cooler no leaks - Christopher Dovales; 2017-02-28 - 13120 - Christopher Dovales-cleaning out old sealant and flashed joints holes on metal curb pan - Christopher Dovales; 2017-03-01 - 13120 - Christopher Dovales-checking on roof leaks no leaks - Christopher Dovales; 2017-03-28 - 13120 - Christopher Dovales-Cleaning out old sealant off metal curb pan joints - Christopher Dovales; 2017-03-30 - 13120 - Christopher Dovales-Cleaning off old sealant on metal pan curb joints - Christopher Dovales; 2017-03-31 - 13120 - Christopher Dovales-Cleaned and flashed in joints on metal pan on AC curb - Christopher Dovales; 2017-04-03 - 13120 - Christopher Dovales-picked up my trash repairs are completed - Christopher Dovales | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-23 | 30194 | TMPE-219963 | Motor shaft seized | 2017-03-14 - 18230 - Thomas Gibble-replace pump.went to grainger to pick it up - Thomas Gibble; 2017-03-14 - 18230 - Gail Jackson-replace pump.went to grainger to pick it up - Thomas Gibble | Motor shaft seized 2017-03-14 - 18230 - Thomas Gibble-replace pump.went to grainger to pick it up - Thomas Gibble; 2017-03-14 - 18230 - Gail Jackson-replace pump.went to grainger to pick it up - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-24 | 167564 | RFMT-140767 | !! door is broken the closet door thing that keeps it sliding dislodged and now it if free swinging 4NO9320 | 2017-03-06 - 13000 - Thomas Zambrano-repair door and flush unit. - Thomas Zambrano | !! door is broken the closet door thing that keeps it sliding dislodged and now it if free swinging 4NO9320 2017-03-06 - 13000 - Thomas Zambrano-repair door and flush unit. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-24 | 230919 | POLY-117279 | Annual | 2017-04-11 - 50010 - Luis Vasquez-3/17 - Luis checked the light tower, and it started right up. All 4 lights work good. Checked all fluids, air in tires and air filter. He cleaned and washed the light tower. - Gayle Swenson | Annual 2017-04-11 - 50010 - Luis Vasquez-3/17 - Luis checked the light tower, and it started right up. All 4 lights work good. Checked all fluids, air in tires and air filter. He cleaned and washed the light tower. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-24 | 29904 | TMPE-220253 | HVAC to PL-Bad circulation pump Strange sound coming from AC vent in the office. 4N63726 | 2017-02-24 - 23100 - Bradley Kruse-Checked out air handler and found nothing leaking. Sound is coming from recirc pump that is on another work oreder - Bradley Kruse | HVAC to PL-Bad circulation pump Strange sound coming from AC vent in the office. 4N63726 2017-02-24 - 23100 - Bradley Kruse-Checked out air handler and found nothing leaking. Sound is coming from recirc pump that is on another work oreder - Bradley Kruse | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-24 | 29935 | TMPE-220222 | !! Call is for Electric Shop. AHU-2 supply fan contactor trips on overload immediately after starting. 4N57E46 | 2017-03-07 - 15000 - Gary Conover-replaced overload relay - Semeon Haile | !! Call is for Electric Shop. AHU-2 supply fan contactor trips on overload immediately after starting. 4N57E46 2017-03-07 - 15000 - Gary Conover-replaced overload relay - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-24 | 30001 | TMPE-220156 | The motor on the vacuum pump is grounded out. The fuses for the disconnect are located under the disconnect. Had an electrician check the MCC and found it to be working correctly. Checked the motor and it is still grounding out and the windings are burnt. Please see WO# TMPE-180615 for addition. . . | 2017-03-09 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-07 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-14 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-21 - 18230 - Derek Gittings-replacing motor,rewire. - Derek Gittings; 2017-04-25 - 18230 - Derek Gittings-replace motor,coupling.rewire - Derek Gittings; 2017-04-26 - 18230 - Michael Kelley-replaced motor. - Derek Gittings; 2017-04-26 - 18230 - Michael Kelley-replaced motor. - Derek Gittings | The motor on the vacuum pump is grounded out. The fuses for the disconnect are located under the disconnect. Had an electrician check the MCC and found it to be working correctly. Checked the motor and it is still grounding out and the windings are burnt. Please see WO# TMPE-180615 for addition. . . 2017-03-09 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-07 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-14 - 18230 - Derek Gittings-replacing motor. - Derek Gittings; 2017-04-21 - 18230 - Derek Gittings-replacing motor,rewire. - Derek Gittings; 2017-04-25 - 18230 - Derek Gittings-replace motor,coupling.rewire - Derek Gittings; 2017-04-26 - 18230 - Michael Kelley-replaced motor. - Derek Gittings; 2017-04-26 - 18230 - Michael Kelley-replaced motor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-02-24 | 30017 | TMPE-220140 | for HVAC Bateman PSF room F12. This room has a temperature alarm that that activates at 80\\xb0F and reports back to Central Plant. Please empty the condensate pan on the portable AC Unit supporting the steam leak. This needs to be checked and emptied 3 times per shift. Please assign to Rober. . . | 2017-02-27 - 18010 - Robert Dauscher-installed condensate pump on to spot cooler to prevent unit from shutting off during the night from excess condensate. - Robert Dauscher; 2017-02-27 - 18010 - Robert Dauscher-verify pump/ac operation - Robert Dauscher; 2017-02-27 - 18010 - Robert Dauscher-verify pump/ac operation - Robert Dauscher | for HVAC Bateman PSF room F12. This room has a temperature alarm that that activates at 80\\xb0F and reports back to Central Plant. Please empty the condensate pan on the portable AC Unit supporting the steam leak. This needs to be checked and emptied 3 times per shift. Please assign to Rober. . . 2017-02-27 - 18010 - Robert Dauscher-installed condensate pump on to spot cooler to prevent unit from shutting off during the night from excess condensate. - Robert Dauscher; 2017-02-27 - 18010 - Robert Dauscher-verify pump/ac operation - Robert Dauscher; 2017-02-27 - 18010 - Robert Dauscher-verify pump/ac operation - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-02-25 | 167548 | RFMT-140783 | !! Dishwasher is plugged up and is leaking. Needs to be cleaned out and fixed. 4O20BKO | 2017-02-27 - 27010 - Thomas Zambrano-troubleshoot dishwasher and found bad door seal and problems with the run dial. need to replace dishwasher. - Thomas Zambrano; 2017-03-03 - 27010 - Thomas Zambrano-replaced dishwasher. - Thomas Zambrano | !! Dishwasher is plugged up and is leaking. Needs to be cleaned out and fixed. 4O20BKO 2017-02-27 - 27010 - Thomas Zambrano-troubleshoot dishwasher and found bad door seal and problems with the run dial. need to replace dishwasher. - Thomas Zambrano; 2017-03-03 - 27010 - Thomas Zambrano-replaced dishwasher. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-25 | 211397 | RACC-117213 | !! A/C filter change needed. 4O0JAGG | NA | !! A/C filter change needed. 4O0JAGG NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-25 | 28555 | TMPE-221602 | !! Building located at 620 E Orange street (NOT in the psychology building!) The quality of the air in the conference room (SCOB 361) is very poor. It changed for the worse during the past two weeks. The air seems to be very filthy and dusty. We would very much appreciate your assistance on t. . . | 2017-02-27 - 18010 - Jennifer Moyer-Dirty filters dated 11/9/16 are causing an increased amount of dust in the room. - Jennifer Moyer [Modified: 2017-02-27 Jennifer Moyer]; 2017-03-06 - 18010 - Jennifer Moyer-Building was added to the filter crew schedule to address the problem. A message was left on the requestor's voice mail explaining that this work order will be addressed. - Jennifer Moyer | !! Building located at 620 E Orange street (NOT in the psychology building!) The quality of the air in the conference room (SCOB 361) is very poor. It changed for the worse during the past two weeks. The air seems to be very filthy and dusty. We would very much appreciate your assistance on t. . . 2017-02-27 - 18010 - Jennifer Moyer-Dirty filters dated 11/9/16 are causing an increased amount of dust in the room. - Jennifer Moyer [Modified: 2017-02-27 Jennifer Moyer]; 2017-03-06 - 18010 - Jennifer Moyer-Building was added to the filter crew schedule to address the problem. A message was left on the requestor's voice mail explaining that this work order will be addressed. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-25 | 28588 | TMPE-221569 | ASUHC Agent: Justin Neel Description: HVAC Leaking water, needs fix and clean up, called Robert and will go take a look and call back with clean up if needed Who was dispatched: Robert Dauscher Time of Dispatch: 1207PM Cindy Luna 02/25/2017 13:04 - Robert called, the leak is contained. Need O. . . | 2017-02-27 - 18050 - Robert Dauscher-Checked unit found frozen back to compressor. Turned off disconnect, used shop vac to remove water - clear drain line. need to return and inspect unit once ice has melted. - Robert Dauscher; 2017-02-27 - 18050 - Robert Dauscher-Returned to inspect unit. found business closed, lights all off. ALARM STICKERS ON WINDOWS. Knocked on both doors- no answer. Will need to return when office staff is in. - Robert Dauscher | ASUHC Agent: Justin Neel Description: HVAC Leaking water, needs fix and clean up, called Robert and will go take a look and call back with clean up if needed Who was dispatched: Robert Dauscher Time of Dispatch: 1207PM Cindy Luna 02/25/2017 13:04 - Robert called, the leak is contained. Need O. . . 2017-02-27 - 18050 - Robert Dauscher-Checked unit found frozen back to compressor. Turned off disconnect, used shop vac to remove water - clear drain line. need to return and inspect unit once ice has melted. - Robert Dauscher; 2017-02-27 - 18050 - Robert Dauscher-Returned to inspect unit. found business closed, lights all off. ALARM STICKERS ON WINDOWS. Knocked on both doors- no answer. Will need to return when office staff is in. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-02-26 | 167532 | RFMT-140799 | !! I need help with the Air Conditioning system. It stopped working and I don't know why. 4O1G68L | 2017-02-27 - 18010 - Scott Berndt-loose wire connection.....reconnnected the wire back on the motor... - Scott Berndt | !! I need help with the Air Conditioning system. It stopped working and I don't know why. 4O1G68L 2017-02-27 - 18010 - Scott Berndt-loose wire connection.....reconnnected the wire back on the motor... - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-26 | 211403 | RACC-117207 | !! Hello, My air conditioning unit is currently leaking in my bathroom. It does this on a regular basis but I can usually clean it up with a towel. Please resolve this issue at your earliest convenience. - Paul Miller Contact Name: Paul Miller Contact Phone Number: 9542571101 Contact Email: pjmille. . . | NA | !! Hello, My air conditioning unit is currently leaking in my bathroom. It does this on a regular basis but I can usually clean it up with a towel. Please resolve this issue at your earliest convenience. - Paul Miller Contact Name: Paul Miller Contact Phone Number: 9542571101 Contact Email: pjmille. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-26 | 211417 | RACC-117193 | Grey water in dishwasher from previous flooding (that occurred prior to me moving in). Air vent in hallway looks extremely dirty. 4NK9FCE | NA | Grey water in dishwasher from previous flooding (that occurred prior to me moving in). Air vent in hallway looks extremely dirty. 4NK9FCE NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-26 | 28567 | TMPE-221590 | !! AC is not cooling the room, fan is blowing but there is no cold air. The temperature is stuck at 74. Please fix asap. 4O03KFF | 2017-04-04 - 18290 - Roque Garcia-Replaced defrost boards and sheave - Roque Garcia | !! AC is not cooling the room, fan is blowing but there is no cold air. The temperature is stuck at 74. Please fix asap. 4O03KFF 2017-04-04 - 18290 - Roque Garcia-Replaced defrost boards and sheave - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-27 | 167479 | RFMT-140852 | Replace Exhaust fan motor San Pablo west | 2017-02-28 - 18160 - John Romero-This work order need to go to Simon or Thor - John Romero | Replace Exhaust fan motor San Pablo west 2017-02-28 - 18160 - John Romero-This work order need to go to Simon or Thor - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-27 | 1583 | WEST-109666 | Central Plant Monthly General Maintenance of Equipment Spaces | 2017-02-27 - xPM-WC-CPGEN-M - David Valentine-putting things away, started touching up curbs in CB. - David Valentine; 2017-02-27 - xPM-WC-CPGEN-M - Joseph McCormick-Shop-vac, mop, clean with scour pad on buffer, then mopped again the following: from #1 sand filter east to pump #7&amp;8, most of eastern half of phase 3. - Joseph McCormick; 2017-02-28 - xPM-WC-CPGEN-M - Kevin Brenden-Painted bases of CH: 1 &amp; 3. (yellow safety paint). - Kevin Brenden; 2017-02-28 - xPM-WC-CPGEN-M - Joseph McCormick-Completed the cleaning of the floor in phase 3. - Joseph McCormick; 2017-03-01 - xPM-WC-CPGEN-M - Anthony Tucson-Sorted and brought spare parts to the control storage area. - Anthony Tucson; 2017-03-03 - xPM-WC-CPGEN-M - David Valentine-cleaned up mess from SF #4 strainer cleaning. - David Valentine; 2017-03-03 - xPM-WC-CPGEN-M - Donald Miller-Cleaned basement and inventoried parts - Donald Miller; 2017-03-06 - xPM-WC-CPGEN-M - Kevin Brenden-Began painting CH: 2 concrete base. (yellow) - Kevin Brenden; 2017-03-06 - xPM-WC-CPGEN-M - Kevin Brenden-Painted remaining CH: 2 concrete base. (yellow). - Kevin Brenden; 2017-03-06 - xPM-WC-CPGEN-M - David Valentine-cleaning up around tube punching ops. - David Valentine; 2017-03-10 - xPM-WC-CPGEN-M - Joseph McCormick-Shop-vac up floor coating chips and dirt in north basement north end from control air compressor to drill press. - Joseph McCormick; 2017-03-10 - xPM-WC-CPGEN-M - Donald Miller-Worked in parts room. Emptied trash from garbage cans. Removed boxes and scrap metal to proper recycle bins - Donald Miller; 2017-03-12 - xPM-WC-CPGEN-M - Kevin Brenden-Took CP basement trash to trash dump. - Kevin Brenden; 2017-03-12 - xPM-WC-CPGEN-M - Kevin Brenden-Swept CP chiller bay floor. - Kevin Brenden; 2017-03-13 - xPM-WC-CPGEN-M - Joseph McCormick-Used scouring pad on buffer, then mopped up soap and dirt until fairly clear. Did this in north basement from north loop tunnel entrance and north control air compressor eastward to drill press. Got the top several layers of grime. Will require a second cleaning. - Joseph McCormick; 2017-03-14 - xPM-WC-CPGEN-M - Kevin Brenden-Cleaned/dusted chemical pvc piping/lines. - Kevin Brenden; 2017-03-14 - xPM-WC-CPGEN-M - David Valentine-cleaning, straightening up. - David Valentine; 2017-03-14 - xPM-WC-CPGEN-M - David Valentine-cleaning around water treatment chemical pumps. - David Valentine; 2017-03-14 - xPM-WC-CPGEN-M - Donald Miller-Started reorganizing parts shelves on right side of parts room. Was able to sort and organize gasket material, orings, motors,and electrical wiring - Donald Miller; 2017-03-15 - xPM-WC-CPGEN-M - Joseph McCormick-Scouring pad under buffer, Mopping and shop-vac paint/ coating chips in north basement from welding table to first section of big shelves. Moved stuff around out of the way as needed. - Joseph McCormick; 2017-03-15 - xPM-WC-CPGEN-M - Donald Miller-Finished reorganizing parts room. - Donald Miller; 2017-03-15 - xPM-WC-CPGEN-M - Chad T Ball-Staged filters from stores warehouse to FAB AHU 1,2,3,4,5,6,7,8,9,10,11 and 12. CLCC1 AHU 1 and 2 - Chad T Ball; 2017-03-16 - xPM-WC-CPGEN-M - Joseph McCormick-used buffer with scouring pad, then mopped til clean in north basement from bead blaster and 7 &amp; 8 VFD eastward to third section of big shelves. Used shop-vac to pic up loosened coating / paint chips. - Joseph McCormick; 2017-03-16 - xPM-WC-CPGEN-M - Donald Miller-Cleaned parts room and repacked tower 4 sand filter valves - Donald Miller; 2017-03-17 - xPM-WC-CPGEN-M - Joseph McCormick-shop-vac up loose paint / coating chips start moving stuff back into north basement between bead blaster and the first two sections of big shelves. - Joseph McCormick; 2017-03-17 - xPM-WC-CPGEN-M - Chad T Ball-Assisted Joe with moving lockers, hydraulic press and bead blast cabinet for floor cleaning. - Chad T Ball; 2017-03-17 - xPM-WC-CPGEN-M - Donald Miller-Worked on sand filter for tower 4. Did prep work to begin grinding rust from filter base - Donald Miller; 2017-03-20 - xPM-WC-CPGEN-M - Kevin Brenden-Swept CP chiller bay floor. - Kevin Brenden; 2017-03-20 - xPM-WC-CPGEN-M - Anthony Tucson-Reorganize parts room. organize siemens parts and controllers. - Anthony Tucson; 2017-03-21 - xPM-WC-CPGEN-M - Donald Miller-Assisted in moving equipment around in basement for floor cleaning and cleaned tool room. Hauled garbage from basement to dumpster - Donald Miller; 2017-03-22 - xPM-WC-CPGEN-M - Joseph McCormick-Cleaned floor in north basement from east wall to 1st concrete pillar. Scouring pad with buffer, mopped until clean. Shop-vac up loose coating / paint chips. - Joseph McCormick; 2017-03-22 - xPM-WC-CPGEN-M - Joseph McCormick-Was in the process of cleaning the last 15' X 20' section of basement floor, whenever I was told that an outside vendor will be in next Wed. to bid on re-coating it. Went ahead and used buffer with scouring pad. Mopped until clean. Shop-vac up loose coating / paint chips. - Joseph McCormick; 2017-03-22 - xPM-WC-CPGEN-M - Donald Miller-Cleaned area around pumps 23 and 24 - Donald Miller; 2017-03-23 - xPM-WC-CPGEN-M - Joseph McCormick-Put away buffer, shop-vac and mop w/ wringer. Moved all of the stuff back into the north end of the basement. Awaiting bid next week for re-surfacing and coating of basement floor. - Joseph McCormick; 2017-03-23 - xPM-WC-CPGEN-M - David Valentine-emptied trash in CB and BSMT, removed "a" frame from sump pump area to storage area. - David Valentine; 2017-03-23 - xPM-WC-CPGEN-M - Donald Miller-Repaired shop tools, cleaned basement, removed trash and disposed of several worthless cabinets - Donald Miller; 2017-03-23 - xPM-WC-CPGEN-M - Ronald Chaffee-Checked batteries on CP golf cart. Added water and put on charger. - Ronald Chaffee; 2017-03-28 - xPM-WC-CPGEN-M - Joseph McCormick-Swept basement floor of loose coating chips in prep for vendor coming to quote the re-surfacing and re-coating of floor. Swept chiller bay and mopped around leaking West Chemical flush pump on #4 condenser. Wiped up grease from pumps. - Joseph McCormick; 2017-03-29 - xPM-WC-CPGEN-M - Chad T Ball-Swept and cleaned up debris and insulation from where we had worked on CLCC1 chilled water valve at tunnel entrance. Removed dirty filters from KIVA mezzanine and took them to the compactor. - Chad T Ball; 2017-03-29 - xPM-WC-CPGEN-M - Joseph McCormick-Cleaned and wiped down pumps 4&amp;17 pumps, motor, piping and baseplates. Did same for chill water sand filter and UV light system. - Joseph McCormick; 2017-03-30 - xPM-WC-CPGEN-M - Joseph McCormick-Continued to wipe down equipment from UV filtration system south to the flat plate heat exchangers. - Joseph McCormick; 2017-03-31 - xPM-WC-CPGEN-M - Randy Randell-sweep and dust chill water pump room studentcenter rec center - Randy Randell; 2017-03-31 - xPM-WC-CPGEN-M - Thomas Wienand-Monthly review - Thomas Wienand | Central Plant Monthly General Maintenance of Equipment Spaces 2017-02-27 - xPM-WC-CPGEN-M - David Valentine-putting things away, started touching up curbs in CB. - David Valentine; 2017-02-27 - xPM-WC-CPGEN-M - Joseph McCormick-Shop-vac, mop, clean with scour pad on buffer, then mopped again the following: from #1 sand filter east to pump #7&amp;8, most of eastern half of phase 3. - Joseph McCormick; 2017-02-28 - xPM-WC-CPGEN-M - Kevin Brenden-Painted bases of CH: 1 &amp; 3. (yellow safety paint). - Kevin Brenden; 2017-02-28 - xPM-WC-CPGEN-M - Joseph McCormick-Completed the cleaning of the floor in phase 3. - Joseph McCormick; 2017-03-01 - xPM-WC-CPGEN-M - Anthony Tucson-Sorted and brought spare parts to the control storage area. - Anthony Tucson; 2017-03-03 - xPM-WC-CPGEN-M - David Valentine-cleaned up mess from SF #4 strainer cleaning. - David Valentine; 2017-03-03 - xPM-WC-CPGEN-M - Donald Miller-Cleaned basement and inventoried parts - Donald Miller; 2017-03-06 - xPM-WC-CPGEN-M - Kevin Brenden-Began painting CH: 2 concrete base. (yellow) - Kevin Brenden; 2017-03-06 - xPM-WC-CPGEN-M - Kevin Brenden-Painted remaining CH: 2 concrete base. (yellow). - Kevin Brenden; 2017-03-06 - xPM-WC-CPGEN-M - David Valentine-cleaning up around tube punching ops. - David Valentine; 2017-03-10 - xPM-WC-CPGEN-M - Joseph McCormick-Shop-vac up floor coating chips and dirt in north basement north end from control air compressor to drill press. - Joseph McCormick; 2017-03-10 - xPM-WC-CPGEN-M - Donald Miller-Worked in parts room. Emptied trash from garbage cans. Removed boxes and scrap metal to proper recycle bins - Donald Miller; 2017-03-12 - xPM-WC-CPGEN-M - Kevin Brenden-Took CP basement trash to trash dump. - Kevin Brenden; 2017-03-12 - xPM-WC-CPGEN-M - Kevin Brenden-Swept CP chiller bay floor. - Kevin Brenden; 2017-03-13 - xPM-WC-CPGEN-M - Joseph McCormick-Used scouring pad on buffer, then mopped up soap and dirt until fairly clear. Did this in north basement from north loop tunnel entrance and north control air compressor eastward to drill press. Got the top several layers of grime. Will require a second cleaning. - Joseph McCormick; 2017-03-14 - xPM-WC-CPGEN-M - Kevin Brenden-Cleaned/dusted chemical pvc piping/lines. - Kevin Brenden; 2017-03-14 - xPM-WC-CPGEN-M - David Valentine-cleaning, straightening up. - David Valentine; 2017-03-14 - xPM-WC-CPGEN-M - David Valentine-cleaning around water treatment chemical pumps. - David Valentine; 2017-03-14 - xPM-WC-CPGEN-M - Donald Miller-Started reorganizing parts shelves on right side of parts room. Was able to sort and organize gasket material, orings, motors,and electrical wiring - Donald Miller; 2017-03-15 - xPM-WC-CPGEN-M - Joseph McCormick-Scouring pad under buffer, Mopping and shop-vac paint/ coating chips in north basement from welding table to first section of big shelves. Moved stuff around out of the way as needed. - Joseph McCormick; 2017-03-15 - xPM-WC-CPGEN-M - Donald Miller-Finished reorganizing parts room. - Donald Miller; 2017-03-15 - xPM-WC-CPGEN-M - Chad T Ball-Staged filters from stores warehouse to FAB AHU 1,2,3,4,5,6,7,8,9,10,11 and 12. CLCC1 AHU 1 and 2 - Chad T Ball; 2017-03-16 - xPM-WC-CPGEN-M - Joseph McCormick-used buffer with scouring pad, then mopped til clean in north basement from bead blaster and 7 &amp; 8 VFD eastward to third section of big shelves. Used shop-vac to pic up loosened coating / paint chips. - Joseph McCormick; 2017-03-16 - xPM-WC-CPGEN-M - Donald Miller-Cleaned parts room and repacked tower 4 sand filter valves - Donald Miller; 2017-03-17 - xPM-WC-CPGEN-M - Joseph McCormick-shop-vac up loose paint / coating chips start moving stuff back into north basement between bead blaster and the first two sections of big shelves. - Joseph McCormick; 2017-03-17 - xPM-WC-CPGEN-M - Chad T Ball-Assisted Joe with moving lockers, hydraulic press and bead blast cabinet for floor cleaning. - Chad T Ball; 2017-03-17 - xPM-WC-CPGEN-M - Donald Miller-Worked on sand filter for tower 4. Did prep work to begin grinding rust from filter base - Donald Miller; 2017-03-20 - xPM-WC-CPGEN-M - Kevin Brenden-Swept CP chiller bay floor. - Kevin Brenden; 2017-03-20 - xPM-WC-CPGEN-M - Anthony Tucson-Reorganize parts room. organize siemens parts and controllers. - Anthony Tucson; 2017-03-21 - xPM-WC-CPGEN-M - Donald Miller-Assisted in moving equipment around in basement for floor cleaning and cleaned tool room. Hauled garbage from basement to dumpster - Donald Miller; 2017-03-22 - xPM-WC-CPGEN-M - Joseph McCormick-Cleaned floor in north basement from east wall to 1st concrete pillar. Scouring pad with buffer, mopped until clean. Shop-vac up loose coating / paint chips. - Joseph McCormick; 2017-03-22 - xPM-WC-CPGEN-M - Joseph McCormick-Was in the process of cleaning the last 15' X 20' section of basement floor, whenever I was told that an outside vendor will be in next Wed. to bid on re-coating it. Went ahead and used buffer with scouring pad. Mopped until clean. Shop-vac up loose coating / paint chips. - Joseph McCormick; 2017-03-22 - xPM-WC-CPGEN-M - Donald Miller-Cleaned area around pumps 23 and 24 - Donald Miller; 2017-03-23 - xPM-WC-CPGEN-M - Joseph McCormick-Put away buffer, shop-vac and mop w/ wringer. Moved all of the stuff back into the north end of the basement. Awaiting bid next week for re-surfacing and coating of basement floor. - Joseph McCormick; 2017-03-23 - xPM-WC-CPGEN-M - David Valentine-emptied trash in CB and BSMT, removed "a" frame from sump pump area to storage area. - David Valentine; 2017-03-23 - xPM-WC-CPGEN-M - Donald Miller-Repaired shop tools, cleaned basement, removed trash and disposed of several worthless cabinets - Donald Miller; 2017-03-23 - xPM-WC-CPGEN-M - Ronald Chaffee-Checked batteries on CP golf cart. Added water and put on charger. - Ronald Chaffee; 2017-03-28 - xPM-WC-CPGEN-M - Joseph McCormick-Swept basement floor of loose coating chips in prep for vendor coming to quote the re-surfacing and re-coating of floor. Swept chiller bay and mopped around leaking West Chemical flush pump on #4 condenser. Wiped up grease from pumps. - Joseph McCormick; 2017-03-29 - xPM-WC-CPGEN-M - Chad T Ball-Swept and cleaned up debris and insulation from where we had worked on CLCC1 chilled water valve at tunnel entrance. Removed dirty filters from KIVA mezzanine and took them to the compactor. - Chad T Ball; 2017-03-29 - xPM-WC-CPGEN-M - Joseph McCormick-Cleaned and wiped down pumps 4&amp;17 pumps, motor, piping and baseplates. Did same for chill water sand filter and UV light system. - Joseph McCormick; 2017-03-30 - xPM-WC-CPGEN-M - Joseph McCormick-Continued to wipe down equipment from UV filtration system south to the flat plate heat exchangers. - Joseph McCormick; 2017-03-31 - xPM-WC-CPGEN-M - Randy Randell-sweep and dust chill water pump room studentcenter rec center - Randy Randell; 2017-03-31 - xPM-WC-CPGEN-M - Thomas Wienand-Monthly review - Thomas Wienand | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 15
2017-02-27 | 211349 | RACC-117261 | !! The air conditioning/heating unit is not working. Even though we have a set temperature, it does not filter air throughout our quad. Thanks! 4NO6GJE | NA | !! The air conditioning/heating unit is not working. Even though we have a set temperature, it does not filter air throughout our quad. Thanks! 4NO6GJE NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-27 | 230930 | POLY-117268 | BILLED Coils CHARGE BACK TO UPSI GN7 ACCOUNT (GN7-1203-02) | NA | BILLED Coils CHARGE BACK TO UPSI GN7 ACCOUNT (GN7-1203-02) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-27 | 28445 | TMPE-221712 | condensate pump #1 leaking needs repair | 2017-03-03 - 23100 - Derek Gittings-cleaned and repaid flaot mec,cleaned water off floor. - Derek Gittings | condensate pump #1 leaking needs repair 2017-03-03 - 23100 - Derek Gittings-cleaned and repaid flaot mec,cleaned water off floor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-27 | 28499 | TMPE-221658 | !! Dust collection unit located in the art warehouse courtyard requires an electrical inspection. 42ALH0O | 2017-03-01 - 15000 - Thomas Engebretson-inspected and energized unit, power is ok, a lot of water in unit that needs to be drained. opened disconnect and locked off per John. - Thomas Engebretson; 2017-03-02 - 15000 - Stephen Toro-checked and tested collector / works properly but has water in it that should be removed. we have left it locked and tagged out until the water can be removed by others. - Stephen Toro | !! Dust collection unit located in the art warehouse courtyard requires an electrical inspection. 42ALH0O 2017-03-01 - 15000 - Thomas Engebretson-inspected and energized unit, power is ok, a lot of water in unit that needs to be drained. opened disconnect and locked off per John. - Thomas Engebretson; 2017-03-02 - 15000 - Stephen Toro-checked and tested collector / works properly but has water in it that should be removed. we have left it locked and tagged out until the water can be removed by others. - Stephen Toro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-02-27 | 28500 | TMPE-221657 | air compressor located in the art warehouse courtyard outside of room 108 requires electrical inspection. 42ALH0O | 2017-02-27 - 15000 - Damon Called and stated to cancel the work order the air compressor is working fine now they were able to fix the issue. - Jeri Zappanti | air compressor located in the art warehouse courtyard outside of room 108 requires electrical inspection. 42ALH0O 2017-02-27 - 15000 - Damon Called and stated to cancel the work order the air compressor is working fine now they were able to fix the issue. - Jeri Zappanti | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-27 | 28522 | TMPE-221635 | ERC RM 133 Transferred to HVAC to check humidifier for proper operation, was reset by EMS (humidifier tripped). Art Handugan says its been an ongoing issue. Please contact Art for further details. EMS WO#220237, HVAC WO#221635. Loss of humidity control. Wed=36%, Thurs=29%, Fri (today)= 26%.. . . | 2017-03-03 - 18010 - Zhi Yu-Arrived at ERC Monday about 1:00 o clock. The unit located in above ceiling. We Ck the LCD display malfunction. Will check back. - Zhi Yu; 2017-03-03 - 18010 - Zhi Yu-We hunted down maintenance manual and microprocessor control system manual.; - Zhi Yu; 2017-03-07 - 18010 - Zhi Yu-Got the Service manual. We diagnose the Display has loosen wire. We tighten wire the lcd display comes on. We are able to see all the error and alarm. . Zhi has an emergency and call of the job. - Zhi Yu; 2017-03-07 - 18010 - Michael Kelley-Got the Service manual. We diagnose the Display has loosen wire. We tighten wire the lcd display comes on. We are able to see all the error and alarm. . Zhi has an emergency and call of the job. - Zhi Yu; 2017-03-07 - 18010 - Zhi Yu-Back on the job, pick up some descale cleaner. We call EMS will turn off unit for 1-2 hr. We removed the water sensor probe and descaled and inspect the tank. Is Full of calcium will need too schedule completely shut down for 2 days cleaning and maintenance. Will need to order gasket kit - Zhi Yu; 2017-03-07 - 18010 - Michael Kelley-Back on the job, pick up some descale cleaner. We call EMS will turn off unit for 1-2 hr. We removed the water sensor probe and descaled and inspect the tank. Is Full of calcium will need too schedule completely shut down for 2 days cleaning and maintenance. Will need to order gasket kit - Zhi Yu; 2017-04-04 - 18010 - Zhi Yu-We drain the humidifier, removed the heat element and probe. we trying to removed some scale, it comes off in big piece. we'er only able to removed portion of it, still large amount remain. we have the descale on order. - Zhi Yu; 2017-04-18 - 18010 - Zhi Yu-install 3 heating element, drain valve , water probe , sensor and clean out gasket. - Zhi Yu | ERC RM 133 Transferred to HVAC to check humidifier for proper operation, was reset by EMS (humidifier tripped). Art Handugan says its been an ongoing issue. Please contact Art for further details. EMS WO#220237, HVAC WO#221635. Loss of humidity control. Wed=36%, Thurs=29%, Fri (today)= 26%.. . . 2017-03-03 - 18010 - Zhi Yu-Arrived at ERC Monday about 1:00 o clock. The unit located in above ceiling. We Ck the LCD display malfunction. Will check back. - Zhi Yu; 2017-03-03 - 18010 - Zhi Yu-We hunted down maintenance manual and microprocessor control system manual.; - Zhi Yu; 2017-03-07 - 18010 - Zhi Yu-Got the Service manual. We diagnose the Display has loosen wire. We tighten wire the lcd display comes on. We are able to see all the error and alarm. . Zhi has an emergency and call of the job. - Zhi Yu; 2017-03-07 - 18010 - Michael Kelley-Got the Service manual. We diagnose the Display has loosen wire. We tighten wire the lcd display comes on. We are able to see all the error and alarm. . Zhi has an emergency and call of the job. - Zhi Yu; 2017-03-07 - 18010 - Zhi Yu-Back on the job, pick up some descale cleaner. We call EMS will turn off unit for 1-2 hr. We removed the water sensor probe and descaled and inspect the tank. Is Full of calcium will need too schedule completely shut down for 2 days cleaning and maintenance. Will need to order gasket kit - Zhi Yu; 2017-03-07 - 18010 - Michael Kelley-Back on the job, pick up some descale cleaner. We call EMS will turn off unit for 1-2 hr. We removed the water sensor probe and descaled and inspect the tank. Is Full of calcium will need too schedule completely shut down for 2 days cleaning and maintenance. Will need to order gasket kit - Zhi Yu; 2017-04-04 - 18010 - Zhi Yu-We drain the humidifier, removed the heat element and probe. we trying to removed some scale, it comes off in big piece. we'er only able to removed portion of it, still large amount remain. we have the descale on order. - Zhi Yu; 2017-04-18 - 18010 - Zhi Yu-install 3 heating element, drain valve , water probe , sensor and clean out gasket. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 6
2017-02-27 | 28548 | TMPE-221609 | I just wanted to let you know the door to 135ui is unlocked. I believe it's an HVAC but our key won't lock it. | 2017-03-01 - 11040 - Michael Kelley-stop by talk to front desk. she showed me the problem. Door to Air handler was unlocked . Locked door. complete. called talked to Maurreen - Michael Kelley | I just wanted to let you know the door to 135ui is unlocked. I believe it's an HVAC but our key won't lock it. 2017-03-01 - 11040 - Michael Kelley-stop by talk to front desk. she showed me the problem. Door to Air handler was unlocked . Locked door. complete. called talked to Maurreen - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-02-27 | 28561 | TMPE-221596 | Compressed air system is down. Do not know at this time if the compressor being down is related to the Fire in the Dust Collector at Fine Arts Warehouse on Feb 23. Submitted at John Howell's request. | 2017-02-28 - 18030 - Brian Qualls-Compressor was running upon arrival. Spoke with customer. Nut and bolted starter and fuse block. Checked unit, OK. - Brian Qualls | Compressed air system is down. Do not know at this time if the compressor being down is related to the Fire in the Dust Collector at Fine Arts Warehouse on Feb 23. Submitted at John Howell's request. 2017-02-28 - 18030 - Brian Qualls-Compressor was running upon arrival. Spoke with customer. Nut and bolted starter and fuse block. Checked unit, OK. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2017-02-28 | 167380 | RFMT-140951 | There appears to be a slight separation between the two walls in the upper corner of the room by the A/C unit. It looked like there was dust and lint collecting in the gap so it may be on the other side of the wall as well. Contact Name: Contact Phone Number: 9513232100 Contact Email: 4NF8M98 | 2017-02-28 - 13000 - Chester Duncan-Caulked 1 1/2" crack in 266-1 and 1/2" hole in 266-2 at ceiling/wall joint with M1 Cleared sink - Chester Duncan | There appears to be a slight separation between the two walls in the upper corner of the room by the A/C unit. It looked like there was dust and lint collecting in the gap so it may be on the other side of the wall as well. Contact Name: Contact Phone Number: 9513232100 Contact Email: 4NF8M98 2017-02-28 - 13000 - Chester Duncan-Caulked 1 1/2" crack in 266-1 and 1/2" hole in 266-2 at ceiling/wall joint with M1 Cleared sink - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-02-28 | 167447 | RFMT-140884 | Ac broken won't click on 4O0AECC | 2017-02-28 - 18010 - John Romero-Checked out a/c unit. Motor is working, but the thermostat is not responding...Need to have Simon take a look at this unit. - John Romero | Ac broken won't click on 4O0AECC 2017-02-28 - 18010 - John Romero-Checked out a/c unit. Motor is working, but the thermostat is not responding...Need to have Simon take a look at this unit. - John Romero | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-02-28 | 25433 | TMPE-224724 | Naumann Hobbs found bad batteries and one bad seat belt. replaced batteries secured cables and tested unit. total: 2606.89 | NA | Naumann Hobbs found bad batteries and one bad seat belt. replaced batteries secured cables and tested unit. total: 2606.89 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-28 | 230755 | POLY-117443 | !! -Outback Hose faucet leaking, handle broken -Air Filter Changed. 4NGL9H2 | NA | !! -Outback Hose faucet leaking, handle broken -Air Filter Changed. 4NGL9H2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-02-28 | 28245 | TMPE-221912 | !! Send to HVAC shop. There is a broken belt on the FC Unit L1.1 in this room. This is a server room and is now being cooled by the Daikin backup unit. Please expedite. Thanks. 42C3NC4 | 2017-03-07 - 18010 - Jennifer Moyer-Installed new belt.Job required two people due to 12 ft. ladder use. - Jennifer Moyer; 2017-03-07 - 18010 - Thomas Gibble-Installed new belt.Job required two people due to 12 ft. ladder use. Two co-workers were in the area. - Jennifer Moyer; 2017-03-07 - 18010 - Michael Longtin-Installed new belt.Job required two people due to 12 ft. ladder use. Two co-workers were in the area. - Jennifer Moyer | !! Send to HVAC shop. There is a broken belt on the FC Unit L1.1 in this room. This is a server room and is now being cooled by the Daikin backup unit. Please expedite. Thanks. 42C3NC4 2017-03-07 - 18010 - Jennifer Moyer-Installed new belt.Job required two people due to 12 ft. ladder use. - Jennifer Moyer; 2017-03-07 - 18010 - Thomas Gibble-Installed new belt.Job required two people due to 12 ft. ladder use. Two co-workers were in the area. - Jennifer Moyer; 2017-03-07 - 18010 - Michael Longtin-Installed new belt.Job required two people due to 12 ft. ladder use. Two co-workers were in the area. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-02-28 | 28305 | TMPE-221852 | motor has weak start windings.have trouble restarting exhaust fan. | NA | motor has weak start windings.have trouble restarting exhaust fan. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 167288 | RFMT-141043 | HVAC Semi-Annual | 2017-03-21 - 50016 - Thor Millsaps-PM. Replaced contactor. - Thor Millsaps | HVAC Semi-Annual 2017-03-21 - 50016 - Thor Millsaps-PM. Replaced contactor. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 167353 | RFMT-140978 | !! RL HVAC - Please install a new thermostat in to this unit (224). 4NEI9DN | 2017-03-09 - 18010 - Simon Fernandez-c.a.r. - Simon Fernandez | !! RL HVAC - Please install a new thermostat in to this unit (224). 4NEI9DN 2017-03-09 - 18010 - Simon Fernandez-c.a.r. - Simon Fernandez | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 1642 | WEST-109607 | HVAC-GENERAL-SPLIT-001 | 2017-03-22 - 18010 - Chad T Ball-Inspected unit for proper operation. Found L1,L2 and L3 fuses blown and fan motor locked up and inoperable. Defective motor has been removed. Filters will be changed after floor refinishing project is completed. Unit is currently locked out and tagged out awaiting request for repair. - Chad T Ball | HVAC-GENERAL-SPLIT-001 2017-03-22 - 18010 - Chad T Ball-Inspected unit for proper operation. Found L1,L2 and L3 fuses blown and fan motor locked up and inoperable. Defective motor has been removed. Filters will be changed after floor refinishing project is completed. Unit is currently locked out and tagged out awaiting request for repair. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5
2017-03-01 | 1699 | WEST-109550 | Ice Machine-ICE-001 | 2017-03-31 - 18210 - Chad T Ball-Inspected unit for proper operation. Ice thickness and clarity is acceptable. Inspected bin for cleanliness and signs of mold growth. Inspected water lines and connections, fill and dump valves operating properly. Drain pump operating properly. Inspected condenser filter. Evaporator is not in need of cleaning at this time. - Chad T Ball | Ice Machine-ICE-001 2017-03-31 - 18210 - Chad T Ball-Inspected unit for proper operation. Ice thickness and clarity is acceptable. Inspected bin for cleanliness and signs of mold growth. Inspected water lines and connections, fill and dump valves operating properly. Drain pump operating properly. Inspected condenser filter. Evaporator is not in need of cleaning at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-03-01 | 1745 | WEST-109504 | Air Handler-Biannual-AHU-012 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-012 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1746 | WEST-109503 | Air Handler-Biannual-AHU-011 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-011 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1747 | WEST-109502 | Air Handler-Biannual-AHU-010 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-010 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1748 | WEST-109501 | Semi-Annual-AHU-009 | 2017-03-29 - 50015 - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson | Semi-Annual-AHU-009 2017-03-29 - 50015 - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 1749 | WEST-109500 | Air Handler-Biannual-AHU-008 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-008 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1750 | WEST-109499 | Air Handler-Biannual-AHU-007 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-007 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1751 | WEST-109498 | Air Handler-Biannual-AHU-006 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-006 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 1752 | WEST-109497 | Air Handler-Biannual-AHU-005 | 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | Air Handler-Biannual-AHU-005 2017-03-29 - xPM-0300.03-B - Edward Hendrickson-Removed and disposed of dirty filters. Inspected evap coil for problems. Installed new filters. - Edward Hendrickson; 2017-03-31 - xPM-0300.03-B - Chad T Ball-Inspected unit for proper operation. Inspected fan belts for wear and proper operation. Exercised isolation valves. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-01 | 211282 | RACC-117328 | !! !!A/C unit broken for the past few days. room is getting hot, please assist. Submitted by 4N80G0G | NA | !! !!A/C unit broken for the past few days. room is getting hot, please assist. Submitted by 4N80G0G NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-01 | 230741 | POLY-117457 | SERVICE A/C EQUIPMENT 4O216EO | 2017-03-22 - 18010 - Allan Blair-serviced units - found 1 with a bad compressor - need to replace - Steve Clark; 2017-03-22 - 18010 - Darusman Amin-serviced units - found 1 with a bad compressor - need to replace - Steve Clark; 2017-03-22 - 18010 - Allan Blair-replaced compressor - checked operation - Steve Clark; 2017-03-22 - 18010 - Allan Blair-replaced compressor - checked operation - Steve Clark | SERVICE A/C EQUIPMENT 4O216EO 2017-03-22 - 18010 - Allan Blair-serviced units - found 1 with a bad compressor - need to replace - Steve Clark; 2017-03-22 - 18010 - Darusman Amin-serviced units - found 1 with a bad compressor - need to replace - Steve Clark; 2017-03-22 - 18010 - Allan Blair-replaced compressor - checked operation - Steve Clark; 2017-03-22 - 18010 - Allan Blair-replaced compressor - checked operation - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 25899 | TMPE-224258 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25900 | TMPE-224257 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25901 | TMPE-224256 | Sidewalk condition and safety check-Monthly | 2017-03-16 - xPM-SWC-M - Bruno Lara-Complete Performed monthly inspection of the sidewalks. Found several areas that require repairs. See attached pix. 1.25 Materials - none - Bruno Lara | Sidewalk condition and safety check-Monthly 2017-03-16 - xPM-SWC-M - Bruno Lara-Complete Performed monthly inspection of the sidewalks. Found several areas that require repairs. See attached pix. 1.25 Materials - none - Bruno Lara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25902 | TMPE-224255 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25903 | TMPE-224254 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25904 | TMPE-224253 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25905 | TMPE-224252 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25906 | TMPE-224251 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25907 | TMPE-224250 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25908 | TMPE-224249 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25909 | TMPE-224248 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25910 | TMPE-224247 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25911 | TMPE-224246 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 25913 | TMPE-224244 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 28123 | TMPE-222034 | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. | 2017-03-06 - 10090 - Gail Jackson-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Thomas Gibble-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Carl Karr-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Gail Jackson-Ohm out motor, check voltage, meg winding, test run, belts ok, motor check ok, complete - Gail Jackson; 2017-03-06 - 10090 - Thomas Gibble-Ohm out motor, check voltage, meg winding, test run, belts ok, motor check ok, complete - Gail Jackson; 2017-03-29 - 10090 - Thomas Gibble-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble; 2017-03-29 - 10090 - Gail Jackson-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble; 2017-03-29 - 10090 - Carl Karr-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. 2017-03-06 - 10090 - Gail Jackson-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Thomas Gibble-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Carl Karr-found fan housing full of water, needs to be pumped out to test motor, worker must tie off on ledge, pumped out - Gail Jackson; 2017-03-06 - 10090 - Gail Jackson-Ohm out motor, check voltage, meg winding, test run, belts ok, motor check ok, complete - Gail Jackson; 2017-03-06 - 10090 - Thomas Gibble-Ohm out motor, check voltage, meg winding, test run, belts ok, motor check ok, complete - Gail Jackson; 2017-03-29 - 10090 - Thomas Gibble-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble; 2017-03-29 - 10090 - Gail Jackson-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble; 2017-03-29 - 10090 - Carl Karr-repaired doors and gaskets. painted a little on the burnt areas. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-01 | 28124 | TMPE-222033 | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. | NA | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 28125 | TMPE-222032 | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. | NA | **Insurance Claim** Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 28126 | TMPE-222031 | **Insurance Claim** Build back repair Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. | NA | **Insurance Claim** Build back repair Art Warehouse: Fire started inside dust collection system in the Art Warehouse. Fire department personnel that responded to fire indicated that it might have been a mechanical failure inside the motor that started the fire. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 28225 | TMPE-221932 | \\u201cDistribute and install portable pumps at known locations all over campus to remove excess rain water.\\u201d \\u201cRemove pumps when rain stops and return to HVAC Shop.\\u201d Please assign to: Mike Kelley Midhat Mukonovich | 2017-03-03 - 23100 - Michael Kelley-cleaned out sump pumps around campus. checked all problem areas for flooding. Put out pumps in areas we know of. Music orgiastic pit. Fine arts PV west Rechecked after lunch. found problems at dixie gammage - Michael Kelley; 2017-03-03 - 23100 - Midhat Mukanovic-cleaned out sump pumps around campus. checked all problem areas for flooding. Put out pumps in areas we know of. Music orgiastic pit. Fine arts PV west Rechecked after lunch. found problems at dixie gammage - Michael Kelley; 2017-03-03 - 23100 - Michael Kelley-picked up pumps Music orgiastic pit. Fine arts PV west - Michael Kelley | \\u201cDistribute and install portable pumps at known locations all over campus to remove excess rain water.\\u201d \\u201cRemove pumps when rain stops and return to HVAC Shop.\\u201d Please assign to: Mike Kelley Midhat Mukonovich 2017-03-03 - 23100 - Michael Kelley-cleaned out sump pumps around campus. checked all problem areas for flooding. Put out pumps in areas we know of. Music orgiastic pit. Fine arts PV west Rechecked after lunch. found problems at dixie gammage - Michael Kelley; 2017-03-03 - 23100 - Midhat Mukanovic-cleaned out sump pumps around campus. checked all problem areas for flooding. Put out pumps in areas we know of. Music orgiastic pit. Fine arts PV west Rechecked after lunch. found problems at dixie gammage - Michael Kelley; 2017-03-03 - 23100 - Michael Kelley-picked up pumps Music orgiastic pit. Fine arts PV west - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 248234 | MUFT-100520 | replace motor on cooler for engrained make up air | 2017-03-14 - 15000 - Michael Landrith-done - Michael Landrith | replace motor on cooler for engrained make up air 2017-03-14 - 15000 - Michael Landrith-done - Michael Landrith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-01 | 29300 | TMPE-220857 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 29307 | TMPE-220850 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 29308 | TMPE-220849 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 250926 | DTPC-117612 | Repair the furniture dollies for the portable judges stage. | 2017-03-05 - 10010 - Thomas Klein-Added brackets and new wheels for dollies. - Thomas Klein | Repair the furniture dollies for the portable judges stage. 2017-03-05 - 10010 - Thomas Klein-Added brackets and new wheels for dollies. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-01 | 251031 | DTPC-117507 | Air Compressor | 2017-03-07 - 18030 - James Hermann-Created PM sheet for air compressor maintenance and perform the bi-annual maintenance service for the air compressor. All readings and information are on the pm sheet. - Keith Griffin | Air Compressor 2017-03-07 - 18030 - James Hermann-Created PM sheet for air compressor maintenance and perform the bi-annual maintenance service for the air compressor. All readings and information are on the pm sheet. - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 251087 | DTPC-117451 | DX Equipment-Biannual | 2017-03-15 - xPM-1700-B - Steve Skibbe-testing why unit has display Waring of compressor over load found condenser not working right Stephan to call dago back - Steve Skibbe; 2017-03-16 - xPM-1700-B - Steve Skibbe-bi annual pm preformed - Steve Skibbe; 2017-03-16 - xPM-1700-B - Larry Smith-bi annual pm preformed - Steve Skibbe | DX Equipment-Biannual 2017-03-15 - xPM-1700-B - Steve Skibbe-testing why unit has display Waring of compressor over load found condenser not working right Stephan to call dago back - Steve Skibbe; 2017-03-16 - xPM-1700-B - Steve Skibbe-bi annual pm preformed - Steve Skibbe; 2017-03-16 - xPM-1700-B - Larry Smith-bi annual pm preformed - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 251088 | DTPC-117450 | DX Equipment-Biannual | 2017-03-15 - xPM-1700-B - Steve Skibbe-found the unit tripping on compressor overload checked out condenser found not operating correctly possibly fan speed controller Stephen to call drago back out as they did the pm a month ago and unit has not run since - Steve Skibbe; 2017-03-15 - xPM-1700-B - James Hermann-found the unit tripping on compressor overload checked out condenser found not operating correctly possibly fan speed controller Stephen to call drago back out as they did the pm a month ago and unit has not run since - Steve Skibbe; 2017-03-21 - xPM-1700-B - Steve Skibbe-annual pm preformed - Steve Skibbe | DX Equipment-Biannual 2017-03-15 - xPM-1700-B - Steve Skibbe-found the unit tripping on compressor overload checked out condenser found not operating correctly possibly fan speed controller Stephen to call drago back out as they did the pm a month ago and unit has not run since - Steve Skibbe; 2017-03-15 - xPM-1700-B - James Hermann-found the unit tripping on compressor overload checked out condenser found not operating correctly possibly fan speed controller Stephen to call drago back out as they did the pm a month ago and unit has not run since - Steve Skibbe; 2017-03-21 - xPM-1700-B - Steve Skibbe-annual pm preformed - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-01 | 251163 | DTPC-117375 | Exhaust Fan | 2017-03-22 - 18160 - Jose Acero-took bearings and shaft out getting new parts to rebuild it - Jose Acero; 2017-03-28 - 18160 - Jose Acero-removed the rest of the parts on Exhaust fan# 12 - Jose Acero; 2017-03-28 - 18160 - Bruce Pickford-removed the rest of the parts on Exhaust fan# 12 - Jose Acero; 2017-03-31 - 18160 - Jose Acero-Installed Pulleys on motor and Shaft - Jose Acero | Exhaust Fan 2017-03-22 - 18160 - Jose Acero-took bearings and shaft out getting new parts to rebuild it - Jose Acero; 2017-03-28 - 18160 - Jose Acero-removed the rest of the parts on Exhaust fan# 12 - Jose Acero; 2017-03-28 - 18160 - Bruce Pickford-removed the rest of the parts on Exhaust fan# 12 - Jose Acero; 2017-03-31 - 18160 - Jose Acero-Installed Pulleys on motor and Shaft - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 29578 | TMPE-220579 | Vehicle Inspection-Monthly | 2017-03-09 - xPM-VEH-M - Gail Jackson-Wash exterior and interior, check all fluids, lights, seat belts. BACK UP ALARM DOES NOT WORK, SAFETY ISSUE. - Gail Jackson | Vehicle Inspection-Monthly 2017-03-09 - xPM-VEH-M - Gail Jackson-Wash exterior and interior, check all fluids, lights, seat belts. BACK UP ALARM DOES NOT WORK, SAFETY ISSUE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-01 | 29580 | TMPE-220577 | Vehicle Inspection-Monthly | 2017-03-31 - xPM-VEH-M - David Brady-Completed the check list and had the mechanic change the tire for the spare. The tires need checking and possible replacing. The "Check Engine" light is on and the AC is not cooling. Relayed this information to Warren and Robert for repair - David Brady | Vehicle Inspection-Monthly 2017-03-31 - xPM-VEH-M - David Brady-Completed the check list and had the mechanic change the tire for the spare. The tires need checking and possible replacing. The "Check Engine" light is on and the AC is not cooling. Relayed this information to Warren and Robert for repair - David Brady | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 167059 | RFMT-141272 | HAV Public Areas- Maintenance | 2017-03-10 - 50024 - Casey Faultner-Inspected Laundry and found a burnt out blower motor. Removed,cleaned housing and replaced blower motor and Run Cap. Used 1 HC/00209 Blower Motor (Long Shaft) and a HC/00090 Run Cap - Casey Faultner | HAV Public Areas- Maintenance 2017-03-10 - 50024 - Casey Faultner-Inspected Laundry and found a burnt out blower motor. Removed,cleaned housing and replaced blower motor and Run Cap. Used 1 HC/00209 Blower Motor (Long Shaft) and a HC/00090 Run Cap - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-02 | 167083 | RFMT-141248 | HAV Public Areas- Maintenance | 2017-03-07 - 50024 - Scott Berndt-paint/patch by whiteboard range hood needs motor and wires - Scott Berndt; 2017-03-07 - 50024 - Chester Duncan-paint/patch by whiteboard range hood needs motor and wires - Scott Berndt | HAV Public Areas- Maintenance 2017-03-07 - 50024 - Scott Berndt-paint/patch by whiteboard range hood needs motor and wires - Scott Berndt; 2017-03-07 - 50024 - Chester Duncan-paint/patch by whiteboard range hood needs motor and wires - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-02 | 167085 | RFMT-141246 | HAV Public Areas- Maintenance | 2017-03-09 - 50024 - Casey Faultner-Turned room and found a bad washer supply line that needed to be replaced. Replaced the supply line. - Casey Faultner | HAV Public Areas- Maintenance 2017-03-09 - 50024 - Casey Faultner-Turned room and found a bad washer supply line that needed to be replaced. Replaced the supply line. - Casey Faultner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 167121 | RFMT-141210 | Center Public Areas- Maintenance | 2017-03-08 - 50011 - Salvatore Marasco Jr-Checked A/C unit and adjusted all window blinds. - Salvatore Marasco Jr | Center Public Areas- Maintenance 2017-03-08 - 50011 - Salvatore Marasco Jr-Checked A/C unit and adjusted all window blinds. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 167123 | RFMT-141208 | Center Public Areas- Maintenance | 2017-03-23 - 50011 - Salvatore Marasco Jr--Checked window blinds, automatic doors, TVs, furniture, flooring, lighting, and A/C units. - Salvatore Marasco Jr | Center Public Areas- Maintenance 2017-03-23 - 50011 - Salvatore Marasco Jr--Checked window blinds, automatic doors, TVs, furniture, flooring, lighting, and A/C units. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 167134 | RFMT-141197 | Center Public Areas- Maintenance | 2017-03-10 - 50011 - Salvatore Marasco Jr--Adjusted all window blinds -Checked all electrical outlets -Checked A/C unit - Salvatore Marasco Jr | Center Public Areas- Maintenance 2017-03-10 - 50011 - Salvatore Marasco Jr--Adjusted all window blinds -Checked all electrical outlets -Checked A/C unit - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 211273 | RACC-117337 | !! Bathroom light went out. Air conditioning filter was never replaced (?) 4NJA9JG | NA | !! Bathroom light went out. Air conditioning filter was never replaced (?) 4NJA9JG NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-02 | 28011 | TMPE-222146 | ERC B23 transfer--Please add the electrical shop to HVAC work order# 217657. Replace 115v receptacle for refrigerated air dryer. Brian Qualls HVAC contact for details. Located in the B/M pump room. The Hankinson refrigerated control air dryer has been disabled and bypassed and so is not removi. . . | NA | ERC B23 transfer--Please add the electrical shop to HVAC work order# 217657. Replace 115v receptacle for refrigerated air dryer. Brian Qualls HVAC contact for details. Located in the B/M pump room. The Hankinson refrigerated control air dryer has been disabled and bypassed and so is not removi. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-03 | 1511 | WEST-109738 | Pump is not running. Please troubleshoot. | 2017-03-03 - 23100 - Chad T Ball-Performed troubleshooting. VFD would shut off on overload. Isolated pump from motor and found pump to be the problem. Removed pump and brought it back to the shop. Determined that we had an interference problem causing excessive friction during rotation. Was able to use the hydraulic press to push the impeller on the shaft approximately .005". Cut a new gasket and re-assembled pump. Ran and tested for proper operation. - Chad T Ball | Pump is not running. Please troubleshoot. 2017-03-03 - 23100 - Chad T Ball-Performed troubleshooting. VFD would shut off on overload. Isolated pump from motor and found pump to be the problem. Removed pump and brought it back to the shop. Determined that we had an interference problem causing excessive friction during rotation. Was able to use the hydraulic press to push the impeller on the shaft approximately .005". Cut a new gasket and re-assembled pump. Ran and tested for proper operation. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 166933 | RFMT-141398 | !! Drain in bathtub is running very slowly - drain cleaning. Replace air filters, air vents are very dirty. Contact Name: Contact Phone Number: 5866122012 Contact Email: 4NJ213D | 2017-03-03 - 18170 - Joe Swan-removed hair from drain working now - Joe Swan | !! Drain in bathtub is running very slowly - drain cleaning. Replace air filters, air vents are very dirty. Contact Name: Contact Phone Number: 5866122012 Contact Email: 4NJ213D 2017-03-03 - 18170 - Joe Swan-removed hair from drain working now - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 166957 | RFMT-141374 | Please replace the vent fan motor number 7831 at San Pablo | 2017-03-03 - 18230 - Thor Millsaps-Replaced exhaust fan motor. Fan up and running. - Thor Millsaps | Please replace the vent fan motor number 7831 at San Pablo 2017-03-03 - 18230 - Thor Millsaps-Replaced exhaust fan motor. Fan up and running. - Thor Millsaps | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-03 | 166958 | RFMT-141373 | Please replace the thermostat in room 308 at McClintock | 2017-03-07 - 18010 - Thor Millsaps-Replaced thermostat and checked blower plug. System up and running. - Thor Millsaps | Please replace the thermostat in room 308 at McClintock 2017-03-07 - 18010 - Thor Millsaps-Replaced thermostat and checked blower plug. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-03 | 211239 | RACC-117371 | !! !!A/C is not working- please assist Called to maintenance Submitted by 4N80G0G | 2017-03-13 - 10010 - replaced fuse - Jim Deal | !! !!A/C is not working- please assist Called to maintenance Submitted by 4N80G0G 2017-03-13 - 10010 - replaced fuse - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 26967 | TMPE-223190 | for HVAC: Provide estimate to add dampers to air conditioning system in EH&S offices, conduct air balance and adjust HVAC system such that heaters and air conditioners work together vs. at the same time. Some areas experience AC running all day long even in winter while the heater runs with adjac. . . | 2017-03-10 - 18010 - Carl Karr-Verify that dampers are present. - Carl Karr; 2017-03-21 - 18010 - Carl Karr-Balance air. - Carl Karr; 2017-03-27 - 18010 - Mitchell Andrews-rebalanced the area of unit 3 and offices surrounding areas - Mitchell Andrews | for HVAC: Provide estimate to add dampers to air conditioning system in EH&S offices, conduct air balance and adjust HVAC system such that heaters and air conditioners work together vs. at the same time. Some areas experience AC running all day long even in winter while the heater runs with adjac. . . 2017-03-10 - 18010 - Carl Karr-Verify that dampers are present. - Carl Karr; 2017-03-21 - 18010 - Carl Karr-Balance air. - Carl Karr; 2017-03-27 - 18010 - Mitchell Andrews-rebalanced the area of unit 3 and offices surrounding areas - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 27771 | TMPE-222386 | ECD 113 The chemical fume hood in ECD 113 was tagged "Out of Service" by EH&S on 1/26/17. I just checked on the roof and the blower motor is running but no exhaust is taking place. The unit number is 2942, and it appears to be direct drive. Please repair ASAP. 42B3D6J | 2017-03-31 - 18190 - Thomas Gibble-ex-fan motor was running backwards - Thomas Gibble | ECD 113 The chemical fume hood in ECD 113 was tagged "Out of Service" by EH&S on 1/26/17. I just checked on the roof and the blower motor is running but no exhaust is taking place. The unit number is 2942, and it appears to be direct drive. Please repair ASAP. 42B3D6J 2017-03-31 - 18190 - Thomas Gibble-ex-fan motor was running backwards - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3
2017-03-03 | 27781 | TMPE-222376 | SPECIAL FUNDING: replace water source heat pumps | 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Checked work done by Pueblo and Sat. April 1. Fans were on ON not AUTO. Everything seemed good - Michael Kelley; 2017-05-05 - 23100 - Michael Kelley-checked on job - Michael Kelley | SPECIAL FUNDING: replace water source heat pumps 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Checked work done by Pueblo and Sat. April 1. Fans were on ON not AUTO. Everything seemed good - Michael Kelley; 2017-05-05 - 23100 - Michael Kelley-checked on job - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-03 | 27782 | TMPE-222375 | SPECIAL FUNDING: replace water source heat pumps | 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Checked work done by Pueblo and Sat. April 1. Fans were on ON not AUTO. Everything seemed good - Michael Kelley | SPECIAL FUNDING: replace water source heat pumps 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-Checked work done by Pueblo and Sat. April 1. Fans were on ON not AUTO. Everything seemed good - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-03 | 27783 | TMPE-222374 | SPECIAL FUNDING: replace water source heat pumps | 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley | SPECIAL FUNDING: replace water source heat pumps 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-04-03 - 23100 - Michael Kelley-checked job with Angel from Pueblo Mechanical. Found smoke detector near unit. Will need Fire techs on work order. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 27791 | TMPE-222366 | SPECIAL FUNDING: replace water source heat pumps | 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-05-05 - 23100 - Michael Kelley-checked out job. customer very happy with job - Michael Kelley | SPECIAL FUNDING: replace water source heat pumps 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oner and John assisted with walk threw. - Michael Kelley; 2017-05-05 - 23100 - Michael Kelley-checked out job. customer very happy with job - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-03 | 27792 | TMPE-222365 | SPECIAL FUNDING: replace water source heat pumps | 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oneaer and John assisted with walk threw. - Michael Kelley | SPECIAL FUNDING: replace water source heat pumps 2017-03-22 - 23100 - Michael Kelley-Checked job with Andy Lester. Oneaer and John assisted with walk threw. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-03 | 27795 | TMPE-222362 | WGTF !! Repeat Request. Previous WO 217457 shows finished in the system. However, the AC continues to blow hot air in the Gymnastics facility. Please repair ASAP. PO is YG202004934. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42. . . | 2017-03-13 - 18290 - Robert Dauscher-checked units 1&amp;2. found filters plugged with chalk dust. filters dated 12-15-16. Recommend having filters changed sooner than current schedule. only lasted 2.5 months - Robert Dauscher | WGTF !! Repeat Request. Previous WO 217457 shows finished in the system. However, the AC continues to blow hot air in the Gymnastics facility. Please repair ASAP. PO is YG202004934. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42. . . 2017-03-13 - 18290 - Robert Dauscher-checked units 1&amp;2. found filters plugged with chalk dust. filters dated 12-15-16. Recommend having filters changed sooner than current schedule. only lasted 2.5 months - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 27812 | TMPE-222345 | sump pump not working needs repair (lower level EQ room Murdock lecture hall) | 2017-03-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 23100 - Jose Lopez-remove non working pump,install,re pipe new pump,adjust float .working @ this time. - Jose Lopez | sump pump not working needs repair (lower level EQ room Murdock lecture hall) 2017-03-23 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 23100 - Jose Lopez-remove non working pump,install,re pipe new pump,adjust float .working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-03 | 27852 | TMPE-222305 | !! Please turn the AC or fan on in this area. The work being done in the rooms across the hallway are creating fumes that are building up in the area. The air circulating should help. Thank you. Contact Name: Robert Booher Contact Phone Number: Contact Email: robert.j.booher@asu.edu 4NIL16N | 2017-03-10 - 18010 - Robert Dauscher-Found area under construction. Fumes were from carpet glue. workers had installed fans on Friday to help with smell. All ok now. call complete - Robert Dauscher | !! Please turn the AC or fan on in this area. The work being done in the rooms across the hallway are creating fumes that are building up in the area. The air circulating should help. Thank you. Contact Name: Robert Booher Contact Phone Number: Contact Email: robert.j.booher@asu.edu 4NIL16N 2017-03-10 - 18010 - Robert Dauscher-Found area under construction. Fumes were from carpet glue. workers had installed fans on Friday to help with smell. All ok now. call complete - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-05 | 166887 | RFMT-141444 | The resident reports that the AC is not working properly within the room. 4NOEA84 | 2017-03-06 - 18010 - Thomas Zambrano-problem with chiller program. central plant forced on chillers. - Thomas Zambrano | The resident reports that the AC is not working properly within the room. 4NOEA84 2017-03-06 - 18010 - Thomas Zambrano-problem with chiller program. central plant forced on chillers. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-05 | 166888 | RFMT-141443 | The resident reports that the AC is not working properly within the room. 4NOEA84 | 2017-03-08 - 18010 - Thomas Zambrano-troubleshoot ac. the chillers were off all weekend, call Tony and he had central plant turn on. - Thomas Zambrano; 2017-03-08 - 18010 - Thomas Zambrano-replaced motor, motor mounts and cleaned coil due to low air flo. - Thomas Zambrano | The resident reports that the AC is not working properly within the room. 4NOEA84 2017-03-08 - 18010 - Thomas Zambrano-troubleshoot ac. the chillers were off all weekend, call Tony and he had central plant turn on. - Thomas Zambrano; 2017-03-08 - 18010 - Thomas Zambrano-replaced motor, motor mounts and cleaned coil due to low air flo. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-05 | 166891 | RFMT-141440 | Air conditioning is not blowing out any air even though it is turned to high 4O10HDC | 2017-03-06 - 18010 - Thomas Zambrano-having issues with program from central plant. they manually forced on chillers. the cooling is working for now. - Thomas Zambrano | Air conditioning is not blowing out any air even though it is turned to high 4O10HDC 2017-03-06 - 18010 - Thomas Zambrano-having issues with program from central plant. they manually forced on chillers. the cooling is working for now. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-06 | 230648 | POLY-117550 | Furnace not working | NA | Furnace not working NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-06 | 27159 | TMPE-222998 | LAW 20 ELECTRICAL-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC | 2017-03-28 - 15000 - Wilford Brown-Disconnected power and pulled wires out of MCC, made safe from mishaps. - Wilford Brown | LAW 20 ELECTRICAL-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC 2017-03-28 - 15000 - Wilford Brown-Disconnected power and pulled wires out of MCC, made safe from mishaps. - Wilford Brown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-06 | 27163 | TMPE-222994 | LAW 20 CARPENTRY-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC | 2017-04-06 - 13000 - Fabian Ortiz-walk job with gym,make material list - Fabian Ortiz; 2017-04-10 - 13000 - Fabian Ortiz-load job,build ramp,clean up job - Fabian Ortiz | LAW 20 CARPENTRY-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC 2017-04-06 - 13000 - Fabian Ortiz-walk job with gym,make material list - Fabian Ortiz; 2017-04-10 - 13000 - Fabian Ortiz-load job,build ramp,clean up job - Fabian Ortiz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-06 | 27166 | TMPE-222991 | LAW 20 HVAC-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC | 2017-03-10 - 18030 - Derek Gittings-removing compressor from building. - Derek Gittings; 2017-03-17 - 18030 - Derek Gittings-removing compressor out. - Derek Gittings; 2017-03-21 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-03-23 - 18030 - Derek Gittings-removing compressor from basement. - Derek Gittings; 2017-03-29 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-04-06 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-04-11 - 18030 - Derek Gittings-removing compressor out of basement - Derek Gittings; 2017-04-13 - 18030 - Derek Gittings-removing compressor out of basement. - Derek Gittings; 2017-04-20 - 18030 - Derek Gittings-removed compressor,back to shop. - Derek Gittings | LAW 20 HVAC-Remove Ingersoll/Rand control air compressor from building. Carpentry to build ramp, Electrical to remove and terminate power at MCC. HVAC,Carpentry and Electrical shops. Contact: Brian HVAC 2017-03-10 - 18030 - Derek Gittings-removing compressor from building. - Derek Gittings; 2017-03-17 - 18030 - Derek Gittings-removing compressor out. - Derek Gittings; 2017-03-21 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-03-23 - 18030 - Derek Gittings-removing compressor from basement. - Derek Gittings; 2017-03-29 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-04-06 - 18030 - Derek Gittings-removing compressor. - Derek Gittings; 2017-04-11 - 18030 - Derek Gittings-removing compressor out of basement - Derek Gittings; 2017-04-13 - 18030 - Derek Gittings-removing compressor out of basement. - Derek Gittings; 2017-04-20 - 18030 - Derek Gittings-removed compressor,back to shop. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-06 | 27189 | TMPE-222968 | !! ECD room 113 has no exhaust for their fume hood. Please create a MWO for HVAC to troubleshoot the fume hood exhaust fan AND install a manual flow control output damper at the fume hood for fpm control. Contact EMS when job is complete so the proper fpm can be adjusted. Then retested and recerti. . . | 2017-03-31 - 18190 - Thomas Gibble-ex-fan motor was running backwards. - Thomas Gibble; 2017-03-31 - 18190 - Gail Jackson-ex-fan motor was running backwards. - Thomas Gibble | !! ECD room 113 has no exhaust for their fume hood. Please create a MWO for HVAC to troubleshoot the fume hood exhaust fan AND install a manual flow control output damper at the fume hood for fpm control. Contact EMS when job is complete so the proper fpm can be adjusted. Then retested and recerti. . . 2017-03-31 - 18190 - Thomas Gibble-ex-fan motor was running backwards. - Thomas Gibble; 2017-03-31 - 18190 - Gail Jackson-ex-fan motor was running backwards. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-07 | 166713 | RFMT-141618 | Water cooler is leaking from hot water spigot. If possible, please repair. Thanks! Attachment(s) 4O3KD62 | 2017-03-08 - 23080 - Chester Duncan-A replacement cooler has been ordered - Chester Duncan | Water cooler is leaking from hot water spigot. If possible, please repair. Thanks! Attachment(s) 4O3KD62 2017-03-08 - 23080 - Chester Duncan-A replacement cooler has been ordered - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-07 | 26951 | TMPE-223206 | bad motor on ef on roof hp:3/4 fr:56h rpm:1725 volts:115-208-230 | 2017-03-24 - 18160 - Thomas Gibble-replaced motor and motor sheave. picked up parts at grainger - Thomas Gibble; 2017-03-24 - 18160 - Gail Jackson-replaced motor and motor sheave. picked up parts at grainger - Thomas Gibble | bad motor on ef on roof hp:3/4 fr:56h rpm:1725 volts:115-208-230 2017-03-24 - 18160 - Thomas Gibble-replaced motor and motor sheave. picked up parts at grainger - Thomas Gibble; 2017-03-24 - 18160 - Gail Jackson-replaced motor and motor sheave. picked up parts at grainger - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-07 | 26985 | TMPE-223172 | !! URGENT!! It is reported, "ISTB-1 room 385 Details: Dr. Liebig's -30 degs C freezer, a SoLow Model No. CH40-13, Serial No. 0607258 has stopped working." Please inspect and service at the earliest opportunity. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warran. . . | 2017-03-10 - 18180 - Zhi Yu-Arrived the -40c freezer was unplug. We plug-in compressor not stating, check solid state relay bad. We removed compressor thermal ohm out ok. We call around and located one at grainger. We install the relay and freezer runes normally condition. - Zhi Yu; 2017-03-13 - 18180 - Zhi Yu-The freezer is maintaining -30c. - Zhi Yu | !! URGENT!! It is reported, "ISTB-1 room 385 Details: Dr. Liebig's -30 degs C freezer, a SoLow Model No. CH40-13, Serial No. 0607258 has stopped working." Please inspect and service at the earliest opportunity. Charges up to $250.00 may be billed to PO #LM502001099. Additional charges will warran. . . 2017-03-10 - 18180 - Zhi Yu-Arrived the -40c freezer was unplug. We plug-in compressor not stating, check solid state relay bad. We removed compressor thermal ohm out ok. We call around and located one at grainger. We install the relay and freezer runes normally condition. - Zhi Yu; 2017-03-13 - 18180 - Zhi Yu-The freezer is maintaining -30c. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-07 | 27012 | TMPE-223145 | Four Swamp-Coolers need annual maintenance and service before it gets hot. (See last years request) 4O190HG | 2017-03-07 - 18100 - Emailed customer for PO - Jeri Zappanti; 2017-03-27 - 18100 - Michael Longtin-complete. drained, and cleaned all coolers. Checked all belts hoses, and pumps. Removed and cleaned all pads. all coolers and pumps are running. Had to replace both pumps on cooler #4. We will need to replace all pads next year. - Michael Longtin | Four Swamp-Coolers need annual maintenance and service before it gets hot. (See last years request) 4O190HG 2017-03-07 - 18100 - Emailed customer for PO - Jeri Zappanti; 2017-03-27 - 18100 - Michael Longtin-complete. drained, and cleaned all coolers. Checked all belts hoses, and pumps. Removed and cleaned all pads. all coolers and pumps are running. Had to replace both pumps on cooler #4. We will need to replace all pads next year. - Michael Longtin | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-07 | 27016 | TMPE-223141 | Seems like a motor from an AC or something is going out in the ceiling in the hallway outside Ryan Oliphant's Office - USB 1152 and above Tracy Brown's cubicle - USB 1150C. With the temperature starting to go up, Financial Services would like to have FACMAN take a look to ensure the AC doesn't go o. . . | NA | Seems like a motor from an AC or something is going out in the ceiling in the hallway outside Ryan Oliphant's Office - USB 1152 and above Tracy Brown's cubicle - USB 1150C. With the temperature starting to go up, Financial Services would like to have FACMAN take a look to ensure the AC doesn't go o. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-08 | 26731 | TMPE-223426 | CWDN 224, 225 FOR MECHANICAL SHOP - THE CHILLED WATER PUMP IS BAD. ELECTRIC WILL BE CHECKING TO SEE IF THE MOTOR IS BAD FIRST. ***ORIGINAL REQUEST***The heat is on, very hot in both of these suites. Please adjust asap, thank you! | 2017-03-30 - 23100 - Derek Gittings-moter is good. - Derek Gittings | CWDN 224, 225 FOR MECHANICAL SHOP - THE CHILLED WATER PUMP IS BAD. ELECTRIC WILL BE CHECKING TO SEE IF THE MOTOR IS BAD FIRST. ***ORIGINAL REQUEST***The heat is on, very hot in both of these suites. Please adjust asap, thank you! 2017-03-30 - 23100 - Derek Gittings-moter is good. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-08 | 26764 | TMPE-223393 | noisy shaft bearings E.F #1937 located on roof | 2017-03-14 - 18160 - Gail Jackson-Found unit on SW corner of roof, bearings bad, recorded type. Trip to warehouse for bearings; not in stock, trip to Kaman; not in stock, trip to Brg, Belt and Chain; in stock. Also new motor sheave; old 1 worn out. Will install at latter date. - Gail Jackson; 2017-03-14 - 18160 - Thomas Gibble-Found unit on SW corner of roof, bearings bad, recorded type. Trip to warehouse for bearings; not in stock, trip to Kaman; not in stock, trip to Brg, Belt and Chain; in stock. Also new motor sheave; old 1 worn out. Will install at latter date. - Gail Jackson; 2017-03-27 - 18160 - Gail Jackson-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson; 2017-03-27 - 18160 - Robert Dauscher-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson; 2017-03-27 - 18160 - Thomas Gibble-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson | noisy shaft bearings E.F #1937 located on roof 2017-03-14 - 18160 - Gail Jackson-Found unit on SW corner of roof, bearings bad, recorded type. Trip to warehouse for bearings; not in stock, trip to Kaman; not in stock, trip to Brg, Belt and Chain; in stock. Also new motor sheave; old 1 worn out. Will install at latter date. - Gail Jackson; 2017-03-14 - 18160 - Thomas Gibble-Found unit on SW corner of roof, bearings bad, recorded type. Trip to warehouse for bearings; not in stock, trip to Kaman; not in stock, trip to Brg, Belt and Chain; in stock. Also new motor sheave; old 1 worn out. Will install at latter date. - Gail Jackson; 2017-03-27 - 18160 - Gail Jackson-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson; 2017-03-27 - 18160 - Robert Dauscher-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson; 2017-03-27 - 18160 - Thomas Gibble-Replace shaft bearings and motor pulley. Sand shaft; badly rusted. Trip to shop to put together puller to reach bearings. Install parts , run test , check amps COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-08 | 26766 | TMPE-223391 | ECB 151 Please adjust the temperature asap!! It's 89 degrees and I just can't work like this. I had the same issue last week. | 2017-03-10 - 18290 - Gail Jackson-Found B151 very hot, talked with CORE Contractor "said roof off limits; in process of replacing roof and A/H systems". Asked if we had spot cooler they could rent/barrow it was they caused heat, talked with Steve took spot cooler over, set in office will notify Jennifer. - Gail Jackson; 2017-03-10 - 18290 - Carl Karr-Found B151 very hot, talked with CORE Contractor "said roof off limits; in process of replacing roof and A/H systems". Asked if we had spot cooler they could rent/barrow it was they caused heat, talked with Steve took spot cooler over, set in office will notify Jennifer. - Gail Jackson; 2017-04-11 - 18290 - Gail Jackson-Remove spot cooler from EngB151 and return to shop. - Gail Jackson; 2017-04-11 - 18290 - Thomas Gibble-Remove spot cooler from EngB151 and return to shop. - Gail Jackson | ECB 151 Please adjust the temperature asap!! It's 89 degrees and I just can't work like this. I had the same issue last week. 2017-03-10 - 18290 - Gail Jackson-Found B151 very hot, talked with CORE Contractor "said roof off limits; in process of replacing roof and A/H systems". Asked if we had spot cooler they could rent/barrow it was they caused heat, talked with Steve took spot cooler over, set in office will notify Jennifer. - Gail Jackson; 2017-03-10 - 18290 - Carl Karr-Found B151 very hot, talked with CORE Contractor "said roof off limits; in process of replacing roof and A/H systems". Asked if we had spot cooler they could rent/barrow it was they caused heat, talked with Steve took spot cooler over, set in office will notify Jennifer. - Gail Jackson; 2017-04-11 - 18290 - Gail Jackson-Remove spot cooler from EngB151 and return to shop. - Gail Jackson; 2017-04-11 - 18290 - Thomas Gibble-Remove spot cooler from EngB151 and return to shop. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-08 | 26770 | TMPE-223387 | I would like to request that someone take a look at my office vent. There is a substance between the vents and I just want to ensure that it is dirt and not something else. I am located in CSB, office #352C. Please let me know if you have questions or need anything else. Thank you in advance for . . . | 2017-05-11 - 18010 - Roque Garcia-The substance was dirt and lent. - Roque Garcia | I would like to request that someone take a look at my office vent. There is a substance between the vents and I just want to ensure that it is dirt and not something else. I am located in CSB, office #352C. Please let me know if you have questions or need anything else. Thank you in advance for . . . 2017-05-11 - 18010 - Roque Garcia-The substance was dirt and lent. - Roque Garcia | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-08 | 26777 | TMPE-223380 | noisy motor bearings on greenhouse A/H #1..located on the roof of L/S E | 2017-04-05 - 18050 - Gail Jackson-Found motor bearings burned out, replaced with new 311 and 309; these bearings I had on truck from job at ISTB 5 #10. A new motor will be used at ISTB 5 # 10. Trip to shop for puller extension. Left grease zerks out for unit had too much grease in old bearings. Run test complete. Observed that evap section of unit has no pump will contact bldg mngr to check status. - Gail Jackson; 2017-04-05 - 18050 - Thomas Gibble-Found motor bearings burned out, replaced with new 311 and 309; these bearings I had on truck from job at ISTB 5 #10. A new motor will be used at ISTB 5 # 10. Trip to shop for puller extension. Left grease zerks out for unit had too much grease in old bearings. Run test complete. Observed that evap section of unit has no pump will contact bldg mngr to check status. - Gail Jackson | noisy motor bearings on greenhouse A/H #1..located on the roof of L/S E 2017-04-05 - 18050 - Gail Jackson-Found motor bearings burned out, replaced with new 311 and 309; these bearings I had on truck from job at ISTB 5 #10. A new motor will be used at ISTB 5 # 10. Trip to shop for puller extension. Left grease zerks out for unit had too much grease in old bearings. Run test complete. Observed that evap section of unit has no pump will contact bldg mngr to check status. - Gail Jackson; 2017-04-05 - 18050 - Thomas Gibble-Found motor bearings burned out, replaced with new 311 and 309; these bearings I had on truck from job at ISTB 5 #10. A new motor will be used at ISTB 5 # 10. Trip to shop for puller extension. Left grease zerks out for unit had too much grease in old bearings. Run test complete. Observed that evap section of unit has no pump will contact bldg mngr to check status. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 26792 | TMPE-223365 | restroom e f bad in rm:128w1 above toilet stall | 2017-03-20 - 18160 - Robert Dauscher-Checked unit found faulty motor(locked up) Removed motor and brought into shop. disassembled motor assembly. Need to pick up parts on Monday. - Robert Dauscher; 2017-03-20 - 18160 - Robert Dauscher-picked up motor from supply house. Returned to shop. reassembled motor assembly. returned to building and installed exhaust fan. - Robert Dauscher | restroom e f bad in rm:128w1 above toilet stall 2017-03-20 - 18160 - Robert Dauscher-Checked unit found faulty motor(locked up) Removed motor and brought into shop. disassembled motor assembly. Need to pick up parts on Monday. - Robert Dauscher; 2017-03-20 - 18160 - Robert Dauscher-picked up motor from supply house. Returned to shop. reassembled motor assembly. returned to building and installed exhaust fan. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-03-08 | 26845 | TMPE-223312 | sump pump not working, cords have been cut need repair, old W/O#186374 Pump is located at exterior north west corner of building. School of Human Evolution and Social Change | 2017-03-17 - 23100 - Derek Gittings-repairing pipe and pump. - Derek Gittings; 2017-03-21 - 23100 - Derek Gittings-replacing pump and pipe. - Derek Gittings; 2017-03-23 - 23100 - Derek Gittings-replacing pump and pipe. - Derek Gittings; 2017-03-24 - 23100 - Derek Gittings-replaced pump and pipe. - Derek Gittings | sump pump not working, cords have been cut need repair, old W/O#186374 Pump is located at exterior north west corner of building. School of Human Evolution and Social Change 2017-03-17 - 23100 - Derek Gittings-repairing pipe and pump. - Derek Gittings; 2017-03-21 - 23100 - Derek Gittings-replacing pump and pipe. - Derek Gittings; 2017-03-23 - 23100 - Derek Gittings-replacing pump and pipe. - Derek Gittings; 2017-03-24 - 23100 - Derek Gittings-replaced pump and pipe. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-08 | 26877 | TMPE-223280 | Bio Design A Repair of fan coil unit. Bio Design team completed, invoice payment to Metal Masters. | NA | Bio Design A Repair of fan coil unit. Bio Design team completed, invoice payment to Metal Masters. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-08 | 27432 | TMPE-222725 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27433 | TMPE-222724 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27434 | TMPE-222723 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27435 | TMPE-222722 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27688 | TMPE-222469 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27689 | TMPE-222468 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27690 | TMPE-222467 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-08 | 27691 | TMPE-222466 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-09 | 150367 | RNLD-100934 | !! The AC unit in this is room is really dirty. There are brown particles that are growing on the vent and dropping on the floor. Please clean the vent blades and sweep the floor of the brown particles. Thank you. 4NI91HM | 2017-03-17 - 18010 - Allan Blair-3/10 - Allan cleaned filters and cleaned vanes. The unit is looking and performing good! - Gayle Swenson | !! The AC unit in this is room is really dirty. There are brown particles that are growing on the vent and dropping on the floor. Please clean the vent blades and sweep the floor of the brown particles. Thank you. 4NI91HM 2017-03-17 - 18010 - Allan Blair-3/10 - Allan cleaned filters and cleaned vanes. The unit is looking and performing good! - Gayle Swenson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-09 | 230537 | POLY-117661 | REPAIR OF BOTH CHILLER PRIMARY WATER PUMPS 4O216EO | 2017-03-10 - 18080 - Allan Blair-3/9 - found cooling fan blades cracked - need to order new blades - Steve Clark; 2017-03-22 - 18080 - Allan Blair-replaced cooling fans on both pump blades - Steve Clark | REPAIR OF BOTH CHILLER PRIMARY WATER PUMPS 4O216EO 2017-03-10 - 18080 - Allan Blair-3/9 - found cooling fan blades cracked - need to order new blades - Steve Clark; 2017-03-22 - 18080 - Allan Blair-replaced cooling fans on both pump blades - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-09 | 230558 | POLY-117640 | Debbie CALLED STEVE !! Hi The compressed air to the lab is down. We need it back up asap please. S 42B2GAA | 2017-03-09 - 18030 - Steve Clark-CHILLER WAS DOWN - WHEN CHILLER CAME BACK ON LINE, COMPRESSOR JUST NEEDED TO BE RESET - Steve Clark | Debbie CALLED STEVE !! Hi The compressed air to the lab is down. We need it back up asap please. S 42B2GAA 2017-03-09 - 18030 - Steve Clark-CHILLER WAS DOWN - WHEN CHILLER CAME BACK ON LINE, COMPRESSOR JUST NEEDED TO BE RESET - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-09 | 26570 | TMPE-223587 | Chamber #2 in LSE 645 is not holding set temp again. Please initiate a work order for HVAC to address at their earliest opportunity. Thank you. 42BLHKH | 2017-04-18 - 18010 - Robert Ecabert-Replaced one bad axial fan and replaced one hot gas solenoid valve. I recovered all of the refrigerant from this system which was 3 LBS 11 Ounces of refrigerant R-22. I used 3LBS 11ounces of R-22 from refrigerant drum cylinder tag number JS160216-22. Purchase Order number 1508533. - Robert Ecabert | Chamber #2 in LSE 645 is not holding set temp again. Please initiate a work order for HVAC to address at their earliest opportunity. Thank you. 42BLHKH 2017-04-18 - 18010 - Robert Ecabert-Replaced one bad axial fan and replaced one hot gas solenoid valve. I recovered all of the refrigerant from this system which was 3 LBS 11 Ounces of refrigerant R-22. I used 3LBS 11ounces of R-22 from refrigerant drum cylinder tag number JS160216-22. Purchase Order number 1508533. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-03-09 | 26625 | TMPE-223532 | air compressor ID number 3487 needs a new pressure switch. Please assign to Derek and Michael Kelley. | 2017-03-16 - 18030 - Derek Gittings-replaced switc h. - Derek Gittings | air compressor ID number 3487 needs a new pressure switch. Please assign to Derek and Michael Kelley. 2017-03-16 - 18030 - Derek Gittings-replaced switc h. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-09 | 26650 | TMPE-223507 | SPECIAL FUNDING: CP condenser water pump #3 has a bad mechanical seal that we need to get replaced before it completely fails to the point where we cannot run it. There is a long lead time on parts and would like to get it repaired prior to the cooling season. This pump will not be covered by the O. . . | NA | SPECIAL FUNDING: CP condenser water pump #3 has a bad mechanical seal that we need to get replaced before it completely fails to the point where we cannot run it. There is a long lead time on parts and would like to get it repaired prior to the cooling season. This pump will not be covered by the O. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-10 | 208462 | RAMA-100802 | !! Air Conditioning Unit leaking -- not cooling. The unit has been turned off with the exception of the fan. The room is humid and warm. 4NHK5AN | NA | !! Air Conditioning Unit leaking -- not cooling. The unit has been turned off with the exception of the fan. The room is humid and warm. 4NHK5AN NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-10 | 230503 | POLY-117695 | Repeat Request. Air filter for conditioning unit needs to be replaced 4NG67I3 | NA | Repeat Request. Air filter for conditioning unit needs to be replaced 4NG67I3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-10 | 230514 | POLY-117684 | Refrigerated chiller not cooling properly. Please inspect and evaluate parts or repairs needed for proper cooling. 42B55N2 | NA | Refrigerated chiller not cooling properly. Please inspect and evaluate parts or repairs needed for proper cooling. 42B55N2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-10 | 26441 | TMPE-223716 | TRANSFER TO HVAC the problem that the requester thinks is a leak is actually a damper control Switch/gear box. This unit is a Meta Sys and has a identifier number that is #26. Its directly inside the ceiling access panel in the ladies rest room at Stauffer B 212. It only makes popping noise when . . . | 2017-05-01 - 13050 - Carl Karr-Found VMA hanging loose. Secured VMA. - Carl Karr; 2017-05-01 - 13050 - Gail Jackson-Found VMA hanging loose. Secured VMA. - Carl Karr; 2017-05-01 - 13050 - Thomas Gibble-Found VMA hanging loose. Secured VMA. - Carl Karr | TRANSFER TO HVAC the problem that the requester thinks is a leak is actually a damper control Switch/gear box. This unit is a Meta Sys and has a identifier number that is #26. Its directly inside the ceiling access panel in the ladies rest room at Stauffer B 212. It only makes popping noise when . . . 2017-05-01 - 13050 - Carl Karr-Found VMA hanging loose. Secured VMA. - Carl Karr; 2017-05-01 - 13050 - Gail Jackson-Found VMA hanging loose. Secured VMA. - Carl Karr; 2017-05-01 - 13050 - Thomas Gibble-Found VMA hanging loose. Secured VMA. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-10 | 26450 | TMPE-223707 | !! Coor Hall, 6th floor West Return Fan 13. Please create MWO for the Electricians to troubleshoot Return Fan VFD 13. Which is in Fault at this time. 42DIM5O | 2017-03-13 - 15100 - Semeon Haile-bad motor bearing transferred to HVAC shop - Semeon Haile; 2017-03-16 - 15100 - Semeon Haile-troubleshoot return fan VFD, motor bad HVAC shop replaced it. - Semeon Haile | !! Coor Hall, 6th floor West Return Fan 13. Please create MWO for the Electricians to troubleshoot Return Fan VFD 13. Which is in Fault at this time. 42DIM5O 2017-03-13 - 15100 - Semeon Haile-bad motor bearing transferred to HVAC shop - Semeon Haile; 2017-03-16 - 15100 - Semeon Haile-troubleshoot return fan VFD, motor bad HVAC shop replaced it. - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-10 | 26459 | TMPE-223698 | T4SP 101 Both A/C units in trailer are not cooling down past 81 degrees. It is starting to get hot. 4O190HG | 2017-03-28 - 18290 - Gail Jackson-Found BARD unit on NW very low on R22, adjusted charge. Trip to ARS for stop leak, installed. Change filters on both BARD units, trip to ARS Mesa for parts, filters not changed in YEARS. Need added to list. PMd both units Complete. Unit on NW passed its useful service life if Stop Leak does not work needs replaced. Customer wants replaced. - Gail Jackson | T4SP 101 Both A/C units in trailer are not cooling down past 81 degrees. It is starting to get hot. 4O190HG 2017-03-28 - 18290 - Gail Jackson-Found BARD unit on NW very low on R22, adjusted charge. Trip to ARS for stop leak, installed. Change filters on both BARD units, trip to ARS Mesa for parts, filters not changed in YEARS. Need added to list. PMd both units Complete. Unit on NW passed its useful service life if Stop Leak does not work needs replaced. Customer wants replaced. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-10 | 26463 | TMPE-223694 | condensate pump runs continuously float needs replacement old W/O#181841 | NA | condensate pump runs continuously float needs replacement old W/O#181841 NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-10 | 26475 | TMPE-223682 | The AC unit at Customer Relations suite 105, the unit by my desk (Cathy Harrison), is blowing only hot air and up to 80 already. I think it must be out of the anti-freeze or whatever coolant they use as they found last year it was leaking. 4ND3478 | 2017-04-14 - 18290 - Thomas Gibble-unit has a big leak and we can not find it. we are going to put a new unit .It is a Californa heat pump. - Thomas Gibble; 2017-04-14 - 18290 - Gail Jackson-unit has a big leak and we can not find it. we are going to put a new unit .It is a Californa heat pump. - Thomas Gibble; 2017-04-18 - 18290 - Gail Jackson-Transport spot cooler 1009 to parking and transit for temporary cooling Ca ac is down, leak in evap coil, unit is past service life. needs replaced. Trip to shop for connectors. - Gail Jackson; 2017-04-18 - 18290 - Robert Dauscher-Transport spot cooler 1009 to parking and transit for temporary cooling Ca ac is down, leak in evap coil, unit is past service life. needs replaced. Trip to shop for connectors. - Gail Jackson; 2017-05-03 - 18290 - Thomas Gibble-delivered spot cooler to 105 area - Thomas Gibble; 2017-05-03 - 18290 - Gail Jackson-delivered spot cooler to 105 area - Thomas Gibble | The AC unit at Customer Relations suite 105, the unit by my desk (Cathy Harrison), is blowing only hot air and up to 80 already. I think it must be out of the anti-freeze or whatever coolant they use as they found last year it was leaking. 4ND3478 2017-04-14 - 18290 - Thomas Gibble-unit has a big leak and we can not find it. we are going to put a new unit .It is a Californa heat pump. - Thomas Gibble; 2017-04-14 - 18290 - Gail Jackson-unit has a big leak and we can not find it. we are going to put a new unit .It is a Californa heat pump. - Thomas Gibble; 2017-04-18 - 18290 - Gail Jackson-Transport spot cooler 1009 to parking and transit for temporary cooling Ca ac is down, leak in evap coil, unit is past service life. needs replaced. Trip to shop for connectors. - Gail Jackson; 2017-04-18 - 18290 - Robert Dauscher-Transport spot cooler 1009 to parking and transit for temporary cooling Ca ac is down, leak in evap coil, unit is past service life. needs replaced. Trip to shop for connectors. - Gail Jackson; 2017-05-03 - 18290 - Thomas Gibble-delivered spot cooler to 105 area - Thomas Gibble; 2017-05-03 - 18290 - Gail Jackson-delivered spot cooler to 105 area - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-10 | 26477 | TMPE-223680 | LS C LL EQ Room: condensate pumps blowing steam assign to AC shop Jose | NA | LS C LL EQ Room: condensate pumps blowing steam assign to AC shop Jose NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-10 | 26478 | TMPE-223679 | LS C LL EQ Room: condensate pumps blowing steam assign to AC shop Jose | 2017-03-20 - 23100 - Jose Lopez-pumps were not working 1 pump stock the other not pumping,remove pump#1 free impeller pump#2 is running now need to lock more. - Jose Lopez | LS C LL EQ Room: condensate pumps blowing steam assign to AC shop Jose 2017-03-20 - 23100 - Jose Lopez-pumps were not working 1 pump stock the other not pumping,remove pump#1 free impeller pump#2 is running now need to lock more. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-03-10 | 26529 | TMPE-223628 | CSB 42 Bldg control air compressor is off in alarm due to faulty motors. Send to HVAC services for checkout and repair. 42B213C | 2017-03-20 - 18030 - Michael Kelley-picked up parts from Grainger. 2 trips - Michael Kelley; 2017-03-20 - 18030 - Roque Garcia-Replaced the two contactors and aux contactors. The original brand of contactors was WEG changed them into Schneider. - Roque Garcia | CSB 42 Bldg control air compressor is off in alarm due to faulty motors. Send to HVAC services for checkout and repair. 42B213C 2017-03-20 - 18030 - Michael Kelley-picked up parts from Grainger. 2 trips - Michael Kelley; 2017-03-20 - 18030 - Roque Garcia-Replaced the two contactors and aux contactors. The original brand of contactors was WEG changed them into Schneider. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-03-10 | 26543 | TMPE-223614 | WFA Women\\u2019s restroom 122 Stall #19 There is a plugged return vent on the ceiling. for HVAC | 2017-05-13 - 18010 - Robert Dauscher-cleaned return air grill - Robert Dauscher | WFA Women\\u2019s restroom 122 Stall #19 There is a plugged return vent on the ceiling. for HVAC 2017-05-13 - 18010 - Robert Dauscher-cleaned return air grill - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-11 | 211146 | RACC-117464 | Air conditioning not working. Room will not go below 80 degrees. Also if ceiling ban could be balanced that would be nice. Contact Name: Contact Phone Number: 2105899194 Contact Email: timothy.trianadavie@gmail.com 4NFL0DL | 2017-03-14 - 10010 - replaced fuse - Jim Deal | Air conditioning not working. Room will not go below 80 degrees. Also if ceiling ban could be balanced that would be nice. Contact Name: Contact Phone Number: 2105899194 Contact Email: timothy.trianadavie@gmail.com 4NFL0DL 2017-03-14 - 10010 - replaced fuse - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-11 | 25918 | TMPE-224239 | ASUHC Lisa D Need AC units turned on in student services to be worked on. Dispatched to Mike Cozens time of dispatch 739 am | 2017-03-13 - 18290 - Michael Cozens-I came in, maximized AH air pressure, repaired one control VAV unit and adjusted local control pneumatic thermostats to full cooling for airflow test. - Mike Cozens | ASUHC Lisa D Need AC units turned on in student services to be worked on. Dispatched to Mike Cozens time of dispatch 739 am 2017-03-13 - 18290 - Michael Cozens-I came in, maximized AH air pressure, repaired one control VAV unit and adjusted local control pneumatic thermostats to full cooling for airflow test. - Mike Cozens | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-12 | 230496 | POLY-117702 | A/C not working, fan turns on but air isn't cool. 4NFB825 | NA | A/C not working, fan turns on but air isn't cool. 4NFB825 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-13 | 166492 | RFMT-141839 | Weekly Building PM Inspection. | 2017-03-17 - 50051 - Salvatore Marasco Jr-Walked all buildings -There is a noisy exhaust fan on the roof of Irish C building (North West corner over Men's bathrooms). A new V-Belt was installed about a month ago. Maybe blower motor bearings are worn or blower wheel is rubbing housing. 40 foot extension ladder is required - Salvatore Marasco Jr; 2017-03-17 - 50051 - Sal's results were noted and a new work order will be created for the Res. Life HVAC team ti inspect. - Gregory Stetka | Weekly Building PM Inspection. 2017-03-17 - 50051 - Salvatore Marasco Jr-Walked all buildings -There is a noisy exhaust fan on the roof of Irish C building (North West corner over Men's bathrooms). A new V-Belt was installed about a month ago. Maybe blower motor bearings are worn or blower wheel is rubbing housing. 40 foot extension ladder is required - Salvatore Marasco Jr; 2017-03-17 - 50051 - Sal's results were noted and a new work order will be created for the Res. Life HVAC team ti inspect. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-13 | 211065 | RACC-117545 | !! Air conditioner on the right side of the apartment no longer works properly and is unable to cool. Every day it is extremely warm in our apartment and we are having to run the overhead fans which doesn't entirely solve the issue with the warmth. Once again, the cooling unit that is shared between. . . | NA | !! Air conditioner on the right side of the apartment no longer works properly and is unable to cool. Every day it is extremely warm in our apartment and we are having to run the overhead fans which doesn't entirely solve the issue with the warmth. Once again, the cooling unit that is shared between. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-13 | 211069 | RACC-117541 | !! Our A/C isn't working. We are only getting a fan. 4O5K425 | NA | !! Our A/C isn't working. We are only getting a fan. 4O5K425 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-13 | 230476 | POLY-117722 | The air handler fan is running, but the AC unit outside does not turn on. 4NM4E6G | NA | The air handler fan is running, but the AC unit outside does not turn on. 4NM4E6G NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 230480 | POLY-117718 | BILLED CALLED STEVE !! Very warm in front office-can hear that the a/c is on but blowing warm air 42AENHG BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) | 2017-03-17 - 18290 - Allan Blair-chiller off - reset chiller corrected problem - Steve Clark | BILLED CALLED STEVE !! Very warm in front office-can hear that the a/c is on but blowing warm air 42AENHG BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) 2017-03-17 - 18290 - Allan Blair-chiller off - reset chiller corrected problem - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-13 | 230494 | POLY-117704 | CALLED STEVE !! Hi The compressed air is down to the lab and its very hot in here. I think water chiller went out again? thx 42B2GAA | 2017-03-17 - 18010 - Steve Clark-chiller was down - once chiller was on line - reset the alarm in the air compressor - Steve Clark | CALLED STEVE !! Hi The compressed air is down to the lab and its very hot in here. I think water chiller went out again? thx 42B2GAA 2017-03-17 - 18010 - Steve Clark-chiller was down - once chiller was on line - reset the alarm in the air compressor - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-13 | 25648 | TMPE-224509 | transfer EL TO HVAC the electricians have indicated there is a bad motor or bearing. Thank you ORIG REQUEST !! Coor Hall, 6th floor West Return Fan 13. Please create MWO for the Electricians to troubleshoot Return Fan VFD 13. Which is in Fault at this time. 42DIM5O | NA | transfer EL TO HVAC the electricians have indicated there is a bad motor or bearing. Thank you ORIG REQUEST !! Coor Hall, 6th floor West Return Fan 13. Please create MWO for the Electricians to troubleshoot Return Fan VFD 13. Which is in Fault at this time. 42DIM5O NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-13 | 230504 | POLY-117694 | CALLED STEVE Hello, The air conditioning appears to be off in rooms 114 - 118 here at the print lab. The large machinery makes the room extremely warm when the ac is not on. Please let me know if you have any questions. Thank you! Chris Halkovic 4NAMLC5 | 2017-03-20 - 18010 - Steve Clark-tech chiller not operating correctly - switched over to NRG plant to get cooling to building - Steve Clark | CALLED STEVE Hello, The air conditioning appears to be off in rooms 114 - 118 here at the print lab. The large machinery makes the room extremely warm when the ac is not on. Please let me know if you have any questions. Thank you! Chris Halkovic 4NAMLC5 2017-03-20 - 18010 - Steve Clark-tech chiller not operating correctly - switched over to NRG plant to get cooling to building - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 25651 | TMPE-224506 | Repeat Request. The fan in the women's restroom stopped working. We had this replaced a few weeks ago so not sure what the problem is. 4O5LJ57 | 2017-04-05 - 18010 - Jennifer Moyer-Removed fan.Motor was seized up. New motor on order. - Jennifer Moyer; 2017-04-17 - 18010 - Jennifer Moyer-picked up motor from maintenance stores, cleaned blower wheel, assembled motor, cut down motor shaft with grinding wheel, installed and tested. - Jennifer Moyer | Repeat Request. The fan in the women's restroom stopped working. We had this replaced a few weeks ago so not sure what the problem is. 4O5LJ57 2017-04-05 - 18010 - Jennifer Moyer-Removed fan.Motor was seized up. New motor on order. - Jennifer Moyer; 2017-04-17 - 18010 - Jennifer Moyer-picked up motor from maintenance stores, cleaned blower wheel, assembled motor, cut down motor shaft with grinding wheel, installed and tested. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-13 | 25663 | TMPE-224494 | !! URGENT! Requesting HVAC shop for repair of rooftop trane unit. 3 fans are not spinning, compressor appears to be running. Interior temps are climbing and at ~90* currently. We have isolation chambers also heating this area. Please call Me (Mike 480-227-3476) for entry if needed. Thanks. . . | NA | !! URGENT! Requesting HVAC shop for repair of rooftop trane unit. 3 fans are not spinning, compressor appears to be running. Interior temps are climbing and at ~90* currently. We have isolation chambers also heating this area. Please call Me (Mike 480-227-3476) for entry if needed. Thanks. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-13 | 25671 | TMPE-224486 | ALBER Please have the HVAC Shop PM all 3 AC units in the Press Box at Farrington. PO is YG202004932. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF | 2017-03-23 - 18010 - Zhi Yu-We PM 3 Panasonic unit. We clean all filter check air temp split @ 20 .. the unit on the west are split around 15. We pick an 5/16 adapter from Ars to check pressure. It appears little low @ 75 psi. We charge 1.5lbs. - Zhi Yu; 2017-03-23 - 18010 - Roque Garcia-We PM 3 Panasonic unit. We clean all filter check air temp split @ 20 .. the unit on the west are split around 15. We pick an 5/16 adapter from Ars to check pressure. It appears little low @ 75 psi. We charge 1.5lbs. - Zhi Yu | ALBER Please have the HVAC Shop PM all 3 AC units in the Press Box at Farrington. PO is YG202004932. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF 2017-03-23 - 18010 - Zhi Yu-We PM 3 Panasonic unit. We clean all filter check air temp split @ 20 .. the unit on the west are split around 15. We pick an 5/16 adapter from Ars to check pressure. It appears little low @ 75 psi. We charge 1.5lbs. - Zhi Yu; 2017-03-23 - 18010 - Roque Garcia-We PM 3 Panasonic unit. We clean all filter check air temp split @ 20 .. the unit on the west are split around 15. We pick an 5/16 adapter from Ars to check pressure. It appears little low @ 75 psi. We charge 1.5lbs. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-13 | 25696 | TMPE-224461 | LIB C00U4 EMS 1. HVAC & EMS 010 Hayden Library Expansion (C00U4) HVAC & EMS to respond to this call together (please coordinate so both are on-site at the same time) Supply fan 1 is short cycling through Supply fan. . . | 2017-04-07 - 18010 - Zhi Yu-I coordinate Nick from EMS. We over at Hayden Library C00U4. The Dampers are set or normally Closed and powered open when fan starts up. SF 1 are in normal operation. SF 2 Missing upper actuator and lower slipping. Need to gain access in the Plenum. - Zhi Yu; 2017-04-07 - 18010 - Zhi Yu-At C00U4. We ask Carl to removed panel on the SF 2 Plenum. The all the damper is pin with screw in Open position. All the bracket and rod are miss aligned. Will need replacement or serious repair. - Zhi Yu; 2017-04-07 - 18010 - Carl Karr-At C00U4. We ask Carl to removed panel on the SF 2 Plenum. The all the damper is pin with screw in Open position. All the bracket and rod are miss aligned. Will need replacement or serious repair. - Zhi Yu; 2017-05-05 - 18010 - Michael Kelley-Checked job status. Job is done. - Michael Kelley | LIB C00U4 EMS 1. HVAC & EMS 010 Hayden Library Expansion (C00U4) HVAC & EMS to respond to this call together (please coordinate so both are on-site at the same time) Supply fan 1 is short cycling through Supply fan. . . 2017-04-07 - 18010 - Zhi Yu-I coordinate Nick from EMS. We over at Hayden Library C00U4. The Dampers are set or normally Closed and powered open when fan starts up. SF 1 are in normal operation. SF 2 Missing upper actuator and lower slipping. Need to gain access in the Plenum. - Zhi Yu; 2017-04-07 - 18010 - Zhi Yu-At C00U4. We ask Carl to removed panel on the SF 2 Plenum. The all the damper is pin with screw in Open position. All the bracket and rod are miss aligned. Will need replacement or serious repair. - Zhi Yu; 2017-04-07 - 18010 - Carl Karr-At C00U4. We ask Carl to removed panel on the SF 2 Plenum. The all the damper is pin with screw in Open position. All the bracket and rod are miss aligned. Will need replacement or serious repair. - Zhi Yu; 2017-05-05 - 18010 - Michael Kelley-Checked job status. Job is done. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 25701 | TMPE-224456 | 4. HVAC 010 Hayden Library Expansion (C00U3) CHW pump 1 not running when commanded Stop switch lockout holding stop switch down at MCC. No lock on lockout mechanism. If there are no issues with CHWP-1, release stop switch lockout. Please check and verify. (From Commissioning; Hayden Exp Issues. . . | 2017-04-12 - 18010 - Zhi Yu-C00U3 The Stop switch cannot holding down. Bad mechanism on the Stop switch. CHWP-1 runs find. Please have the Electrician to replaced the Stop and Start Switch. - Zhi Yu | 4. HVAC 010 Hayden Library Expansion (C00U3) CHW pump 1 not running when commanded Stop switch lockout holding stop switch down at MCC. No lock on lockout mechanism. If there are no issues with CHWP-1, release stop switch lockout. Please check and verify. (From Commissioning; Hayden Exp Issues. . . 2017-04-12 - 18010 - Zhi Yu-C00U3 The Stop switch cannot holding down. Bad mechanism on the Stop switch. CHWP-1 runs find. Please have the Electrician to replaced the Stop and Start Switch. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-03-13 | 25703 | TMPE-224454 | 2. HVAC 010 Hayden Library Expansion (C00U4) Hayden Expansion CHW pump 2 is commanded on but not running. HOA switch is off. If no outstanding issue exists with pump 2, place HOA in auto. Please check and verify. (From Commissioning; Hayden Exp I. . . | 2017-04-12 - 18010 - Zhi Yu-We started the pump #2. No issue were found. We placed HOA in Auto. - Zhi Yu | 2. HVAC 010 Hayden Library Expansion (C00U4) Hayden Expansion CHW pump 2 is commanded on but not running. HOA switch is off. If no outstanding issue exists with pump 2, place HOA in auto. Please check and verify. (From Commissioning; Hayden Exp I. . . 2017-04-12 - 18010 - Zhi Yu-We started the pump #2. No issue were found. We placed HOA in Auto. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 25706 | TMPE-224451 | LIB C00U4 3. HVAC 010 Hayden Library Expansion (C00U4) Hayden Expansion CHW pump 3 is will not turn when VFD is on. Pump appears to be locked up. VFD is currently turned off at disconnect on VFD. Please check and verify. (From Commissioning; Hayden Exp Issues. . . | 2017-04-12 - 18010 - Zhi Yu-CHW pump #3 engage the VFD pump are not turn. We separated coupling from motor to pump. We turn the pump is seize up. We try to break loose by turn with pipe wrench,but no go.. We also start the motor and runs find.. Will need assist to remove the pump!! - Zhi Yu | LIB C00U4 3. HVAC 010 Hayden Library Expansion (C00U4) Hayden Expansion CHW pump 3 is will not turn when VFD is on. Pump appears to be locked up. VFD is currently turned off at disconnect on VFD. Please check and verify. (From Commissioning; Hayden Exp Issues. . . 2017-04-12 - 18010 - Zhi Yu-CHW pump #3 engage the VFD pump are not turn. We separated coupling from motor to pump. We turn the pump is seize up. We try to break loose by turn with pipe wrench,but no go.. We also start the motor and runs find.. Will need assist to remove the pump!! - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-03-13 | 25738 | TMPE-224419 | !! it's time for an a/c tech to check the swamp cooler on the roof over this room. it has stopped running. thank you. Contact Name: sarah hurd rindy Contact Phone Number: 678 7943 Contact Email: 42CAB57 | 2017-05-15 - 18100 - Robert Dauscher-replaced non-working evap cooler pump with truck stock - Robert Dauscher | !! it's time for an a/c tech to check the swamp cooler on the roof over this room. it has stopped running. thank you. Contact Name: sarah hurd rindy Contact Phone Number: 678 7943 Contact Email: 42CAB57 2017-05-15 - 18100 - Robert Dauscher-replaced non-working evap cooler pump with truck stock - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 25758 | TMPE-224399 | There is no air coming out of the vent in my office (324H) 4O3DCE4 | 2017-04-28 - 18010 - Nicholas Sizow-Restarted Trane Unit AC-2 - Nicholas Sizow | There is no air coming out of the vent in my office (324H) 4O3DCE4 2017-04-28 - 18010 - Nicholas Sizow-Restarted Trane Unit AC-2 - Nicholas Sizow | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-13 | 25789 | TMPE-224368 | SDFC 100S1 There's a leak in the EQ Rm that's coming from a pump. | 2017-03-13 - 23100 - CALLED TO BRIAN Q. - Monica Moraga; 2017-03-22 - 23100 - Michael Kelley-Talk to Lance found ou8t it was condensate pump. 7407 id # both pumps need to be new seals. - Michael Kelley; 2017-04-04 - 23100 - Michael Kelley-Talk to Jose Lopez. This is a job that belongs to him. He ordered a new float., seals for pump. I do not have the work order number. Jose is waiting for the weather to warm up. - Michael Kelley | SDFC 100S1 There's a leak in the EQ Rm that's coming from a pump. 2017-03-13 - 23100 - CALLED TO BRIAN Q. - Monica Moraga; 2017-03-22 - 23100 - Michael Kelley-Talk to Lance found ou8t it was condensate pump. 7407 id # both pumps need to be new seals. - Michael Kelley; 2017-04-04 - 23100 - Michael Kelley-Talk to Jose Lopez. This is a job that belongs to him. He ordered a new float., seals for pump. I do not have the work order number. Jose is waiting for the weather to warm up. - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-13 | 25793 | TMPE-224364 | due to fridge drainage, will need a small dehumidifier. 42CB734 | 2017-05-09 - 18010 - Jennifer Moyer-Issue resolved. - Jennifer Moyer | due to fridge drainage, will need a small dehumidifier. 42CB734 2017-05-09 - 18010 - Jennifer Moyer-Issue resolved. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-14 | 211034 | RACC-117576 | We are having several issues involving the air conditioner, fan, and towel rack in the bathroom. 4NL4BAO | NA | We are having several issues involving the air conditioner, fan, and towel rack in the bathroom. 4NL4BAO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-14 | 211042 | RACC-117568 | AC unit has completely stopped working and requires fixing, perhaps even replacement (I don't don't know enough to say, but something in the unit is definitely broken). 4NNNMDK | NA | AC unit has completely stopped working and requires fixing, perhaps even replacement (I don't don't know enough to say, but something in the unit is definitely broken). 4NNNMDK NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-14 | 25412 | TMPE-224745 | !! there are high frequency and low frequency sound in my room ERC 419. It sounds like and AC pipe vibration or light harmonic balancer problems. Please get them fixed. 4O1GM1B | 2017-03-15 - 18010 - Mauricio Martinez Reyes-Transferred to HVAC. after looking around for several minutes I able to identify the source of the sounds. The high pitched sound was coming from the motion sensor locates just outside the room. I reset the sensor and the noise stopped. The low pitch sound, I believe is coming from either the air handler in the E.Q. room above or the extraction fan in the roof. Booth items are vibrating loudly. I reported this to my supervisor and he is to send HVAC out to check it out. Labor:1.75 Hrs. Material:N/A - Mauricio Martinez Reyes | !! there are high frequency and low frequency sound in my room ERC 419. It sounds like and AC pipe vibration or light harmonic balancer problems. Please get them fixed. 4O1GM1B 2017-03-15 - 18010 - Mauricio Martinez Reyes-Transferred to HVAC. after looking around for several minutes I able to identify the source of the sounds. The high pitched sound was coming from the motion sensor locates just outside the room. I reset the sensor and the noise stopped. The low pitch sound, I believe is coming from either the air handler in the E.Q. room above or the extraction fan in the roof. Booth items are vibrating loudly. I reported this to my supervisor and he is to send HVAC out to check it out. Labor:1.75 Hrs. Material:N/A - Mauricio Martinez Reyes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-14 | 25467 | TMPE-224690 | MU second floor catering kitchen freezer heavy ice build up! | 2017-03-21 - 18180 - Gail Jackson-Found condensate pan broke loose, drain line froze up and busted, no heater installed on line, ice all over product underneath evap. Han kitchen help remove product, trip to shop for new piping and tools. Replaced drain line and insulate. - Gail Jackson; 2017-03-21 - 18180 - Carl Karr-Found condensate pan broke loose, drain line froze up and busted, no heater installed on line, ice all over product underneath evap. Had kitchen help remove product, trip to shop for new piping and tools. Replaced drain line and insulate. - Gail Jackson; 2017-03-23 - 18180 - Gail Jackson-Removed condensate pan from evap to remove ice. Repair and reinstall. Install heat tape on drain line. Run test. Trip to Grainger for heat tape. Complete. - Gail Jackson; 2017-03-23 - 18180 - Thomas Gibble-Removed condensate pan from evap to remove ice. Repair and reinstall. Install heat tape on drain line. Run test. Trip to Grainger for heat tape. Complete. - Gail Jackson | MU second floor catering kitchen freezer heavy ice build up! 2017-03-21 - 18180 - Gail Jackson-Found condensate pan broke loose, drain line froze up and busted, no heater installed on line, ice all over product underneath evap. Han kitchen help remove product, trip to shop for new piping and tools. Replaced drain line and insulate. - Gail Jackson; 2017-03-21 - 18180 - Carl Karr-Found condensate pan broke loose, drain line froze up and busted, no heater installed on line, ice all over product underneath evap. Had kitchen help remove product, trip to shop for new piping and tools. Replaced drain line and insulate. - Gail Jackson; 2017-03-23 - 18180 - Gail Jackson-Removed condensate pan from evap to remove ice. Repair and reinstall. Install heat tape on drain line. Run test. Trip to Grainger for heat tape. Complete. - Gail Jackson; 2017-03-23 - 18180 - Thomas Gibble-Removed condensate pan from evap to remove ice. Repair and reinstall. Install heat tape on drain line. Run test. Trip to Grainger for heat tape. Complete. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3
2017-03-14 | 25480 | TMPE-224677 | !! Hi, We need someone from facilities to please come and check the 37 C CIVV warm room on the 3rd floor as soon as possible - I believe it is B349A. The digital thermometer outside of the room says that it is 37 C in the room, but we currently have thermometers in 2 different locations readi. . . | 2017-03-17 - 18010 - Robert Ecabert-Robert Bantz called in Controlled Enviroment Management Company to recalibrate the sensors for the CIVV room at Biodesign Institute Building B Room B349A and now the room is at its set point and working properly. The set point is at 37 degrees celcius. Robert Bantz is going to call Steve Palumbo and talk to Steve about having this company calibrating all of the sensors to these types of units at the Biodesign Buidings. This company is already working on units throughout this campus already according to Robert Bantz. They calibrate the sensors by using 4 Thermocouples and getting the temperature at each one and then they add all4 separate temperatures together and find the average temperature of the thermocouples combined and the they add an offset to the sensors in the box. - Robert Ecabert | !! Hi, We need someone from facilities to please come and check the 37 C CIVV warm room on the 3rd floor as soon as possible - I believe it is B349A. The digital thermometer outside of the room says that it is 37 C in the room, but we currently have thermometers in 2 different locations readi. . . 2017-03-17 - 18010 - Robert Ecabert-Robert Bantz called in Controlled Enviroment Management Company to recalibrate the sensors for the CIVV room at Biodesign Institute Building B Room B349A and now the room is at its set point and working properly. The set point is at 37 degrees celcius. Robert Bantz is going to call Steve Palumbo and talk to Steve about having this company calibrating all of the sensors to these types of units at the Biodesign Buidings. This company is already working on units throughout this campus already according to Robert Bantz. They calibrate the sensors by using 4 Thermocouples and getting the temperature at each one and then they add all4 separate temperatures together and find the average temperature of the thermocouples combined and the they add an offset to the sensors in the box. - Robert Ecabert | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-14 | 25484 | TMPE-224673 | Air handler 1 supply fan vfd will not run, in auto, fault 4029 drive link failed.is now running in by pass. For electric shop repair. 42A7J3M | 2017-03-17 - 15100 - Gary Conover-Replace VFD - Gary Conover; 2017-03-17 - 15100 - Gary Conover-Job complete - Gary Conover | Air handler 1 supply fan vfd will not run, in auto, fault 4029 drive link failed.is now running in by pass. For electric shop repair. 42A7J3M 2017-03-17 - 15100 - Gary Conover-Replace VFD - Gary Conover; 2017-03-17 - 15100 - Gary Conover-Job complete - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-14 | 25530 | TMPE-224627 | ERC B46 Please assign Duane Rider to look at the two HX-300 Chillers - He has worked on both units in the past. 1) The unit that faces south has not been able to control the temperature. The set point is 15deg C and now is at 21degC. May need a refrigerant charge (R420A). 2) The unit facing east . . . | 2017-03-17 - 18080 - Duane Rider-found leak on valve, turned over to HVAC shop - Duane Rider | ERC B46 Please assign Duane Rider to look at the two HX-300 Chillers - He has worked on both units in the past. 1) The unit that faces south has not been able to control the temperature. The set point is 15deg C and now is at 21degC. May need a refrigerant charge (R420A). 2) The unit facing east . . . 2017-03-17 - 18080 - Duane Rider-found leak on valve, turned over to HVAC shop - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-03-14 | 25544 | TMPE-224613 | !!In the main room, the fan is extremely loud. Please check out and assist. Thank you! | 2017-03-22 - 18010 - Roque Garcia-Spoke with Connie and she stated the fan was off and FACMAN was going to get access to work on the fan - Roque Garcia | !!In the main room, the fan is extremely loud. Please check out and assist. Thank you! 2017-03-22 - 18010 - Roque Garcia-Spoke with Connie and she stated the fan was off and FACMAN was going to get access to work on the fan - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-14 | 25609 | TMPE-224548 | SDFC - 229M1: BT transfer to HVAC - leak coming from 2 pumps - Leak in pipe in the room and it is dripping down into the women's locker room below | 2017-03-14 - 23100 - Called to Steve P. - Jeri Zappanti; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress,waiting for project manager's answer on how to go by fixing unit. - Jose Lopez; 2017-03-20 - 23100 - Jose Lopez-There is a leak on SP-1 pump/pot feeder contained water.my understanding is that EMCAP will respond to this issue. - Jose Lopez | SDFC - 229M1: BT transfer to HVAC - leak coming from 2 pumps - Leak in pipe in the room and it is dripping down into the women's locker room below 2017-03-14 - 23100 - Called to Steve P. - Jeri Zappanti; 2017-03-17 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-03-17 - 23100 - Jose Lopez-work in progress,waiting for project manager's answer on how to go by fixing unit. - Jose Lopez; 2017-03-20 - 23100 - Jose Lopez-There is a leak on SP-1 pump/pot feeder contained water.my understanding is that EMCAP will respond to this issue. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-03-14 | 248233 | MUFT-100521 | replace bearing on cooler for engrained make up air | 2017-03-14 - 15000 - Michael Landrith-done - Michael Landrith | replace bearing on cooler for engrained make up air 2017-03-14 - 15000 - Michael Landrith-done - Michael Landrith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-14 | 250750 | DTPC-117788 | replace batteries on controls for splits on IDF rooms | 2017-03-14 - 18010 - Jose Acero-Replaced old batteries on remote controls for A/C on the IDF rooms - Jose Acero | replace batteries on controls for splits on IDF rooms 2017-03-14 - 18010 - Jose Acero-Replaced old batteries on remote controls for A/C on the IDF rooms - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 166267 | RFMT-142064 | !! The air conditioning is not working at all and it is very hot! Also the bathroom door does not close. Contact Name: Candy Hernandez Contact Phone Number: 6026288551 Contact Email: 4NN4E84 | 2017-03-16 - 18010 - John Romero-Checked out A/C unit. Not getting any power to the motor. Motor is good. Will need to have Simon take a look at it..Removed bathroom door and planed it down 1/4 and replaced. - John Romero | !! The air conditioning is not working at all and it is very hot! Also the bathroom door does not close. Contact Name: Candy Hernandez Contact Phone Number: 6026288551 Contact Email: 4NN4E84 2017-03-16 - 18010 - John Romero-Checked out A/C unit. Not getting any power to the motor. Motor is good. Will need to have Simon take a look at it..Removed bathroom door and planed it down 1/4 and replaced. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 166279 | RFMT-142052 | RES LIFE / Chet: Wall pak not working. Please repair by rm A528U1 | 2017-03-15 - 10010 - Chester Duncan-Replaced motor and run cap - Chester Duncan | RES LIFE / Chet: Wall pak not working. Please repair by rm A528U1 2017-03-15 - 10010 - Chester Duncan-Replaced motor and run cap - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 166281 | RFMT-142050 | RES LIFE / Chet: Wall pak not working. Please repair | 2017-04-06 - 10010 - Chester Duncan-Rebuilt fan unit Installed new squirrel cage - Chester Duncan | RES LIFE / Chet: Wall pak not working. Please repair 2017-04-06 - 10010 - Chester Duncan-Rebuilt fan unit Installed new squirrel cage - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-15 | 166286 | RFMT-142045 | Check HVAC unit for Sonora maint shop. Unit is not working in cooling mode. | 2017-03-17 - 18010 - Thor Millsaps-Replaced actuator on chilled water line. System up and running. - Thor Millsaps | Check HVAC unit for Sonora maint shop. Unit is not working in cooling mode. 2017-03-17 - 18010 - Thor Millsaps-Replaced actuator on chilled water line. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 166325 | RFMT-142006 | !! There is no air conditioning in Best B. If you could turn it on that would be great. | 2017-03-15 - 18010 - Simon Fernandez-checked air handler found filters dirty replaced.also chill water valve in the closed position,notified EMS to open and to check their system. - Simon Fernandez | !! There is no air conditioning in Best B. If you could turn it on that would be great. 2017-03-15 - 18010 - Simon Fernandez-checked air handler found filters dirty replaced.also chill water valve in the closed position,notified EMS to open and to check their system. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-03-15 | 18856 | TMPE-231301 | Naumann Hobbs found battery dead. I left unit with my charger on it returned and tested total:96.30 | NA | Naumann Hobbs found battery dead. I left unit with my charger on it returned and tested total:96.30 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-15 | 210966 | RACC-117644 | !! Vent on wall has fallen off. 4NCAEK6 | NA | !! Vent on wall has fallen off. 4NCAEK6 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 210967 | RACC-117643 | AC unit is leaking. | NA | AC unit is leaking. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 25054 | TMPE-225103 | Naumann Hobbs Located unit, inspected and found bad charger. Ordered a new charger. Installed new charger & reassembled unit. Tested charging system, found batteries low for charger to turn on. Charged each battery individually and left unit on charge. Returned & tested charging system. total: 1. . . | NA | Naumann Hobbs Located unit, inspected and found bad charger. Ordered a new charger. Installed new charger & reassembled unit. Tested charging system, found batteries low for charger to turn on. Charged each battery individually and left unit on charge. Returned & tested charging system. total: 1. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-15 | 25288 | TMPE-224869 | !!HVAC came and put a portable A?C unit inside my office- however it is too loud and a huge distraction for my working condition, please remove. | 2017-03-17 - 18010 - Derek Gittings-moved to a diffrent office at cob - Derek Gittings; 2017-05-01 - 18010 - Derek Gittings-pick up ac unit. - Derek Gittings | !!HVAC came and put a portable A?C unit inside my office- however it is too loud and a huge distraction for my working condition, please remove. 2017-03-17 - 18010 - Derek Gittings-moved to a diffrent office at cob - Derek Gittings; 2017-05-01 - 18010 - Derek Gittings-pick up ac unit. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-15 | 25306 | TMPE-224851 | noisy motor bearings on return fan y-8782. bearing sizes 206...and 208 | NA | noisy motor bearings on return fan y-8782. bearing sizes 206...and 208 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 25346 | TMPE-224811 | ERC B46 TRANSFER TO HVAC TMPE-224627 will need to be transferred to the AC shop. The service request has been troubleshot by Mr. Duane Rider. He has discovered a leak on the threaded nut of the hot gas solenoid valve. Next steps will include refrigerant recovery, leak repair, evacuating the syst. . . | 2017-03-24 - 18080 - Robert Ecabert-The chiller that was tripping had a bad condenser fan motor and was replaced and the schraeder valve stem was leaking on the discharge line and I tried to replace but the schraeder core removal tool would not extract the bad core and it would not tighten down the core to stop the leak completely so I put a tee on it so you can still access the high side discharge port and Art Handdugan said that is all he wants to do to that unit for now because it is cooling the tools for the clean room and he does not want to shut it down since it is the only chiller that is operating at this time.The day that I completed this unit was on 3-22-2017. - Robert Ecabert [Modified: 2017-03-28 Robert Ecabert]; 2017-03-28 - 18080 - Robert Ecabert-On the second chiller that was the south chiller I was able to locate the where the refrigerant leak was coming from. it was leaking out from underneath of the liquid line solenoid valve stem nut I tried to tighten down the nut surrounding the liquid line solenoid valve nut but it would not move.I ordere a new solenoid valve body and I will install it tomorrow. - Robert Ecabert; 2017-03-28 - 18080 - Robert Ecabert-On Thursday March 23rd 2017 I was able to get the liquid line solenoid valve nut off of the solenoid but there was no refrigerant left in the system to recover at the time. I installed the new solenoid valve plunger assembly,kickoff spring,return spring,spring guide,and enclosing tube into the old valve body of the liquid line solenoid valve and then I tightened it down to 360 inch pounds as required as per the instructions. After installing the liquid line solenoid valve assembly I pressureized the system with 250psi of nitrogen to leak check the system but I could not find any leaks in the system and it held the 250pounds of nitrogen. I released the nitrogen out of the system and then I put the system in a vacuum and it pulled down to 250microns and it held the vacuum of 250microns for one hour. After that I charged the unit with 5LBS of refrigerant R-420A and the unit is running fine and taking care of the load it is trying to satisfy in the clean room. I used 5LBS of refrigerant R-420A from refrigerant drum DR122013-4 - Robert Ecabert | ERC B46 TRANSFER TO HVAC TMPE-224627 will need to be transferred to the AC shop. The service request has been troubleshot by Mr. Duane Rider. He has discovered a leak on the threaded nut of the hot gas solenoid valve. Next steps will include refrigerant recovery, leak repair, evacuating the syst. . . 2017-03-24 - 18080 - Robert Ecabert-The chiller that was tripping had a bad condenser fan motor and was replaced and the schraeder valve stem was leaking on the discharge line and I tried to replace but the schraeder core removal tool would not extract the bad core and it would not tighten down the core to stop the leak completely so I put a tee on it so you can still access the high side discharge port and Art Handdugan said that is all he wants to do to that unit for now because it is cooling the tools for the clean room and he does not want to shut it down since it is the only chiller that is operating at this time.The day that I completed this unit was on 3-22-2017. - Robert Ecabert [Modified: 2017-03-28 Robert Ecabert]; 2017-03-28 - 18080 - Robert Ecabert-On the second chiller that was the south chiller I was able to locate the where the refrigerant leak was coming from. it was leaking out from underneath of the liquid line solenoid valve stem nut I tried to tighten down the nut surrounding the liquid line solenoid valve nut but it would not move.I ordere a new solenoid valve body and I will install it tomorrow. - Robert Ecabert; 2017-03-28 - 18080 - Robert Ecabert-On Thursday March 23rd 2017 I was able to get the liquid line solenoid valve nut off of the solenoid but there was no refrigerant left in the system to recover at the time. I installed the new solenoid valve plunger assembly,kickoff spring,return spring,spring guide,and enclosing tube into the old valve body of the liquid line solenoid valve and then I tightened it down to 360 inch pounds as required as per the instructions. After installing the liquid line solenoid valve assembly I pressureized the system with 250psi of nitrogen to leak check the system but I could not find any leaks in the system and it held the 250pounds of nitrogen. I released the nitrogen out of the system and then I put the system in a vacuum and it pulled down to 250microns and it held the vacuum of 250microns for one hour. After that I charged the unit with 5LBS of refrigerant R-420A and the unit is running fine and taking care of the load it is trying to satisfy in the clean room. I used 5LBS of refrigerant R-420A from refrigerant drum DR122013-4 - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-15 | 25349 | TMPE-224808 | TRANSFER TO HVAC Please create a WO for HVAC to check on this issue. The BT stated that the vibration is pretty extreme in this room *original message** !! there are high frequency and low frequency sound in my room ERC 419. It sounds like and AC pipe vibration or light harmonic balancer proble. . . | 2017-03-23 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 18010 - Jose Lopez-unable to find any problems with unit,talk to customer explained what i did.if problem come back he is going to call again. - Jose Lopez | TRANSFER TO HVAC Please create a WO for HVAC to check on this issue. The BT stated that the vibration is pretty extreme in this room *original message** !! there are high frequency and low frequency sound in my room ERC 419. It sounds like and AC pipe vibration or light harmonic balancer proble. . . 2017-03-23 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-03-24 - 18010 - Jose Lopez-unable to find any problems with unit,talk to customer explained what i did.if problem come back he is going to call again. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-15 | 25361 | TMPE-224796 | GHALL 145 The AC is not working. Can someone please be sent out to fix this? Thank you. 4O25GF6 | 2017-03-22 - 18290 - Jennifer Moyer-Replaced motor and cleaned coil. Coil was completely plugged. - Jennifer Moyer; 2017-03-22 - 18290 - Midhat Mukanovic-Replaced motor and cleaned coil. Coil was completely plugged. - Jennifer Moyer; 2017-03-22 - 18290 - Jennifer Moyer-Complete cleaning and install - Jennifer Moyer; 2017-03-22 - 18290 - No temperature regulation. The water valve for this unit is open all the time and there is no way to set the temperature of the room. To fix this, the fan coil would need to be rewired and the water valve changed to 110 as there is no drop in replacement for this thermostat. This would be costly. Customer is pleased with the operation of the unit and the unit does function. No further action at this time. - Jennifer Moyer | GHALL 145 The AC is not working. Can someone please be sent out to fix this? Thank you. 4O25GF6 2017-03-22 - 18290 - Jennifer Moyer-Replaced motor and cleaned coil. Coil was completely plugged. - Jennifer Moyer; 2017-03-22 - 18290 - Midhat Mukanovic-Replaced motor and cleaned coil. Coil was completely plugged. - Jennifer Moyer; 2017-03-22 - 18290 - Jennifer Moyer-Complete cleaning and install - Jennifer Moyer; 2017-03-22 - 18290 - No temperature regulation. The water valve for this unit is open all the time and there is no way to set the temperature of the room. To fix this, the fan coil would need to be rewired and the water valve changed to 110 as there is no drop in replacement for this thermostat. This would be costly. Customer is pleased with the operation of the unit and the unit does function. No further action at this time. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-03-15 | 25363 | TMPE-224794 | The AC is not working. Can someone please be sent out to fix this? Thank you. 4O25GF6 Per HVAC Tech Jennifer Moyer. Steam valve needs to be shut-down. Transfer to plumbing. | 2017-03-20 - 18010 - Please disregard. Wojciech just informed me that they already have a work order for this. Brian - Juliana Blusiewicz | The AC is not working. Can someone please be sent out to fix this? Thank you. 4O25GF6 Per HVAC Tech Jennifer Moyer. Steam valve needs to be shut-down. Transfer to plumbing. 2017-03-20 - 18010 - Please disregard. Wojciech just informed me that they already have a work order for this. Brian - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-03-15 | 25379 | TMPE-224778 | !! Our air compressor isn't working properly. We've noticed it's turning on at 65 when it should be turning on around 80-85. 4O6N9AA | 2017-03-21 - 18030 - Brian Qualls-Found #2 motor had tripped O/L. O/L were set 21amps, motor FLA is 21 also. This is marginal for heavy load, restarts. Maybe cause for nuisance failures. Adjusted O/L to 24amps. All is good. - Brian Qualls | !! Our air compressor isn't working properly. We've noticed it's turning on at 65 when it should be turning on around 80-85. 4O6N9AA 2017-03-21 - 18030 - Brian Qualls-Found #2 motor had tripped O/L. O/L were set 21amps, motor FLA is 21 also. This is marginal for heavy load, restarts. Maybe cause for nuisance failures. Adjusted O/L to 24amps. All is good. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 25405 | TMPE-224752 | MU - POD Market: the reach in cooler at grab & go temps ok on the bottom but temping at 61 on the top. | 2017-03-17 - 18100 - Gail Jackson-Found 2 condenser fan motors burned out, 1 evap fan burned out and condenser coil very dirty. - Gail Jackson; 2017-03-17 - 18100 - Gail Jackson-Trip to Johnstone for Condenser fan motors; back to MU POD and installed and cleaned coil. Called MFG, motor discontinued, a replacement is available through them. - Gail Jackson; 2017-03-17 - 18100 - Thomas Gibble-Trip to Johnstone for Condenser fan motors; back to MU POD and installed and cleaned coil. Called MFG, motor discontinued, a replacement is available through them. - Gail Jackson; 2017-03-28 - 18100 - Gail Jackson-Install evap fan motor. Run test complete. - Gail Jackson; 2017-03-28 - 18100 - Thomas Gibble-Install evap fan motor. Run test complete. - Gail Jackson | MU - POD Market: the reach in cooler at grab & go temps ok on the bottom but temping at 61 on the top. 2017-03-17 - 18100 - Gail Jackson-Found 2 condenser fan motors burned out, 1 evap fan burned out and condenser coil very dirty. - Gail Jackson; 2017-03-17 - 18100 - Gail Jackson-Trip to Johnstone for Condenser fan motors; back to MU POD and installed and cleaned coil. Called MFG, motor discontinued, a replacement is available through them. - Gail Jackson; 2017-03-17 - 18100 - Thomas Gibble-Trip to Johnstone for Condenser fan motors; back to MU POD and installed and cleaned coil. Called MFG, motor discontinued, a replacement is available through them. - Gail Jackson; 2017-03-28 - 18100 - Gail Jackson-Install evap fan motor. Run test complete. - Gail Jackson; 2017-03-28 - 18100 - Thomas Gibble-Install evap fan motor. Run test complete. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-15 | 25406 | TMPE-224751 | Sonora Market - the reach in cooler that was worked on last week is making an extremely loud noise. | 2017-03-17 - 18240 - Gail Jackson-Found power cord contacting fan blade, adjusted and fastened. Run test. - Gail Jackson; 2017-03-17 - 18240 - Thomas Gibble-Found power cord contacting fan blade, adjusted and fastened. Run test. - Gail Jackson | Sonora Market - the reach in cooler that was worked on last week is making an extremely loud noise. 2017-03-17 - 18240 - Gail Jackson-Found power cord contacting fan blade, adjusted and fastened. Run test. - Gail Jackson; 2017-03-17 - 18240 - Thomas Gibble-Found power cord contacting fan blade, adjusted and fastened. Run test. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-15 | 230421 | POLY-117777 | Quad 1 AC has stopped working. Was reported that the AC pipe outside was completely frozen. **Called Steve and let him know about the issue.** | 2017-03-20 - 18010 - Steve Clark-found indoor coil frozen over - a/h was not working - condenser was operating - Steve Clark; 2017-03-20 - 18010 - Allan Blair-3/16 unit was working when I arrived - checked over unit - thermostat acted up when I was there- need to replace t'stat 3/17 - replace t'stat - checked unit a couple of times that day and each time unit was satisfied at set point temp (74deg) - Steve Clark; 2017-03-20 - 18010 - Allan Blair-3/16 unit was working when I arrived - checked over unit - thermostat acted up when I was there- need to replace t'stat 3/17 - replace t'stat - checked unit a couple of times that day and each time unit was satisfied at set point temp (74deg) - Steve Clark | Quad 1 AC has stopped working. Was reported that the AC pipe outside was completely frozen. **Called Steve and let him know about the issue.** 2017-03-20 - 18010 - Steve Clark-found indoor coil frozen over - a/h was not working - condenser was operating - Steve Clark; 2017-03-20 - 18010 - Allan Blair-3/16 unit was working when I arrived - checked over unit - thermostat acted up when I was there- need to replace t'stat 3/17 - replace t'stat - checked unit a couple of times that day and each time unit was satisfied at set point temp (74deg) - Steve Clark; 2017-03-20 - 18010 - Allan Blair-3/16 unit was working when I arrived - checked over unit - thermostat acted up when I was there- need to replace t'stat 3/17 - replace t'stat - checked unit a couple of times that day and each time unit was satisfied at set point temp (74deg) - Steve Clark | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26149 | TMPE-224008 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26150 | TMPE-224007 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26151 | TMPE-224006 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26152 | TMPE-224005 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26153 | TMPE-224004 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26154 | TMPE-224003 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-15 | 26155 | TMPE-224002 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-16 | 208450 | RAMA-100814 | !! Air conditioner is out 4NF7BC8 | NA | !! Air conditioner is out 4NF7BC8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-16 | 210950 | RACC-117660 | AC unit between room A and B is leaking. Room A shower drain is clogged (put in request separately as well) Thank you in advance! 4NFA0DA | NA | AC unit between room A and B is leaking. Room A shower drain is clogged (put in request separately as well) Thank you in advance! 4NFA0DA NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-16 | 25096 | TMPE-225061 | MU POD Hi Please create a work order to have someone fix the air screen cooler in the MU POD It is running warm Location Memorial Union First Floor Charge to GN7 | 2017-03-28 - 18100 - Gail Jackson-Washed condenser coil in Outta Here Grab and Go. We previously replaced cond. fan motor in this unit. We checked because they said it was not cooling properly. We put time on unit in MU POD. Washed coil this day because plugged. Complete - Gail Jackson; 2017-03-28 - 18100 - Thomas Gibble-Washed condenser coil in Outta Here Grab and Go. We previously replaced cond. fan motor in this unit. We checked because they said it was not cooling properly. We put time on unit in MU POD. Washed coil this day because plugged. Complete - Gail Jackson | MU POD Hi Please create a work order to have someone fix the air screen cooler in the MU POD It is running warm Location Memorial Union First Floor Charge to GN7 2017-03-28 - 18100 - Gail Jackson-Washed condenser coil in Outta Here Grab and Go. We previously replaced cond. fan motor in this unit. We checked because they said it was not cooling properly. We put time on unit in MU POD. Washed coil this day because plugged. Complete - Gail Jackson; 2017-03-28 - 18100 - Thomas Gibble-Washed condenser coil in Outta Here Grab and Go. We previously replaced cond. fan motor in this unit. We checked because they said it was not cooling properly. We put time on unit in MU POD. Washed coil this day because plugged. Complete - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-16 | 25107 | TMPE-225050 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-05-18 - 18100 - Michael Kelley-assisted contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-05-18 - 18100 - Michael Kelley-assisted contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25108 | TMPE-225049 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-05-18 - 18100 - Michael Kelley-Asisted contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-05-18 - 18100 - Michael Kelley-Asisted contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25109 | TMPE-225048 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-05-18 - 18100 - Michael Kelley-assited contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-05-18 - 18100 - Michael Kelley-assited contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25110 | TMPE-225047 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-05-18 - 18100 - Michael Kelley-assisted contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-05-18 - 18100 - Michael Kelley-assisted contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25111 | TMPE-225046 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-05-18 - 18100 - Michael Kelley-opened doors - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-05-18 - 18100 - Michael Kelley-opened doors - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25112 | TMPE-225045 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25113 | TMPE-225044 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-05-05 - 18100 - Michael Kelley-Assisted contractor roofer getg on roof - Michael Kelley; 2017-05-18 - 18100 - Michael Kelley-opened doors for contractor - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-Assisted contractor - Michael Kelley; 2017-05-05 - 18100 - Michael Kelley-Assisted contractor roofer getg on roof - Michael Kelley; 2017-05-18 - 18100 - Michael Kelley-opened doors for contractor - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25114 | TMPE-225043 | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . | 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-27 - 18100 - Michael Kelley-stopped checked out evap coolers. Told contractor to lable units. all look good - Michael Kelley; 2017-05-05 - 18100 - Michael Kelley-checked job. found no problem - Michael Kelley; 2017-05-18 - 18100 - Michael Kelley-Job walk - Michael Kelley | SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Proposed to route the condensate drain lin. . . 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-17 - 18100 - Michael Kelley-assisted contractor with doors. - Michael Kelley; 2017-04-27 - 18100 - Michael Kelley-stopped checked out evap coolers. Told contractor to lable units. all look good - Michael Kelley; 2017-05-05 - 18100 - Michael Kelley-checked job. found no problem - Michael Kelley; 2017-05-18 - 18100 - Michael Kelley-Job walk - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-16 | 25133 | TMPE-225024 | CNTRPT 312-22 Need to add supply air registers and ductwork per Zhi. The HVAC system is really loud. Can someone come by to see if there is anything wrong, and try to quiet it? Thank you! 4NF62MD | 2017-03-23 - 18010 - Zhi Yu-The air come form register are whistling and unit pulsing . This unit are over size, feeding two office room about 14x16. We need relief some of the air pressure, We have decided to add 4 more supplies. - Zhi Yu; 2017-03-28 - 18010 - Zhi Yu-Schedule with Karen. - Zhi Yu; 2017-04-04 - 18010 - Zhi Yu-Relocated 2 room register and add new register to distributed air evenly. - Zhi Yu; 2017-04-04 - 18010 - Mitchell Andrews-Relocated 2 room register and add new register to distributed air evenly. - Zhi Yu | CNTRPT 312-22 Need to add supply air registers and ductwork per Zhi. The HVAC system is really loud. Can someone come by to see if there is anything wrong, and try to quiet it? Thank you! 4NF62MD 2017-03-23 - 18010 - Zhi Yu-The air come form register are whistling and unit pulsing . This unit are over size, feeding two office room about 14x16. We need relief some of the air pressure, We have decided to add 4 more supplies. - Zhi Yu; 2017-03-28 - 18010 - Zhi Yu-Schedule with Karen. - Zhi Yu; 2017-04-04 - 18010 - Zhi Yu-Relocated 2 room register and add new register to distributed air evenly. - Zhi Yu; 2017-04-04 - 18010 - Mitchell Andrews-Relocated 2 room register and add new register to distributed air evenly. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-03-16 | 25189 | TMPE-224968 | SW Water Softening repaired bad solenoid valve on unit #3. | NA | SW Water Softening repaired bad solenoid valve on unit #3. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-03-16 | 25214 | TMPE-224943 | CP 102 !! FACMAN - The circulating pump on the DHW boiler that was installed a month ago by your department (mechanical) has failed. I need emergency service to fix this situation and get this boiler operating. If you have any questions, please do not hesitate to contact me at 602-694-3087. Bill . . . | 2017-03-17 - 23020 - Thomas Gibble-replaced motor from DW boiler #2 to DW boiler #1. - Thomas Gibble; 2017-03-17 - 23020 - Derek Gittings-replaced motor from DW boiler #2 to DW boiler #1. - Thomas Gibble | CP 102 !! FACMAN - The circulating pump on the DHW boiler that was installed a month ago by your department (mechanical) has failed. I need emergency service to fix this situation and get this boiler operating. If you have any questions, please do not hesitate to contact me at 602-694-3087. Bill . . . 2017-03-17 - 23020 - Thomas Gibble-replaced motor from DW boiler #2 to DW boiler #1. - Thomas Gibble; 2017-03-17 - 23020 - Derek Gittings-replaced motor from DW boiler #2 to DW boiler #1. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-17 | 1267 | WEST-109982 | Perform equipment data info gathering for SDFC. | 2017-03-17 - 10010 - Chad T Ball-confirm equipment inventory on air handlers, split system heat pumps, exhaust fans, boilers, hot water pumps. - Chad T Ball; 2017-03-17 - 10010 - Joseph McCormick-Gathered info as to equipment list from WEBTMA to the actual equipment in the building. Found 8 pumps and motors in the second floor EQ room that are not listed and three in pool pump house. Reported to Jim of discrepancies. - Joseph McCormick; 2017-03-17 - 10010 - Donald Miller-Walked through center inventorying equipment and verifying with TMA. - Donald Miller; 2017-03-23 - 10010 - Chad T Ball-Updating equipment inventory list - Chad T Ball; 2017-03-23 - 10010 - Joseph McCormick-Spent two hours organizing and transcribing equipment info for bldg heat, domestic water heating and solar heat exchange systems. Found out that has been done. Need to do pool pump house eqipment. Spent two hours doing that. Found out that the info will be added directly by boss. No need to fill out WEBTMA equipment data sheets. - Joseph McCormick; 2017-03-28 - 10010 - Ronald Chaffee-Gathering info and pictures of solar heating equipment. - Ronald Chaffee; 2017-05-08 - 10010 - Thomas Wienand-Lost ability to add equipment will work with Catherine. - Thomas Wienand | Perform equipment data info gathering for SDFC. 2017-03-17 - 10010 - Chad T Ball-confirm equipment inventory on air handlers, split system heat pumps, exhaust fans, boilers, hot water pumps. - Chad T Ball; 2017-03-17 - 10010 - Joseph McCormick-Gathered info as to equipment list from WEBTMA to the actual equipment in the building. Found 8 pumps and motors in the second floor EQ room that are not listed and three in pool pump house. Reported to Jim of discrepancies. - Joseph McCormick; 2017-03-17 - 10010 - Donald Miller-Walked through center inventorying equipment and verifying with TMA. - Donald Miller; 2017-03-23 - 10010 - Chad T Ball-Updating equipment inventory list - Chad T Ball; 2017-03-23 - 10010 - Joseph McCormick-Spent two hours organizing and transcribing equipment info for bldg heat, domestic water heating and solar heat exchange systems. Found out that has been done. Need to do pool pump house eqipment. Spent two hours doing that. Found out that the info will be added directly by boss. No need to fill out WEBTMA equipment data sheets. - Joseph McCormick; 2017-03-28 - 10010 - Ronald Chaffee-Gathering info and pictures of solar heating equipment. - Ronald Chaffee; 2017-05-08 - 10010 - Thomas Wienand-Lost ability to add equipment will work with Catherine. - Thomas Wienand | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-03-17 | 24974 | TMPE-225183 | TRANSFER TO HVAC Please transfer this work order to the HVAC shop. There is an air handler in the ceiling space out in front of the server room entry door that leaks water because there is no tee and vent in the condensate drain line to prevent the pan from overflowing. Please install a 3/4\\u2019\\u2019 cop. . . | 2017-03-22 - 23040 - Zhi Yu-Arrived at university center B. NO condensation leak at the time of arrival. There is Tee vent 3' after p-trap, Will need the electrician the removed MC wire , install disconnect and relocate feed. - Zhi Yu; 2017-03-24 - 23040 - CALLED TO JOHN H. LORIE GOODIN CALLED AND SAID IT'S ACTIVELY LEAKING. MM - Monica Moraga; 2017-05-11 - 23040 - Zhi Yu-Add electrician to replace MC to EMT from panel unit and disconnect. - Zhi Yu | TRANSFER TO HVAC Please transfer this work order to the HVAC shop. There is an air handler in the ceiling space out in front of the server room entry door that leaks water because there is no tee and vent in the condensate drain line to prevent the pan from overflowing. Please install a 3/4\\u2019\\u2019 cop. . . 2017-03-22 - 23040 - Zhi Yu-Arrived at university center B. NO condensation leak at the time of arrival. There is Tee vent 3' after p-trap, Will need the electrician the removed MC wire , install disconnect and relocate feed. - Zhi Yu; 2017-03-24 - 23040 - CALLED TO JOHN H. LORIE GOODIN CALLED AND SAID IT'S ACTIVELY LEAKING. MM - Monica Moraga; 2017-05-11 - 23040 - Zhi Yu-Add electrician to replace MC to EMT from panel unit and disconnect. - Zhi Yu | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-17 | 25029 | TMPE-225128 | Pueblo Mechanical to provide and install (2) new Daikin split system for elevator equipment rooms. \\uf0b7 2 ton split systems \\uf0b7 Wall mount AHU. \\uf0b7 Straight Cool \\uf0b7 New condensers to be roof mounted on new C-port and unistrut stands. \\uf0b7 Provide and install new condensate lines to nearest termination. \\uf0b7. . . | 2017-05-05 - 18050 - Michael Kelley-Let contractor in roof equipment room. got fire tec s on the job to turn of detectors - Michael Kelley; 2017-05-05 - 18050 - Michael Kelley-contractor assist - Michael Kelley; 2017-05-05 - 18050 - Michael Kelley-Checked job. contractor done. - Michael Kelley; 2017-05-18 - 18050 - Michael Kelley-job walk contractor - Michael Kelley; 2017-05-18 - 18050 - Michael Kelley-opened doors done - Michael Kelley | Pueblo Mechanical to provide and install (2) new Daikin split system for elevator equipment rooms. \\uf0b7 2 ton split systems \\uf0b7 Wall mount AHU. \\uf0b7 Straight Cool \\uf0b7 New condensers to be roof mounted on new C-port and unistrut stands. \\uf0b7 Provide and install new condensate lines to nearest termination. \\uf0b7. . . 2017-05-05 - 18050 - Michael Kelley-Let contractor in roof equipment room. got fire tec s on the job to turn of detectors - Michael Kelley; 2017-05-05 - 18050 - Michael Kelley-contractor assist - Michael Kelley; 2017-05-05 - 18050 - Michael Kelley-Checked job. contractor done. - Michael Kelley; 2017-05-18 - 18050 - Michael Kelley-job walk contractor - Michael Kelley; 2017-05-18 - 18050 - Michael Kelley-opened doors done - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-17 | 25066 | TMPE-225091 | VDD !! The AC is not on in the VDD. This is urgent. PO is YG202004944. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF | 2017-03-20 - 18290 - Robert Dauscher-checked condensers --- north units not calling for cooling.. contacted EMS Tech who said AH was not able to run... found blown fuse in disconnect box. Replaced with Temporary fuse to bring AH back online. Need to pick up 3 Fuses on Monday ad return to install. - Robert Dauscher; 2017-03-20 - 18290 - Robert Dauscher-Returned Monday after picking up 3 new fuses. installed new fuses(placed date 3-20-17 on all 3) unit working ok Elect. said he will call us out when he transfers power again to see if it was the problem which caused the fuse to fail. - Robert Dauscher; 2017-04-10 - 18290 - Nicholas Sizow-North AC unit trips on overload. Call transferred to AC Shop. - Nicholas Sizow | VDD !! The AC is not on in the VDD. This is urgent. PO is YG202004944. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.Wozniak@asu.edu 42BDEDF 2017-03-20 - 18290 - Robert Dauscher-checked condensers --- north units not calling for cooling.. contacted EMS Tech who said AH was not able to run... found blown fuse in disconnect box. Replaced with Temporary fuse to bring AH back online. Need to pick up 3 Fuses on Monday ad return to install. - Robert Dauscher; 2017-03-20 - 18290 - Robert Dauscher-Returned Monday after picking up 3 new fuses. installed new fuses(placed date 3-20-17 on all 3) unit working ok Elect. said he will call us out when he transfers power again to see if it was the problem which caused the fuse to fail. - Robert Dauscher; 2017-04-10 - 18290 - Nicholas Sizow-North AC unit trips on overload. Call transferred to AC Shop. - Nicholas Sizow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-17 | 25086 | TMPE-225071 | Top of the morning to you and Happy St, Patrick's Day. For Old Main critical communications rooms, 138 and 139. We have 5 chilled water (CRAC) A/C units, two in 139 and three in 138. We would like the A/C shop to clean coils, fix any issues they find, do a full preventive maintenance inspection. . . . | 2017-03-31 - 18090 - Gail Jackson-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. Belimo damper motor disconnected at plenum and electronic actuator bypassed, no control by EMS. - Gail Jackson [Modified: 2017-03-31 Gail Jackson]; 2017-03-31 - 18090 - Zhi Yu-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. - Gail Jackson; 2017-03-31 - 18090 - Midhat Mukanovic-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. - Gail Jackson; 2017-04-04 - 18090 - Zhi Yu-Will Have DPair give us estimate on repair and new unit. - Zhi Yu; 2017-04-04 - 18090 - Gail Jackson-Will Have DPair give us estimate on repair and new unit. - Zhi Yu | Top of the morning to you and Happy St, Patrick's Day. For Old Main critical communications rooms, 138 and 139. We have 5 chilled water (CRAC) A/C units, two in 139 and three in 138. We would like the A/C shop to clean coils, fix any issues they find, do a full preventive maintenance inspection. . . . 2017-03-31 - 18090 - Gail Jackson-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. Belimo damper motor disconnected at plenum and electronic actuator bypassed, no control by EMS. - Gail Jackson [Modified: 2017-03-31 Gail Jackson]; 2017-03-31 - 18090 - Zhi Yu-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. - Gail Jackson; 2017-03-31 - 18090 - Midhat Mukanovic-Inspect all 5 Liebert Units in communication rooms 138 and 139 found that all humidifiers leak, badly corroded and all sheaves need replaced and 2 condensate pumps. - Gail Jackson; 2017-04-04 - 18090 - Zhi Yu-Will Have DPair give us estimate on repair and new unit. - Zhi Yu; 2017-04-04 - 18090 - Gail Jackson-Will Have DPair give us estimate on repair and new unit. - Zhi Yu | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8
2017-03-17 | 250691 | DTPC-117847 | Sink not working in 211W1. | 2017-03-17 - 23070 - Ross Hossack-Replaced bad valve module. - Ross Hossack | Sink not working in 211W1. 2017-03-17 - 23070 - Ross Hossack-Replaced bad valve module. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-03-18 | 166121 | RFMT-142210 | !! Repeat Request. Ac not working 4O0LMJ9 | 2017-03-20 - 18010 - Thomas Zambrano-flushed unit out 2 times already and the coil is still clogging up. need HVAC to blow out chiller lines. - Thomas Zambrano; 2017-03-21 - 18010 - Thomas Zambrano-called tony m. to make work order for clogged coil. - Thomas Zambrano | !! Repeat Request. Ac not working 4O0LMJ9 2017-03-20 - 18010 - Thomas Zambrano-flushed unit out 2 times already and the coil is still clogging up. need HVAC to blow out chiller lines. - Thomas Zambrano; 2017-03-21 - 18010 - Thomas Zambrano-called tony m. to make work order for clogged coil. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-18 | 166128 | RFMT-142203 | !! AC does not blow out cold air. The fan is working but the room is very hot despite changing the thermostat number. 4NJK5B9 | 2017-03-20 - 18010 - Thor Millsaps-Repaired open low voltage circuit. System up and running. - Thor Millsaps | !! AC does not blow out cold air. The fan is working but the room is very hot despite changing the thermostat number. 4NJK5B9 2017-03-20 - 18010 - Thor Millsaps-Repaired open low voltage circuit. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-18 | 166129 | RFMT-142202 | !! Is there anyway we can get Alpha Chi Omegas patio power washed?There are nats because ice cream was left in a cooler and not there is an awful smell and there is gross stuff on the ground. We need something done please. 4NL4BF3 | 2017-03-24 - 14000 - Working with Carli Mercer need to charge fraternity for this room. - Yvette Castro; 2017-03-28 - 14000 - Please close out all remaining WO\\u2019s that were not turned in this earlier today. William Falkner - Yvette Castro | !! Is there anyway we can get Alpha Chi Omegas patio power washed?There are nats because ice cream was left in a cooler and not there is an awful smell and there is gross stuff on the ground. We need something done please. 4NL4BF3 2017-03-24 - 14000 - Working with Carli Mercer need to charge fraternity for this room. - Yvette Castro; 2017-03-28 - 14000 - Please close out all remaining WO\\u2019s that were not turned in this earlier today. William Falkner - Yvette Castro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-18 | 24242 | TMPE-225915 | ASUHC Agent: Spencer Leisy Description: University Building C, gate unlocked at 7:30 pm on the Northeast side of the building. Caller seemed unsure of who was supposed to test the AC. Who was dispatched: Time of Dispatch: 17:18: Left a message for the Standby contact Jennifer Moyer 17:40: Ca. . . | 2017-03-20 - 18010 - Roque Garcia-Spoke with Austin he is a third party contractor he needed to move the portable AC systems located near the generator. He needed somebody to unlock the gate. Austin stated this pm was scheduled three days prior. - Roque Garcia | ASUHC Agent: Spencer Leisy Description: University Building C, gate unlocked at 7:30 pm on the Northeast side of the building. Caller seemed unsure of who was supposed to test the AC. Who was dispatched: Time of Dispatch: 17:18: Left a message for the Standby contact Jennifer Moyer 17:40: Ca. . . 2017-03-20 - 18010 - Roque Garcia-Spoke with Austin he is a third party contractor he needed to move the portable AC systems located near the generator. He needed somebody to unlock the gate. Austin stated this pm was scheduled three days prior. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-03-19 | 1248 | WEST-110001 | HVAC-GENERAL-EVAP COOLER -WEST | 2017-03-23 - 18010 - Chad T Ball-Vacuumed inside of cabinet and water tray.Reconnected water supply, turned on water and filled water tray. Verified proper water level and operation of fill valve. Inspected drive belt, motor and pump. Ran unit to verify proper operation. - Chad T Ball | HVAC-GENERAL-EVAP COOLER -WEST 2017-03-23 - 18010 - Chad T Ball-Vacuumed inside of cabinet and water tray.Reconnected water supply, turned on water and filled water tray. Verified proper water level and operation of fill valve. Inspected drive belt, motor and pump. Ran unit to verify proper operation. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-03-19 | 1249 | WEST-110000 | HVAC-GENERAL-EVAP COOLER -EAST | 2017-03-23 - 18010 - Chad T Ball-Vacuumed inside of cabinet and water tray.Reconnected water supply, turned on water and filled water tray. Verified proper water level and operation of fill valve. Inspected drive belt, motor and pump. Ran unit to verify proper operation. - Chad T Ball | HVAC-GENERAL-EVAP COOLER -EAST 2017-03-23 - 18010 - Chad T Ball-Vacuumed inside of cabinet and water tray.Reconnected water supply, turned on water and filled water tray. Verified proper water level and operation of fill valve. Inspected drive belt, motor and pump. Ran unit to verify proper operation. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-03-19 | 1250 | WEST-109999 | HVAC-GENERAL-EVAP COOLER 6 | 2017-03-23 - 18010 - Ronald Chaffee-Already done reference w/o 109969 - Ronald Chaffee | HVAC-GENERAL-EVAP COOLER 6 2017-03-23 - 18010 - Ronald Chaffee-Already done reference w/o 109969 - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-19 | 1251 | WEST-109998 | HVAC-GENERAL-EVAP COOLER 5 | 2017-03-29 - 18010 - David Valentine-cleaned out, tightened electrical, replaced pump, greased fan, test ran ok. - David Valentine | HVAC-GENERAL-EVAP COOLER 5 2017-03-29 - 18010 - David Valentine-cleaned out, tightened electrical, replaced pump, greased fan, test ran ok. - David Valentine | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-19 | 1252 | WEST-109997 | HVAC-GENERAL-EVAP COOLER 4 | 2017-05-05 - 18010 - Joseph McCormick-Took Rodney Moore to bid on replacement of #2,3 and 4 evap coolers, as well as the two over at the tin shed. - Joseph McCormick; 2017-05-08 - 18010 - Thomas Wienand-this unit is on the replacement list due to condition - Thomas Wienand | HVAC-GENERAL-EVAP COOLER 4 2017-05-05 - 18010 - Joseph McCormick-Took Rodney Moore to bid on replacement of #2,3 and 4 evap coolers, as well as the two over at the tin shed. - Joseph McCormick; 2017-05-08 - 18010 - Thomas Wienand-this unit is on the replacement list due to condition - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-19 | 166115 | RFMT-142216 | !! Air conditioning not working properly, not blowing cool air 4NMBK3E | 2017-03-20 - 18010 - Salvatore Marasco Jr-Flushed coil with help from Thor. Temp. at coil read 65 dgrs. - Salvatore Marasco Jr; 2017-03-20 - 18010 - Thor Millsaps-Flushed coil with help from Thor. Temp. at coil read 65 dgrs. - Salvatore Marasco Jr | !! Air conditioning not working properly, not blowing cool air 4NMBK3E 2017-03-20 - 18010 - Salvatore Marasco Jr-Flushed coil with help from Thor. Temp. at coil read 65 dgrs. - Salvatore Marasco Jr; 2017-03-20 - 18010 - Thor Millsaps-Flushed coil with help from Thor. Temp. at coil read 65 dgrs. - Salvatore Marasco Jr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-19 | 210891 | RACC-117719 | The drain in the bathroom of suite B in room 3093 does not drain properly, and the vent above the bed may need to have a filter replaced because it does not properly allow air flow into the room. Contact Name: Contact Phone Number: 3077608474 Contact Email: 4NLE779 | NA | The drain in the bathroom of suite B in room 3093 does not drain properly, and the vent above the bed may need to have a filter replaced because it does not properly allow air flow into the room. Contact Name: Contact Phone Number: 3077608474 Contact Email: 4NLE779 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-20 | 1212 | WEST-110037 | Air Conditioning had broke in Co-Op. Uncertain reason; random occurrence. | 2017-03-21 - 18290 - Thomas Wienand-61 degree aux temp space is warm will have Chad follow up - Thomas Wienand; 2017-03-22 - 18290 - Chad T Ball-Troubleshoot and repair unit. Fan was not running. Fan belt had excessive wear. Replaced fan belt. Cycled TEC and found motor starter overload tripped. Reset motor starter and fan runs properly. Chilled water valve is working properly. Unit is blowing cold air. - Chad T Ball; 2017-03-22 - 18290 - Donald Miller-Assist with troubleshoot and repair. - Chad T Ball | Air Conditioning had broke in Co-Op. Uncertain reason; random occurrence. 2017-03-21 - 18290 - Thomas Wienand-61 degree aux temp space is warm will have Chad follow up - Thomas Wienand; 2017-03-22 - 18290 - Chad T Ball-Troubleshoot and repair unit. Fan was not running. Fan belt had excessive wear. Replaced fan belt. Cycled TEC and found motor starter overload tripped. Reset motor starter and fan runs properly. Chilled water valve is working properly. Unit is blowing cold air. - Chad T Ball; 2017-03-22 - 18290 - Donald Miller-Assist with troubleshoot and repair. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 4
2017-03-20 | 165952 | RFMT-142379 | Weekly Building PM Inspection. | 2017-03-24 - 50051 - John Romero-Looking for shut off valves for bathroom in the hub.. PV East. - John Romero; 2017-03-24 - 50051 - John Romero-Helped change out sinks and angle stop on restrooms in the hub. PV East - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds. Checked all common areas. - John Romero; 2017-03-24 - 50051 - John Romero-changed out A/C blower motor in laundry room E-616 - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds, checked all common areas. - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds, Checked all common areas, door,security lights, EQ rooms - John Romero; 2017-03-24 - 50051 - John Romero-Replaced lamp in security light.. - John Romero; 2017-03-24 - 50051 - John Romero-PV West. Walked with Bob form EMS checking temps in rooms. - John Romero | Weekly Building PM Inspection. 2017-03-24 - 50051 - John Romero-Looking for shut off valves for bathroom in the hub.. PV East. - John Romero; 2017-03-24 - 50051 - John Romero-Helped change out sinks and angle stop on restrooms in the hub. PV East - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds. Checked all common areas. - John Romero; 2017-03-24 - 50051 - John Romero-changed out A/C blower motor in laundry room E-616 - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds, checked all common areas. - John Romero; 2017-03-24 - 50051 - John Romero-Walked the building and grounds, Checked all common areas, door,security lights, EQ rooms - John Romero; 2017-03-24 - 50051 - John Romero-Replaced lamp in security light.. - John Romero; 2017-03-24 - 50051 - John Romero-PV West. Walked with Bob form EMS checking temps in rooms. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-03-20 | 166085 | RFMT-142246 | The elevator equipment AC is not cooling, resulting in elevator equipment not working. Please address immediately. Thank you. | 2017-03-23 - 18010 - Thor Millsaps-Reset breaker for elevator penthouse ac condenser. Compressor is hard-starting. Installed hard start kit. Forwarded model and serial so replacement compressor or condenser can be purchased. Condenser make- Carrier, model- 38ETG030300, product- 38ETG030-301, serial- 4405E47771 - Thor Millsaps | The elevator equipment AC is not cooling, resulting in elevator equipment not working. Please address immediately. Thank you. 2017-03-23 - 18010 - Thor Millsaps-Reset breaker for elevator penthouse ac condenser. Compressor is hard-starting. Installed hard start kit. Forwarded model and serial so replacement compressor or condenser can be purchased. Condenser make- Carrier, model- 38ETG030300, product- 38ETG030-301, serial- 4405E47771 - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
2017-03-20 | 210828 | RACC-117782 | !! Air conditioning unit is broken. Needs to be fixed ASAP. 4NGJK4F | NA | !! Air conditioning unit is broken. Needs to be fixed ASAP. 4NGJK4F NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-20 | 24023 | TMPE-226134 | Environmental chamber not cooling down. Suspect Freon leak or low Freon in compressor. The machine is UTM-C. Can you please evaluate and repair? Please let me know if I need to provide a PO number for the requested work. Please see me and I can show you where the chamber is located in the lab. Thank. . . | 2017-03-22 - 18140 - Duane Rider-Check for leak, - Duane Rider | Environmental chamber not cooling down. Suspect Freon leak or low Freon in compressor. The machine is UTM-C. Can you please evaluate and repair? Please let me know if I need to provide a PO number for the requested work. Please see me and I can show you where the chamber is located in the lab. Thank. . . 2017-03-22 - 18140 - Duane Rider-Check for leak, - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-20 | 24184 | TMPE-225973 | SOCCER 115W1 !! The AC is not cooling in the Locker Room 115W1 at Soccer. PO is YG202004940. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Vujs@asu.edu 42BDEDF | 2017-03-24 - 18290 - Roque Garcia-Replaced the fuses, found the motor not operating, checked the amps on the motor and it was working to MFG specs. - Roque Garcia | SOCCER 115W1 !! The AC is not cooling in the Locker Room 115W1 at Soccer. PO is YG202004940. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Vujs@asu.edu 42BDEDF 2017-03-24 - 18290 - Roque Garcia-Replaced the fuses, found the motor not operating, checked the amps on the motor and it was working to MFG specs. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
2017-03-20 | 24206 | TMPE-225951 | My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. I currently do not have any AC in my office and it is starting to get warm. Is there a way to turn on the AC for my specific office. The id on the thermostat in my office is. . . | 2017-03-20 - 18290 - follow-up status email sent to HVAC (FF) - Francesca Fernandez; 2017-04-24 - 18290 - Carl Karr-Fabricate and install transition,repair duct work. - Carl Karr; 2017-04-25 - 18290 - Zhi Yu-Unit replacement. We disconnect all electrical, t/sat wire, water supply, return line and disconnect supply ducts. We have the Genie up and secure. We starting removed all thread and drop unit. We clean out the premises and put caution tape around it. - Zhi Yu; 2017-04-25 - 18290 - Mitchell Andrews-Unit replacement. We disconnect all electrical, t/sat wire, water supply, return line and disconnect supply ducts. We have the Genie up and secure. We starting removed all thread and drop unit. We clean out the premises and put caution tape around it. - Zhi Yu; 2017-04-25 - 18290 - Zhi Yu-The new unit is different. We have relocated the all thread by add u-channel. We have unit up and secure. Starting reconnect all electrical, Water supply and return. We have the fire tech Danny to turn-off fire alarm. so we can proceed soldering the condensation line. On the supply plenum have Carl make us an transition. Start-up unit and contact EMS back to normal set point. - Zhi Yu; 2017-04-25 - 18290 - Mitchell Andrews-The new unit is different. We have relocated the all thread by add u-channel. We have unit up and secure. Starting reconnect all electrical, Water supply and return. We have the fire tech Danny to turn-off fire alarm. so we can proceed soldering the condensation line. On the supply plenum have Carl make us an transition. Start-up unit and contact EMS back to normal set point. - Zhi Yu; 2017-04-26 - 18290 - Zhi Yu-We have an call yesterday Unit in 303 no working. Arrived the unit is off , we check the temp control lost signal. We bypass the control ,unit start to run in cool. We temporary install Beaburn non-programmable T/sat. - Zhi Yu; 2017-04-26 - 18290 - Michael Kelley-We have an call yesterday Unit in 303 no working. Arrived the unit is off , we check the temp control lost signal. We bypass the control ,unit start to run in cool. We temporary install Beaburn non-programmable T/sat. - Zhi Yu | My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. I currently do not have any AC in my office and it is starting to get warm. Is there a way to turn on the AC for my specific office. The id on the thermostat in my office is. . . 2017-03-20 - 18290 - follow-up status email sent to HVAC (FF) - Francesca Fernandez; 2017-04-24 - 18290 - Carl Karr-Fabricate and install transition,repair duct work. - Carl Karr; 2017-04-25 - 18290 - Zhi Yu-Unit replacement. We disconnect all electrical, t/sat wire, water supply, return line and disconnect supply ducts. We have the Genie up and secure. We starting removed all thread and drop unit. We clean out the premises and put caution tape around it. - Zhi Yu; 2017-04-25 - 18290 - Mitchell Andrews-Unit replacement. We disconnect all electrical, t/sat wire, water supply, return line and disconnect supply ducts. We have the Genie up and secure. We starting removed all thread and drop unit. We clean out the premises and put caution tape around it. - Zhi Yu; 2017-04-25 - 18290 - Zhi Yu-The new unit is different. We have relocated the all thread by add u-channel. We have unit up and secure. Starting reconnect all electrical, Water supply and return. We have the fire tech Danny to turn-off fire alarm. so we can proceed soldering the condensation line. On the supply plenum have Carl make us an transition. Start-up unit and contact EMS back to normal set point. - Zhi Yu; 2017-04-25 - 18290 - Mitchell Andrews-The new unit is different. We have relocated the all thread by add u-channel. We have unit up and secure. Starting reconnect all electrical, Water supply and return. We have the fire tech Danny to turn-off fire alarm. so we can proceed soldering the condensation line. On the supply plenum have Carl make us an transition. Start-up unit and contact EMS back to normal set point. - Zhi Yu; 2017-04-26 - 18290 - Zhi Yu-We have an call yesterday Unit in 303 no working. Arrived the unit is off , we check the temp control lost signal. We bypass the control ,unit start to run in cool. We temporary install Beaburn non-programmable T/sat. - Zhi Yu; 2017-04-26 - 18290 - Michael Kelley-We have an call yesterday Unit in 303 no working. Arrived the unit is off , we check the temp control lost signal. We bypass the control ,unit start to run in cool. We temporary install Beaburn non-programmable T/sat. - Zhi Yu | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2017-03-20 | 24278 | TMPE-225879 | ASUHC-Agent Max L. Description: Domestic hot water boiler out and cannot get it to come back on. Who was dispatched: Pete Sandoval Time of dispatch: 08:26pm ASUHC - Max L. Hassan called back and requested HVAC mechanical be sent to location. Called Roque Garcia, dispatched 08:49pm. | 2017-03-20 - 23020 - Roque Garcia-Found DHW pump working only problem was the pressure gauge. Cant replace gauge until the boiler is off due to the other boiler is locked out. Joe the building tech found the boiler in alarm at 8pm and reset all resettable buttons. Boiler was and still is working. - Roque Garcia | ASUHC-Agent Max L. Description: Domestic hot water boiler out and cannot get it to come back on. Who was dispatched: Pete Sandoval Time of dispatch: 08:26pm ASUHC - Max L. Hassan called back and requested HVAC mechanical be sent to location. Called Roque Garcia, dispatched 08:49pm. 2017-03-20 - 23020 - Roque Garcia-Found DHW pump working only problem was the pressure gauge. Cant replace gauge until the boiler is off due to the other boiler is locked out. Joe the building tech found the boiler in alarm at 8pm and reset all resettable buttons. Boiler was and still is working. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-03-20 | 230321 | POLY-117877 | !! Ac unit isn't cooling down air. AC also needs an airfilter and is missing screws. Contact Name: Raaqim Wright Contact Phone Number: (571)419-9802 Contact Email: raaqimw27@gmail.com 4NEAL36 | NA | !! Ac unit isn't cooling down air. AC also needs an airfilter and is missing screws. Contact Name: Raaqim Wright Contact Phone Number: (571)419-9802 Contact Email: raaqimw27@gmail.com 4NEAL36 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-20 | 250608 | DTPC-117930 | call back for crack dx unit no start | 2017-03-21 - 18050 - Steve Skibbe-checked out unit found oil on top of compressors preventing start so the internal over load is not its a external manual reset . Was told once again that the low charge could have created issue they will submit bid to top off or change out to new refrigerant. - Steve Skibbe | call back for crack dx unit no start 2017-03-21 - 18050 - Steve Skibbe-checked out unit found oil on top of compressors preventing start so the internal over load is not its a external manual reset . Was told once again that the low charge could have created issue they will submit bid to top off or change out to new refrigerant. - Steve Skibbe | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-20 | 250638 | DTPC-117900 | !! Hello, The air ducts have been pushing out a lot of black sticky material into the lab. It is coating the ceiling, walls and all the areas below the duct. This causes contamination with the media we use for our Microbiology labs. We cleaned these areas at the beginning of the semester. Attache. . . | 2017-03-21 - 18010 - Steve Skibbe-added filters rack to discharge on two drops - Steve Skibbe | !! Hello, The air ducts have been pushing out a lot of black sticky material into the lab. It is coating the ceiling, walls and all the areas below the duct. This causes contamination with the media we use for our Microbiology labs. We cleaned these areas at the beginning of the semester. Attache. . . 2017-03-21 - 18010 - Steve Skibbe-added filters rack to discharge on two drops - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-03-21 | 1203 | WEST-110046 | Garbage disposal is not working. Salvajor 2hp commercial disposer $1,723.14 2 1/2 hours GM labor 1 hour electrical labor. Ready to quote; RJ 04/04/2017 Emailed estimate to Greg Mauro. 4/4/17 CMR | 2017-03-22 - 23090 - Joseph Danielek-checked the fuses as per tim jowels request. fuses ok. looked at contacts on switch - Joseph Danielek; 2017-03-22 - 23090 - Joseph Danielek-got called by tim to check fuses again - fuses ok - checked voltage - ok. - Joseph Danielek; 2017-03-22 - 23090 - Joseph Danielek-add on notes: motor has a intermittent open winding that is getting worse. the unit ran fine but the open winding is presenting itself more often, getting worse. Also the bearings are getting rough increasing the vibration when it runs. - Joseph Danielek; 2017-03-23 - 23090 - Tim Jowers-priced out the disposal - Tim Jowers; 2017-03-23 - 23090 - Tim Jowers-checked the unit with Joe - Tim Jowers | Garbage disposal is not working. Salvajor 2hp commercial disposer $1,723.14 2 1/2 hours GM labor 1 hour electrical labor. Ready to quote; RJ 04/04/2017 Emailed estimate to Greg Mauro. 4/4/17 CMR 2017-03-22 - 23090 - Joseph Danielek-checked the fuses as per tim jowels request. fuses ok. looked at contacts on switch - Joseph Danielek; 2017-03-22 - 23090 - Joseph Danielek-got called by tim to check fuses again - fuses ok - checked voltage - ok. - Joseph Danielek; 2017-03-22 - 23090 - Joseph Danielek-add on notes: motor has a intermittent open winding that is getting worse. the unit ran fine but the open winding is presenting itself more often, getting worse. Also the bearings are getting rough increasing the vibration when it runs. - Joseph Danielek; 2017-03-23 - 23090 - Tim Jowers-priced out the disposal - Tim Jowers; 2017-03-23 - 23090 - Tim Jowers-checked the unit with Joe - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-03-21 | 165987 | RFMT-142344 | Please repair chiller water supply line to fan coil. | 2017-03-21 - 18010 - Dan Guerra-We went to unit#105 and checked out leak and found a 3/4" union leaking and shut off ball valve and Bill H. had Thor bring an A.C. unit over to unit#105 and will need to make this repair at summer break on chiller line. Mat. picked up at Ferguson 1-3/4" threaded ball valve 2-3/4"X 2 1/2" bass nipples 3-3/4"X 2" " " 2-3/4" bass 90s 1-3/4" " street 90 - Dan Guerra; 2017-03-21 - 18010 - Antonio Romero-We went to unit#105 and checked out leak and found a 3/4" union leaking and shut off ball valve and Bill H. had Thor bring an A.C. unit over to unit#105 and will need to make this repair at summer break on chiller line. Mat. picked up at Ferguson 1-3/4" threaded ball valve 2-3/4"X 2 1/2" bass nipples 3-3/4"X 2" " " 2-3/4" bass 90s 1-3/4" " street 90 - Dan Guerra; 2017-03-22 - 18010 - Repair work scheduled for summer break - Gregory Stetka | Please repair chiller water supply line to fan coil. 2017-03-21 - 18010 - Dan Guerra-We went to unit#105 and checked out leak and found a 3/4" union leaking and shut off ball valve and Bill H. had Thor bring an A.C. unit over to unit#105 and will need to make this repair at summer break on chiller line. Mat. picked up at Ferguson 1-3/4" threaded ball valve 2-3/4"X 2 1/2" bass nipples 3-3/4"X 2" " " 2-3/4" bass 90s 1-3/4" " street 90 - Dan Guerra; 2017-03-21 - 18010 - Antonio Romero-We went to unit#105 and checked out leak and found a 3/4" union leaking and shut off ball valve and Bill H. had Thor bring an A.C. unit over to unit#105 and will need to make this repair at summer break on chiller line. Mat. picked up at Ferguson 1-3/4" threaded ball valve 2-3/4"X 2 1/2" bass nipples 3-3/4"X 2" " " 2-3/4" bass 90s 1-3/4" " street 90 - Dan Guerra; 2017-03-22 - 18010 - Repair work scheduled for summer break - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-03-21 | 165997 | RFMT-142334 | Please fix the water (Evap) coolers in the warehouse. Its getting hot in there. | 2017-03-21 - 18010 - Thor Millsaps-Did start-up on all 10 coolers. Made sure water pumps are functioning properly, made sure water supply valves are open, made sure disconnects are in on position, made sure water nozzles are clear, made sure motors and belts are functioning properly, made sure side panels are secure, made sure float valves are in correct position, replaced one water pump, replaced one belt (6L196G, A95), replaced 3 fuses (FRS-R-20) - Thor Millsaps | Please fix the water (Evap) coolers in the warehouse. Its getting hot in there. 2017-03-21 - 18010 - Thor Millsaps-Did start-up on all 10 coolers. Made sure water pumps are functioning properly, made sure water supply valves are open, made sure disconnects are in on position, made sure water nozzles are clear, made sure motors and belts are functioning properly, made sure side panels are secure, made sure float valves are in correct position, replaced one water pump, replaced one belt (6L196G, A95), replaced 3 fuses (FRS-R-20) - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-03-21 | 210793 | RACC-117817 | !! To whom it may concern, My roommates and I are requesting an inspection/fixation of our air conditioning system because it's no longer running. When we turn the thermostat nothing happens. Also, our bathroom light went out. Much appreciated, Vanessa Ly 4NOOM3A | NA | !! To whom it may concern, My roommates and I are requesting an inspection/fixation of our air conditioning system because it's no longer running. When we turn the thermostat nothing happens. Also, our bathroom light went out. Much appreciated, Vanessa Ly 4NOOM3A NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-21 | 210804 | RACC-117806 | It seems the air conditioning may have been turned off in this room. They need it much cooler. 42BFD40 | NA | It seems the air conditioning may have been turned off in this room. They need it much cooler. 42BFD40 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-21 | 210865 | RACC-117745 | !! Repeat Request. The AC is broken, as even though the temperature is set at 70, the temperature has slowly climbed up to 80. The AC is on, when you look at the system control located in the bathroom, however the fans in either rooms don't provide any air conditioned cool air into the rooms. 4NO89OF | NA | !! Repeat Request. The AC is broken, as even though the temperature is set at 70, the temperature has slowly climbed up to 80. The AC is on, when you look at the system control located in the bathroom, however the fans in either rooms don't provide any air conditioned cool air into the rooms. 4NO89OF NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-03-21 | 23899 | TMPE-226258 | noisy outboard shaft bearing.(quieted down a little when greased.) | 2017-05-11 - 18050 - Thomas Gibble-checked out bearings and they sounded good - Thomas Gibble; 2017-05-11 - 18050 - Gail Jackson-checked out bearings and they sounded good - Thomas Gibble | noisy outboard shaft bearing.(quieted down a little when greased.) 2017-05-11 - 18050 - Thomas Gibble-checked out bearings and they sounded good - Thomas Gibble; 2017-05-11 - 18050 - Gail Jackson-checked out bearings and they sounded good - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-21 | 23969 | TMPE-226188 | IRISHA 124 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . | 2017-03-28 - 18290 - Jennifer Moyer-Replaced thermostat battery. - Jennifer Moyer; 2017-05-03 - 18290 - coil was cleaned and new filter installed. - Jennifer Moyer | IRISHA 124 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . 2017-03-28 - 18290 - Jennifer Moyer-Replaced thermostat battery. - Jennifer Moyer; 2017-05-03 - 18290 - coil was cleaned and new filter installed. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-03-21 | 24008 | TMPE-226149 | The air screen cooler in the MU POD is acting up again It is running warm Will you have the tech repair it please Charge to ARAMARK Gn7 | 2017-03-28 - 18100 - Gail Jackson-Jim Emmons put this work order in because he thought we were taking TOO LONG, he said he called outside company to do work, his assistant was informed of need to order OEM part. MAYBE WE SHOULD LOOK AT NEXT DAY AIR SHIPPING INSTEAD OF GROUND. - Gail Jackson | The air screen cooler in the MU POD is acting up again It is running warm Will you have the tech repair it please Charge to ARAMARK Gn7 2017-03-28 - 18100 - Gail Jackson-Jim Emmons put this work order in because he thought we were taking TOO LONG, he said he called outside company to do work, his assistant was informed of need to order OEM part. MAYBE WE SHOULD LOOK AT NEXT DAY AIR SHIPPING INSTEAD OF GROUND. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-22 | 165899 | RFMT-142432 | Joe please install temp a/c units in Adelphi II rooms U 206 & 208. A/C unit needs a new compressor. !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be f. . . | 2017-03-22 - 18010 - Joe Swan-Installed temporary A/C units in room - Joe Swan | Joe please install temp a/c units in Adelphi II rooms U 206 & 208. A/C unit needs a new compressor. !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be f. . . 2017-03-22 - 18010 - Joe Swan-Installed temporary A/C units in room - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-22 | 165903 | RFMT-142428 | !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be fixed soon as it is starting to get hot again. Side note I don't know what the number part of this request w. . . | 2017-03-23 - 18010 - Thor Millsaps-Replaced compressor, 35/5 mfd dual capacitor, liquid line filter dryer, condenser fan motor (1/4 HP 825 RPM), recovered 6.5 lbs R-22 and recharged back into system. System up and running. - Simon Fernandez | !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be fixed soon as it is starting to get hot again. Side note I don't know what the number part of this request w. . . 2017-03-23 - 18010 - Thor Millsaps-Replaced compressor, 35/5 mfd dual capacitor, liquid line filter dryer, condenser fan motor (1/4 HP 825 RPM), recovered 6.5 lbs R-22 and recharged back into system. System up and running. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-03-22 | 165913 | RFMT-142418 | !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be fixed soon as it is starting to get hot again. Side note I don't know what the number part of this request w. . . | 2017-03-23 - 18010 - David Cates-Compressor runs intermittently, called Greg to have Simon and Thor check the unit. Thor determined that the compressor is bad, and requested for Joe Swan to install portables in both rooms. - Gregory Stetka | !! Hello, I am a resident of the Adelphi II U cluster, room 206 and very recently our ac has stopped blowing cold air. This has made the room start to get too warm for comfort and needs to be fixed soon as it is starting to get hot again. Side note I don't know what the number part of this request w. . . 2017-03-23 - 18010 - David Cates-Compressor runs intermittently, called Greg to have Simon and Thor check the unit. Thor determined that the compressor is bad, and requested for Joe Swan to install portables in both rooms. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-22 | 20078 | TMPE-230079 | Toyota urgent safety recall national traffic and motor vehicle safety act. Power Window Master switch assembly which controls the driver and passenger windows is located in the driver door. These switches may have been manufactured with insufficient lubricant grease. | NA | Toyota urgent safety recall national traffic and motor vehicle safety act. Power Window Master switch assembly which controls the driver and passenger windows is located in the driver door. These switches may have been manufactured with insufficient lubricant grease. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-22 | 23719 | TMPE-226438 | ASUHC Agent: Justin Neel Description: water from the ceiling is dripping onto electrical wires inside the suite (304) Called Pete Wozniak at 700PM, advised I call HVAC Called Roque Garcia at 704PM, No answer, left message Called Roque Garcia Home Phone at 706PM, No answer, left message Called R. . . | 2017-03-23 - 18010 - Roque Garcia-The badge reader at the swing gate I had no access. The code to the elevator had been changed. So I took the stairs to the 4th floor and was able to access the elevator to the 6th floor. The air vent was leaking water by so I contacted plumbing and we both agreed to close the ball valve and replace the air vent the next morning. - Roque Garcia; 2017-03-23 - 18010 - Roque Garcia-2.5 hrs OT adjusted for 3-hr min-JG. - Jennifer Gorney | ASUHC Agent: Justin Neel Description: water from the ceiling is dripping onto electrical wires inside the suite (304) Called Pete Wozniak at 700PM, advised I call HVAC Called Roque Garcia at 704PM, No answer, left message Called Roque Garcia Home Phone at 706PM, No answer, left message Called R. . . 2017-03-23 - 18010 - Roque Garcia-The badge reader at the swing gate I had no access. The code to the elevator had been changed. So I took the stairs to the 4th floor and was able to access the elevator to the 6th floor. The air vent was leaking water by so I contacted plumbing and we both agreed to close the ball valve and replace the air vent the next morning. - Roque Garcia; 2017-03-23 - 18010 - Roque Garcia-2.5 hrs OT adjusted for 3-hr min-JG. - Jennifer Gorney | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-03-22 | 23745 | TMPE-226412 | Requesting service from FACMAN Mechanical Dept.. Please repair CHWP # 2 / Y-3902 in the Best C basement eq. rm.. Res. Life GMM Rick Miller has reported it is leaking and running louder than normal. Thank you. Submitted by 42DINIB | 2017-04-28 - 23100 - Jose Lopez-closed water,lock tag unit - Jose Lopez | Requesting service from FACMAN Mechanical Dept.. Please repair CHWP # 2 / Y-3902 in the Best C basement eq. rm.. Res. Life GMM Rick Miller has reported it is leaking and running louder than normal. Thank you. Submitted by 42DINIB 2017-04-28 - 23100 - Jose Lopez-closed water,lock tag unit - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-03-22 | 23839 | TMPE-226318 | Centerpoint HP4-9 (open office/RM436) Transferred to HVAC, HP4-9 is calling for cooling and is putting out 78 deg discharge temperature. !! We need someone to look at the A/C. The controls are reading that it's set to 74 but the temp shows 78.5. Hp4-9 ADD=12 HP4-13 ADD=16 42C4D5J | 2017-03-24 - 18290 - Roque Garcia-Replaced the contactor checked and tested good. The amps checked out good. - Roque Garcia | Centerpoint HP4-9 (open office/RM436) Transferred to HVAC, HP4-9 is calling for cooling and is putting out 78 deg discharge temperature. !! We need someone to look at the A/C. The controls are reading that it's set to 74 but the temp shows 78.5. Hp4-9 ADD=12 HP4-13 ADD=16 42C4D5J 2017-03-24 - 18290 - Roque Garcia-Replaced the contactor checked and tested good. The amps checked out good. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-22 | 23846 | TMPE-226311 | !! The cooling in the room has stopped and the room is very warm. The room use to be very cool. Please fix as soon as possible to avoid damage to research and equipment. Thank You 4O1GM1B | 2017-05-13 - 18290 - Robert Dauscher-found bad motor- no suitable replacement in parts room stock - Robert Dauscher; 2017-05-13 - 18290 - Robert Dauscher-picked up new motor and cap and installed - Robert Dauscher | !! The cooling in the room has stopped and the room is very warm. The room use to be very cool. Please fix as soon as possible to avoid damage to research and equipment. Thank You 4O1GM1B 2017-05-13 - 18290 - Robert Dauscher-found bad motor- no suitable replacement in parts room stock - Robert Dauscher; 2017-05-13 - 18290 - Robert Dauscher-picked up new motor and cap and installed - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-22 | 23854 | TMPE-226303 | Please send someone to WILSON HALL Food Service area called DAVES DOGS and CHICK IN It is very hot in these areas, it does not feel like the AC is coming on at all | 2017-03-27 - 18290 - Mitchell Andrews-unit had blown fuses on the transformer was tripped reset it and replaced the fuses - Mitchell Andrews | Please send someone to WILSON HALL Food Service area called DAVES DOGS and CHICK IN It is very hot in these areas, it does not feel like the AC is coming on at all 2017-03-27 - 18290 - Mitchell Andrews-unit had blown fuses on the transformer was tripped reset it and replaced the fuses - Mitchell Andrews | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-22 | 24895 | TMPE-225262 | Air Compressor-Biannual | 2017-03-23 - xPM-0100-B - Michael Bauer-replaced belt and oil,checked auto drain,air filter and operation. condition good. - Michael Bauer | Air Compressor-Biannual 2017-03-23 - xPM-0100-B - Michael Bauer-replaced belt and oil,checked auto drain,air filter and operation. condition good. - Michael Bauer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-22 | 24900 | TMPE-225257 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-22 | 24901 | TMPE-225256 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-22 | 24910 | TMPE-225247 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-22 | 230263 | POLY-117935 | Air filter replacement for HVAC system . 4NCGMFC | NA | Air filter replacement for HVAC system . 4NCGMFC NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-22 | 230269 | POLY-117929 | BILLED Steve - Can you take a look at the chiller at Palo Blanco asap? It is completely locked out, low oil pressure, compressors A & B will not start. CHARGE BACK STEVE'S LABOR TO RESIDENTIAL FACILITIES (JC5-7008) | 2017-04-05 - 18010 - Steve Clark-3/22 - STEVE (PFM) met with Charlie, and helped him ID the problem with the chiller (burnt board). - Gayle Swenson | BILLED Steve - Can you take a look at the chiller at Palo Blanco asap? It is completely locked out, low oil pressure, compressors A & B will not start. CHARGE BACK STEVE'S LABOR TO RESIDENTIAL FACILITIES (JC5-7008) 2017-04-05 - 18010 - Steve Clark-3/22 - STEVE (PFM) met with Charlie, and helped him ID the problem with the chiller (burnt board). - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-03-22 | 230273 | POLY-117925 | Water leaking from furnace when we turn on the A/C 4O0GF8D | NA | Water leaking from furnace when we turn on the A/C 4O0GF8D NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-22 | 230275 | POLY-117923 | !! Air conditioning broken 4O2D5EB | NA | !! Air conditioning broken 4O2D5EB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-22 | 250581 | DTPC-117957 | !! No air in 780F or 780G the entire week. 42B1674 | 2017-03-23 - 18290 - Steve Skibbe-found fan not running opened ceiling and unit found motor dead on med speed with jumper plug also the fire relay has power in no power out getting quotes on relay replacement and new motor - Steve Skibbe; 2017-03-23 - 18290 - Ross Hossack-found fan not running opened ceiling and unit found motor dead on med speed with jumper plug also the fire relay has power in no power out getting quotes on relay replacement and new motor - Steve Skibbe; 2017-04-05 - 18290 - Steve Skibbe-took down fan wall changed out motor will reinstall soon - Steve Skibbe; 2017-04-05 - 18290 - Robert Bartels-took down fan wall changed out motor will reinstall soon - Steve Skibbe; 2017-04-06 - 18290 - Steve Skibbe-put fan wall back in unit closed up unit and ceiling waiting on fire relay to start up unit - Steve Skibbe; 2017-04-13 - 18290 - Steve Skibbe-replaced pam relay checked operation of unit - Steve Skibbe; 2017-04-13 - 18290 - Bruce Pickford-replaced pam relay checked operation of unit - Steve Skibbe | !! No air in 780F or 780G the entire week. 42B1674 2017-03-23 - 18290 - Steve Skibbe-found fan not running opened ceiling and unit found motor dead on med speed with jumper plug also the fire relay has power in no power out getting quotes on relay replacement and new motor - Steve Skibbe; 2017-03-23 - 18290 - Ross Hossack-found fan not running opened ceiling and unit found motor dead on med speed with jumper plug also the fire relay has power in no power out getting quotes on relay replacement and new motor - Steve Skibbe; 2017-04-05 - 18290 - Steve Skibbe-took down fan wall changed out motor will reinstall soon - Steve Skibbe; 2017-04-05 - 18290 - Robert Bartels-took down fan wall changed out motor will reinstall soon - Steve Skibbe; 2017-04-06 - 18290 - Steve Skibbe-put fan wall back in unit closed up unit and ceiling waiting on fire relay to start up unit - Steve Skibbe; 2017-04-13 - 18290 - Steve Skibbe-replaced pam relay checked operation of unit - Steve Skibbe; 2017-04-13 - 18290 - Bruce Pickford-replaced pam relay checked operation of unit - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-23 | 1186 | WEST-110063 | Parking requested an inspection of the exhaust fan in this restroom. It is making a loud noise. | 2017-03-23 - 18160 - Chad T Ball-Troubleshoot noise. Found intermittent noise from motor. After removing belt found the bearings in the motor to be the problem. Removed motor from unit. Went to ARS to pick up a replacement. Installed replacement motor and replaced wiring harness from roof disconnect switch to motor. - Chad T Ball | Parking requested an inspection of the exhaust fan in this restroom. It is making a loud noise. 2017-03-23 - 18160 - Chad T Ball-Troubleshoot noise. Found intermittent noise from motor. After removing belt found the bearings in the motor to be the problem. Removed motor from unit. Went to ARS to pick up a replacement. Installed replacement motor and replaced wiring harness from roof disconnect switch to motor. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-23 | 165839 | RFMT-142492 | RES LIFE/ Chet: elevator lobby missing carpet transition strip and a/c wall pack near lobby, blowwing hot air | 2017-03-28 - 13000 - Chester Duncan-Re-glued transition strip Exercised actuators - Chester Duncan | RES LIFE/ Chet: elevator lobby missing carpet transition strip and a/c wall pack near lobby, blowwing hot air 2017-03-28 - 13000 - Chester Duncan-Re-glued transition strip Exercised actuators - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-23 | 18863 | TMPE-231294 | Naumann Hobbs Locate unit, found would not charge, rectifier bad. ordered part and returned to cart. Removed bed and covers. replaced rectifier and cleaned paint off of wires. total: 458.12 | NA | Naumann Hobbs Locate unit, found would not charge, rectifier bad. ordered part and returned to cart. Removed bed and covers. replaced rectifier and cleaned paint off of wires. total: 458.12 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-23 | 23599 | TMPE-226558 | CNTRPT 312-22 ADD CA : In room 312 the ceiling grid is sagging needs to be supported. There are also ceiling tiles missing, but may be in the room. Please talk to Mitch or Zhi. Need to add supply air registers and ductwork per Zhi. The HVAC system is really loud. Can someone come by to see. . . | 2017-03-27 - 13050 - Todd Green-In progress repaired ceiling grid materials ordered to replace broken ceiling tiles - Todd Green; 2017-03-28 - 13050 - Todd Green-Complete Replaced missing and damaged 24in x 24in ceiling tiles Replaced damaged cross T for ceiling grid - Todd Green | CNTRPT 312-22 ADD CA : In room 312 the ceiling grid is sagging needs to be supported. There are also ceiling tiles missing, but may be in the room. Please talk to Mitch or Zhi. Need to add supply air registers and ductwork per Zhi. The HVAC system is really loud. Can someone come by to see. . . 2017-03-27 - 13050 - Todd Green-In progress repaired ceiling grid materials ordered to replace broken ceiling tiles - Todd Green; 2017-03-28 - 13050 - Todd Green-Complete Replaced missing and damaged 24in x 24in ceiling tiles Replaced damaged cross T for ceiling grid - Todd Green | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 2
2017-03-23 | 23613 | TMPE-226544 | MCRD 1ST FL Please send someone out asap to check the air handler above the ceiling on the 1st floor hallway between rooms 170 & 176. It is very loud and sounds like it's off balance. | 2017-03-23 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2017-04-19 - 18010 - Roque Garcia-Replaced blower assy and placed wire screen to prevent insulation to be drawn into blower assy - Roque Garcia | MCRD 1ST FL Please send someone out asap to check the air handler above the ceiling on the 1st floor hallway between rooms 170 & 176. It is very loud and sounds like it's off balance. 2017-03-23 - 18010 - CALLED TO STEVE P. - Monica Moraga; 2017-04-19 - 18010 - Roque Garcia-Replaced blower assy and placed wire screen to prevent insulation to be drawn into blower assy - Roque Garcia | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-23 | 250544 | DTPC-117994 | Could we please have filters for the return air ducts in 365 and 360C. 42B55M9 | 2017-03-28 - 18170 - Steve Skibbe-showed Dominick from Dave downing he proposed that they clean the coils and units and use different filters that Kenny removed cause they were too expensive he also stated it may be easier to replace flex duct than clean it - Steve Skibbe; 2017-03-28 - 18170 - James Hermann-showed Dominick from Dave downing he proposed that they clean the coils and units and use different filters that Kenny removed cause they were too expensive he also stated it may be easier to replace flex duct than clean it - Steve Skibbe | Could we please have filters for the return air ducts in 365 and 360C. 42B55M9 2017-03-28 - 18170 - Steve Skibbe-showed Dominick from Dave downing he proposed that they clean the coils and units and use different filters that Kenny removed cause they were too expensive he also stated it may be easier to replace flex duct than clean it - Steve Skibbe; 2017-03-28 - 18170 - James Hermann-showed Dominick from Dave downing he proposed that they clean the coils and units and use different filters that Kenny removed cause they were too expensive he also stated it may be easier to replace flex duct than clean it - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-03-24 | 165796 | RFMT-142535 | !! Moldy smell, dirty air vents, very musty in the room 4O021N2 | 2017-03-27 - 18020 - Mike Guckian-i didn't smell anything. - Mike Guckian | !! Moldy smell, dirty air vents, very musty in the room 4O021N2 2017-03-27 - 18020 - Mike Guckian-i didn't smell anything. - Mike Guckian | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-24 | 165811 | RFMT-142520 | !! something has been leaking in the room for the past few days. The carpet is soaked. CALLED TO DALE H Submitted by 4NID637 | 2017-03-24 - 13050 - Rene Arrieta-replace all damaged tiles and set all a/c units t-stats - Rene Arrieta | !! something has been leaking in the room for the past few days. The carpet is soaked. CALLED TO DALE H Submitted by 4NID637 2017-03-24 - 13050 - Rene Arrieta-replace all damaged tiles and set all a/c units t-stats - Rene Arrieta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-24 | 165813 | RFMT-142518 | RES LIFE / Scott: Please clean bathroom vent, a/c wall pack / replace filter. Check for shower ceiling leak | 2017-03-24 - 18130 - Scott Berndt-cleaned the vent and a/c vents...replaced a/c filter...cut open the ceiling for Dan to replaced the p trap for the shower... - Scott Berndt | RES LIFE / Scott: Please clean bathroom vent, a/c wall pack / replace filter. Check for shower ceiling leak 2017-03-24 - 18130 - Scott Berndt-cleaned the vent and a/c vents...replaced a/c filter...cut open the ceiling for Dan to replaced the p trap for the shower... - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-24 | 23452 | TMPE-226705 | Hot water pump # 1 is leaking Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A | 2017-04-13 - 23100 - Derek Gittings-removing and pump,replacing seal and bearings. - Derek Gittings; 2017-05-16 - 23100 - Derek Gittings-droped motor off. - Derek Gittings | Hot water pump # 1 is leaking Contact Name: Contact Phone Number: 6023504317 Contact Email: 4N07O4A 2017-04-13 - 23100 - Derek Gittings-removing and pump,replacing seal and bearings. - Derek Gittings; 2017-05-16 - 23100 - Derek Gittings-droped motor off. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-24 | 23465 | TMPE-226692 | broken 3 groove motor sheave. running on 2 belts. | 2017-04-05 - 18050 - Jennifer Moyer-Located room (not numbered and located outside of the building, difficult to find). LOTO and measured sheaves for replacement. - Jennifer Moyer; 2017-05-11 - 18050 - Jennifer Moyer-Go over shut down procedure with LEAD. - Jennifer Moyer | broken 3 groove motor sheave. running on 2 belts. 2017-04-05 - 18050 - Jennifer Moyer-Located room (not numbered and located outside of the building, difficult to find). LOTO and measured sheaves for replacement. - Jennifer Moyer; 2017-05-11 - 18050 - Jennifer Moyer-Go over shut down procedure with LEAD. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-03-24 | 23539 | TMPE-226618 | Purchase Portable AC for ISTB-4 critical areas that do not have back up cooling. | NA | Purchase Portable AC for ISTB-4 critical areas that do not have back up cooling. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-24 | 23556 | TMPE-226601 | LSE subbasement: Booster pump #1 Y#7743 seal needs to be replaced. | 2017-03-24 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-07 - 18010 - Jose Lopez-lock and tag unit,closed water,disconnect pump,replaced bearings,shaft seal.clean &amp; paint pump,make gaskets.re assemble pump.check for leaks unit working @ this time. - Jose Lopez | LSE subbasement: Booster pump #1 Y#7743 seal needs to be replaced. 2017-03-24 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-03 - 18010 - Jose Lopez-work in progress - Jose Lopez; 2017-04-07 - 18010 - Jose Lopez-lock and tag unit,closed water,disconnect pump,replaced bearings,shaft seal.clean &amp; paint pump,make gaskets.re assemble pump.check for leaks unit working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-03-24 | 230190 | POLY-118008 | *** PLEASE ROUTE TO FRANK**** PLEASE CK TRUCK #9070 FOR EXCESS OIL USAGE 4O216EO | 2017-04-11 - 26000 - Frank Calderon Jr-4/10 - Frank replaced spark plugs in #9070, and conducted a cylinder compression test. - Gayle Swenson | *** PLEASE ROUTE TO FRANK**** PLEASE CK TRUCK #9070 FOR EXCESS OIL USAGE 4O216EO 2017-04-11 - 26000 - Frank Calderon Jr-4/10 - Frank replaced spark plugs in #9070, and conducted a cylinder compression test. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-03-24 | 250518 | DTPC-118020 | Chilled water pump 1B has a coupler that is deteriorating. | 2017-03-24 - 23100 - Ross Hossack-Looked up and found a replacement coupler.Ordered it. Contacted Emcor as they installed the motor and coupler less than 2 years ago.Tom came out and agreed to replace coupler and align the motor and pump on his dime. - Ross Hossack; 2017-03-31 - 23100 - Ross Hossack-Mike Robins with Emcor came out and found that the alignment for the motor is way off.He aligned the motor and replace the rubber bushing at there cost.NO CHARGE! - Ross Hossack | Chilled water pump 1B has a coupler that is deteriorating. 2017-03-24 - 23100 - Ross Hossack-Looked up and found a replacement coupler.Ordered it. Contacted Emcor as they installed the motor and coupler less than 2 years ago.Tom came out and agreed to replace coupler and align the motor and pump on his dime. - Ross Hossack; 2017-03-31 - 23100 - Ross Hossack-Mike Robins with Emcor came out and found that the alignment for the motor is way off.He aligned the motor and replace the rubber bushing at there cost.NO CHARGE! - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-25 | 22194 | TMPE-227963 | HC-Sofia G Humidifier not working in cleaning room 133 in Energy Research Building. Dispatched:Tom Gibble Time: 6:14 | 2017-03-28 - 18010 - Thomas Gibble-found bad fuse. 600 vac 40 amp. I could not find a fuse. I transfer to weekend worker. - Thomas Gibble | HC-Sofia G Humidifier not working in cleaning room 133 in Energy Research Building. Dispatched:Tom Gibble Time: 6:14 2017-03-28 - 18010 - Thomas Gibble-found bad fuse. 600 vac 40 amp. I could not find a fuse. I transfer to weekend worker. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-26 | 165770 | RFMT-142561 | !! Air unit is not working 4NJE2A5 | 2017-03-27 - 18010 - Salvatore Marasco Jr-Checked t-stat, could hear motor turn on but did not hear or feel the blower come on. Requested the A.C. tech. to make repair. - Salvatore Marasco Jr; 2017-03-27 - 18010 - Copied Res. Life HVAC tech on work order and contacted HVAC supervisor. - Gregory Stetka | !! Air unit is not working 4NJE2A5 2017-03-27 - 18010 - Salvatore Marasco Jr-Checked t-stat, could hear motor turn on but did not hear or feel the blower come on. Requested the A.C. tech. to make repair. - Salvatore Marasco Jr; 2017-03-27 - 18010 - Copied Res. Life HVAC tech on work order and contacted HVAC supervisor. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-26 | 230176 | POLY-118022 | AC not working. Fan blows but no cool air. 4NFB825 | NA | AC not working. Fan blows but no cool air. 4NFB825 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-27 | 165663 | RFMT-142668 | Air conditioning isn't working (hasn't been for about a week) 4NO8ACF | 2017-03-27 - 18010 - John Romero-Checked out A/C unit and everything is working like it should... Thermostat is wired backwards.Advised Simon about problem. - John Romero | Air conditioning isn't working (hasn't been for about a week) 4NO8ACF 2017-03-27 - 18010 - John Romero-Checked out A/C unit and everything is working like it should... Thermostat is wired backwards.Advised Simon about problem. - John Romero | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-27 | 165674 | RFMT-142657 | Weekly Building PM Inspection. | 2017-03-31 - 50051 - John Romero-Walked the building and grounds,Checked all common areas,doors,gates ext - John Romero; 2017-03-31 - 50051 - John Romero-Replaced lamp in laundry room 161 - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds. checked all common areas,doors,light,gates..replaced air filter in laundry room W-301. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,gate,light....Lamp out in lounge W-103. Lamps on order. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,lights,gates.. Changed air filters in roof units. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,gates,lights.ext - John Romero | Weekly Building PM Inspection. 2017-03-31 - 50051 - John Romero-Walked the building and grounds,Checked all common areas,doors,gates ext - John Romero; 2017-03-31 - 50051 - John Romero-Replaced lamp in laundry room 161 - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds. checked all common areas,doors,light,gates..replaced air filter in laundry room W-301. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,gate,light....Lamp out in lounge W-103. Lamps on order. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,lights,gates.. Changed air filters in roof units. - John Romero; 2017-03-31 - 50051 - John Romero-Walked the building and grounds.Checked all common areas,doors,gates,lights.ext - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-27 | 22017 | TMPE-228140 | BT Art bldg 1st fl. water fountain has a display that is blank. 4O3HAEN | 2017-04-03 - 23080 - Bruno Lara-Complete The bottle count on the EZH20 display was blank. Took the top cover off to reset the system, but that did not correct the issue. Removed the bottom panel to gain access to the power supply. Shut the water off at the angle stop to remove the filter which was in the way of the power supply. Unplugged the unit for approximately 60 seconds and plugged back in. Display is functional again. Put the filter back in and turned the water on. Purged the system from air in the line. .75 Materials - none - Bruno Lara | BT Art bldg 1st fl. water fountain has a display that is blank. 4O3HAEN 2017-04-03 - 23080 - Bruno Lara-Complete The bottle count on the EZH20 display was blank. Took the top cover off to reset the system, but that did not correct the issue. Removed the bottom panel to gain access to the power supply. Shut the water off at the angle stop to remove the filter which was in the way of the power supply. Unplugged the unit for approximately 60 seconds and plugged back in. Display is functional again. Put the filter back in and turned the water on. Purged the system from air in the line. .75 Materials - none - Bruno Lara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-27 | 22051 | TMPE-228106 | USB SHOP AREA The ice machine in our shop area has a broken part and is calling for "clean me". I have ordered the part. | 2017-04-03 - 18210 - Gail Jackson-Trip to ARS Phx for new cutain which was broke causing machine to stick in off mode. Clean machine and bin, install new parts, relocate curtain sensor and run test complete. - Gail Jackson; 2017-04-03 - 18210 - Thomas Gibble-Trip to ARS Phx for new cutain which was broke causing machine to stick in off mode. Clean machine and bin, install new parts, relocate curtain sensor and run test complete. - Gail Jackson | USB SHOP AREA The ice machine in our shop area has a broken part and is calling for "clean me". I have ordered the part. 2017-04-03 - 18210 - Gail Jackson-Trip to ARS Phx for new cutain which was broke causing machine to stick in off mode. Clean machine and bin, install new parts, relocate curtain sensor and run test complete. - Gail Jackson; 2017-04-03 - 18210 - Thomas Gibble-Trip to ARS Phx for new cutain which was broke causing machine to stick in off mode. Clean machine and bin, install new parts, relocate curtain sensor and run test complete. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-27 | 22131 | TMPE-228026 | IRISHA 128 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . | 2017-03-28 - 18290 - Jennifer Moyer-Replaced motor and cleaned coil. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Fixed a rattle in the unit. Worked with plumber to find out why these units were not cooling, even though there was plenty of chill water and the coil was not clogged. - Jennifer Moyer | IRISHA 128 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . 2017-03-28 - 18290 - Jennifer Moyer-Replaced motor and cleaned coil. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Fixed a rattle in the unit. Worked with plumber to find out why these units were not cooling, even though there was plenty of chill water and the coil was not clogged. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-27 | 22162 | TMPE-227995 | Central Plant- Please work with vendor on replacing the Air Drier for the compressed air system. See Mike T for information. 4NNI9H6 | NA | Central Plant- Please work with vendor on replacing the Air Drier for the compressed air system. See Mike T for information. 4NNI9H6 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-28 | 21961 | TMPE-228196 | !! Hello, We have an experiment, for our undergraduate classes, with a small ac unit, on which the compressor seems to be low on freon. Previously HVAC personel have serviced the unit for me and recharged the freon. If that is still possible I would like to request service for the experimental AC. . . | NA | !! Hello, We have an experiment, for our undergraduate classes, with a small ac unit, on which the compressor seems to be low on freon. Previously HVAC personel have serviced the unit for me and recharged the freon. If that is still possible I would like to request service for the experimental AC. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-28 | 210630 | RACC-117980 | !! The vent fan and some of the numbers on the microwave are not working. 4NEI1B3 | NA | !! The vent fan and some of the numbers on the microwave are not working. 4NEI1B3 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-28 | 230102 | POLY-118096 | The fan in bathroom attached to 215 is much louder than it should be. 4NNFEK1 | NA | The fan in bathroom attached to 215 is much louder than it should be. 4NNFEK1 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-28 | 230120 | POLY-118078 | FLOYD - *ESTIMATE ONLY* (per Henry, this would be a chargeable) The louver motors in the roof ridge are frozen with the louvers open and birds are now perching inside the greenhouse cells 103 and 105. Please replace the louver motors. 42C43B2 | NA | FLOYD - *ESTIMATE ONLY* (per Henry, this would be a chargeable) The louver motors in the roof ridge are frozen with the louvers open and birds are now perching inside the greenhouse cells 103 and 105. Please replace the louver motors. 42C43B2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-28 | 230137 | POLY-118061 | Please check and re-replenish the chemicals in the pump dispensers for the book store bathroom and the kitchen drains. thanks 4NF4KMJ | NA | Please check and re-replenish the chemicals in the pump dispensers for the book store bathroom and the kitchen drains. thanks 4NF4KMJ NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
2017-03-29 | 956 | WEST-110293 | HVAC return is loud. Investigate. | 2017-03-30 - 18010 - Chad T Ball-Went up in ceiling grid and found return air noise insulator was not positioned over return air grate. Re-positioned noise insulator over return grid. Found motor inspection cover loose causing air noise. Removed inspection cover and inspected fan motor and blower wheel. Replaced inspection cover and properly secured to eliminate source of noise. - Chad T Ball | HVAC return is loud. Investigate. 2017-03-30 - 18010 - Chad T Ball-Went up in ceiling grid and found return air noise insulator was not positioned over return air grate. Re-positioned noise insulator over return grid. Found motor inspection cover loose causing air noise. Removed inspection cover and inspected fan motor and blower wheel. Replaced inspection cover and properly secured to eliminate source of noise. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-29 | 957 | WEST-110292 | Sink in bike co-op has low water pressure. Water doesn't come out very well. Was addressed earlier and water pressure was improved, but is still weak. | 2017-04-06 - 23070 - Daniel Tanner-Took the fixture all apart, blew the lines out with compressed air, removed things that were in the line restricting the water flow. - Daniel Tanner; 2017-04-06 - 23070 - Robert Gailey-Assisted Dan with the sink fixture. - Daniel Tanner | Sink in bike co-op has low water pressure. Water doesn't come out very well. Was addressed earlier and water pressure was improved, but is still weak. 2017-04-06 - 23070 - Daniel Tanner-Took the fixture all apart, blew the lines out with compressed air, removed things that were in the line restricting the water flow. - Daniel Tanner; 2017-04-06 - 23070 - Robert Gailey-Assisted Dan with the sink fixture. - Daniel Tanner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-29 | 165481 | RFMT-142850 | PM repair on HVAC equipment | 2017-03-30 - 18010 - Thor Millsaps-PM. Replaced contactor. Tino will enter part. - Thor Millsaps | PM repair on HVAC equipment 2017-03-30 - 18010 - Thor Millsaps-PM. Replaced contactor. Tino will enter part. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-29 | 21688 | TMPE-228469 | PSH H32 process chilled water in PSH32 has been traced back to a pump in H47U1 (Y#7439) that is not in operation. There is strong and sustained pressure in the line, but supply and return are locked together- bypass appears to be open somewhere, and location of pump is unknown. process chilled . . . | 2017-04-13 - 23100 - Derek Gittings-ck out lines,from pumpgood.ck out pump good restared pump all good. - Derek Gittings | PSH H32 process chilled water in PSH32 has been traced back to a pump in H47U1 (Y#7439) that is not in operation. There is strong and sustained pressure in the line, but supply and return are locked together- bypass appears to be open somewhere, and location of pump is unknown. process chilled . . . 2017-04-13 - 23100 - Derek Gittings-ck out lines,from pumpgood.ck out pump good restared pump all good. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2
2017-03-29 | 21692 | TMPE-228465 | LSD 102 !! Environmental chamber 102D is unable to cool. Could HVAC shop or someone familiar with these units take a look? This is a restricted access area, please call me (Mike 480-227-3476) if access is needed. Thanks! Contact Name: Contact Phone Number: 4802273476 Contact Email:. . . | 2017-04-04 - 18140 - Zhi Yu-Arrived Ecabert is working on the unit. I assist for parts and diagnose. - Zhi Yu; 2017-04-04 - 18140 - Robert Ecabert-I ordered a solid state relay for this growth chamber today which is Tuesday 4-4-2017 and they said it should be in at our warehouse on Friday. - Robert Ecabert; 2017-04-04 - 18140 - Robert Ecabert-The hot gas valve is turning on and off sporadically, I believe this growth chamber has a faulty solid state relay. I will Order a new relay for this unit on Tuesday 4-4-2017. - Robert Ecabert; 2017-04-13 - 18140 - Robert Ecabert-This growth chamber cannot maintain the set point temperature because it has an electrical problem. I replaced one bad solid state relay on this unit but that only fixed one of the problems on this unit and I will go back to this unit to try to solve the other electrical issue I am having with this unit tomorrow. - Robert Ecabert; 2017-04-13 - 18140 - Robert Ecabert-The other reason that this unit is not working properly is because the hot gas solenoid is sticking intermittently. On 4-13-2017, Thursday I back ordered a new solenoid valve and a new coil for this valve. I ordered these parts from RSD and they said the parts will arrive in about 2 weeks because they had to be back ordered. - Robert Ecabert | LSD 102 !! Environmental chamber 102D is unable to cool. Could HVAC shop or someone familiar with these units take a look? This is a restricted access area, please call me (Mike 480-227-3476) if access is needed. Thanks! Contact Name: Contact Phone Number: 4802273476 Contact Email:. . . 2017-04-04 - 18140 - Zhi Yu-Arrived Ecabert is working on the unit. I assist for parts and diagnose. - Zhi Yu; 2017-04-04 - 18140 - Robert Ecabert-I ordered a solid state relay for this growth chamber today which is Tuesday 4-4-2017 and they said it should be in at our warehouse on Friday. - Robert Ecabert; 2017-04-04 - 18140 - Robert Ecabert-The hot gas valve is turning on and off sporadically, I believe this growth chamber has a faulty solid state relay. I will Order a new relay for this unit on Tuesday 4-4-2017. - Robert Ecabert; 2017-04-13 - 18140 - Robert Ecabert-This growth chamber cannot maintain the set point temperature because it has an electrical problem. I replaced one bad solid state relay on this unit but that only fixed one of the problems on this unit and I will go back to this unit to try to solve the other electrical issue I am having with this unit tomorrow. - Robert Ecabert; 2017-04-13 - 18140 - Robert Ecabert-The other reason that this unit is not working properly is because the hot gas solenoid is sticking intermittently. On 4-13-2017, Thursday I back ordered a new solenoid valve and a new coil for this valve. I ordered these parts from RSD and they said the parts will arrive in about 2 weeks because they had to be back ordered. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-03-29 | 21706 | TMPE-228451 | IRISHA 128 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . | 2017-03-29 - 18290 - Jennifer Moyer-Cleaned evap coil and flushed coil. Sand came out of it. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Work with plumbing to figure out why water is not circulating through the coil. This coil has been flushed several times.Water valve in the return line was shut. Once opened, the room cooled off. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Flushed coil, worked with plumber to figure out why water is not circulating through the unit. Looked in the basement, looked in other rooms,flushed basement valves and flushed chill water valves in the breezeway. No luck. Try again tomorrow. - Jennifer Moyer | IRISHA 128 EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not working properly. Contact Name: Lori Be. . . 2017-03-29 - 18290 - Jennifer Moyer-Cleaned evap coil and flushed coil. Sand came out of it. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Work with plumbing to figure out why water is not circulating through the coil. This coil has been flushed several times.Water valve in the return line was shut. Once opened, the room cooled off. - Jennifer Moyer; 2017-04-25 - 18290 - Jennifer Moyer-Flushed coil, worked with plumber to figure out why water is not circulating through the unit. Looked in the basement, looked in other rooms,flushed basement valves and flushed chill water valves in the breezeway. No luck. Try again tomorrow. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-03-29 | 21736 | TMPE-228421 | Motor has a bad bearing (note: CHWP 1 is currently down) | NA | Motor has a bad bearing (note: CHWP 1 is currently down) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-29 | 210585 | RACC-118025 | Liquid is dripping from the ceiling vent of the AC unit that is on the left when you walk in the door. 4NDGL1O | NA | Liquid is dripping from the ceiling vent of the AC unit that is on the left when you walk in the door. 4NDGL1O NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-29 | 210601 | RACC-118009 | !! The light in room 5145K-A stopped working. It might need a new bulb. The air conditioning in the apartment has been slow. We don't feel any cold air coming from the vents and the temperature in the apartment has not been cooling down. 4NC6DMI | NA | !! The light in room 5145K-A stopped working. It might need a new bulb. The air conditioning in the apartment has been slow. We don't feel any cold air coming from the vents and the temperature in the apartment has not been cooling down. 4NC6DMI NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-30 | 165422 | RFMT-142909 | !! our AC is no working properly. dorm is extremely warm, 4NNC742 | 2017-04-03 - 18010 - Thomas Zambrano-flushed,cleaned coil externally,change motor. the coil has low air flow and wiil need to changed by hvac techs. - Thomas Zambrano | !! our AC is no working properly. dorm is extremely warm, 4NNC742 2017-04-03 - 18010 - Thomas Zambrano-flushed,cleaned coil externally,change motor. the coil has low air flow and wiil need to changed by hvac techs. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-30 | 21531 | TMPE-228626 | IRISHA 124 maint. and flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not . . . | 2017-04-05 - 18290 - Jennifer Moyer-Shaded pole motor was seized up and will need replaced. Very dirty coil that will need cleaned. Missing wing nut. Removed blower assembly, condensate pan, and register for cleaning and repair. Work to be scheduled. This room has cooling from a RUUD DX unit, but the fan coil needs repaired before extremely hot weather arrives. - Jennifer Moyer; 2017-05-03 - 18290 - Jennifer Moyer-Routine fan coil clean &amp; tune. - Jennifer Moyer | IRISHA 124 maint. and flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not . . . 2017-04-05 - 18290 - Jennifer Moyer-Shaded pole motor was seized up and will need replaced. Very dirty coil that will need cleaned. Missing wing nut. Removed blower assembly, condensate pan, and register for cleaning and repair. Work to be scheduled. This room has cooling from a RUUD DX unit, but the fan coil needs repaired before extremely hot weather arrives. - Jennifer Moyer; 2017-05-03 - 18290 - Jennifer Moyer-Routine fan coil clean &amp; tune. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-03-30 | 21533 | TMPE-228624 | IRISHA 124 maint. & flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not wo. . . | 2017-04-05 - 18290 - Jennifer Moyer-Extremely dirty. Coil and blower assembly need cleaned. Chill water is not flowing through this unit. Many of the units on this wing have plugged coils. Repairs will be scheduled. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-05-03 - 18290 - Jennifer Moyer-Clean coil and blower assembly. - Jennifer Moyer; 2017-05-03 - 18290 - Unable to flush coil, missing isolation valve. Work order created for plumbing. - Jennifer Moyer | IRISHA 124 maint. & flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not wo. . . 2017-04-05 - 18290 - Jennifer Moyer-Extremely dirty. Coil and blower assembly need cleaned. Chill water is not flowing through this unit. Many of the units on this wing have plugged coils. Repairs will be scheduled. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-05-03 - 18290 - Jennifer Moyer-Clean coil and blower assembly. - Jennifer Moyer; 2017-05-03 - 18290 - Unable to flush coil, missing isolation valve. Work order created for plumbing. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-03-30 | 21537 | TMPE-228620 | IRISHA 124 maint. and flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also no. . . | 2017-04-05 - 18290 - Jennifer Moyer-This unit has too high of an RPM which causes excessive noise. The chill water is not flowing through the coil and the whole wing on this side of the building seems to have plugged coils. Work to be scheduled.This room does have cooling from a RUUD unit, but it may not keep up when the temperature rises in the 100's.Evap coil needs cleaned. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-04-18 - 18290 - Jennifer Moyer-Tried to clear a clog in the water line with the pancake compressor. Did not work.Evaporator cleaned. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-05-03 - 18290 - Stem valve on unit needs replaced. Work order created for plumbing. - Jennifer Moyer | IRISHA 124 maint. and flush garbage in water lines EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also no. . . 2017-04-05 - 18290 - Jennifer Moyer-This unit has too high of an RPM which causes excessive noise. The chill water is not flowing through the coil and the whole wing on this side of the building seems to have plugged coils. Work to be scheduled.This room does have cooling from a RUUD unit, but it may not keep up when the temperature rises in the 100's.Evap coil needs cleaned. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-04-18 - 18290 - Jennifer Moyer-Tried to clear a clog in the water line with the pancake compressor. Did not work.Evaporator cleaned. - Jennifer Moyer [Modified: 2017-05-03 Jennifer Moyer]; 2017-05-03 - 18290 - Stem valve on unit needs replaced. Work order created for plumbing. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-03-30 | 21591 | TMPE-228566 | IRISHA 128 add BT - need 1 ceiling tile repair EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not wo. . . | 2017-03-31 - 13050 - Lance Tapia-Complete. Located and installed 1-2'x4' ceiling tile. Cut ceiling tile to fit into ceiling grid. Also restored 1 ceiling tile. Used 6' ladder to complete work. Radioed for vacuum clean up in office 128. Materials-Attic Stock 1.25 hrs - Lance Tapia | IRISHA 128 add BT - need 1 ceiling tile repair EMS verified the building is in cooling and the pump is running, call goes to HVAC. !! The air conditioning unit in the conference room is not working properly (no cold air is coming out of the unit). Also, the A./C in room 128 is also not wo. . . 2017-03-31 - 13050 - Lance Tapia-Complete. Located and installed 1-2'x4' ceiling tile. Cut ceiling tile to fit into ceiling grid. Also restored 1 ceiling tile. Used 6' ladder to complete work. Radioed for vacuum clean up in office 128. Materials-Attic Stock 1.25 hrs - Lance Tapia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-30 | 21627 | TMPE-228530 | Please also add the Electrical shop to it to address a power issue. Please generate an Urgent work order mirroring the description in Emergency work order# 228515 and schedule to Thomas Gibble. A/C is broken and blowing hot air. Please reference previous ticket:268100 ORIG REQUEST ASUHC Agent. . . | 2017-03-30 - 15000 - Gary Conover-Job complete - Gary Conover; 2017-03-30 - 15000 - Semeon Haile-Job complete - Gary Conover | Please also add the Electrical shop to it to address a power issue. Please generate an Urgent work order mirroring the description in Emergency work order# 228515 and schedule to Thomas Gibble. A/C is broken and blowing hot air. Please reference previous ticket:268100 ORIG REQUEST ASUHC Agent. . . 2017-03-30 - 15000 - Gary Conover-Job complete - Gary Conover; 2017-03-30 - 15000 - Semeon Haile-Job complete - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-03-30 | 21628 | TMPE-228529 | Please generate an Urgent work order mirroring the description in Emergency work order# 228515 and schedule to Thomas Gibble. A/C is broken and blowing hot air. Please reference previous ticket:268100 ORIG REQUEST ASUHC Agent: Justin Neel Description: A/C is broken and blowing room temp air...I. . . | 2017-03-31 - 18290 - Thomas Gibble-re-set 3 pole breaker. cleaned condenser coil and checked out unit - Thomas Gibble; 2017-03-31 - 18290 - Gail Jackson-re-set 3 pole breaker. cleaned condenser coil and checked out unit - Thomas Gibble | Please generate an Urgent work order mirroring the description in Emergency work order# 228515 and schedule to Thomas Gibble. A/C is broken and blowing hot air. Please reference previous ticket:268100 ORIG REQUEST ASUHC Agent: Justin Neel Description: A/C is broken and blowing room temp air...I. . . 2017-03-31 - 18290 - Thomas Gibble-re-set 3 pole breaker. cleaned condenser coil and checked out unit - Thomas Gibble; 2017-03-31 - 18290 - Gail Jackson-re-set 3 pole breaker. cleaned condenser coil and checked out unit - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4
2017-03-30 | 210557 | RACC-118053 | !! Fan/Air conditioner not running 4NO7MJM | NA | !! Fan/Air conditioner not running 4NO7MJM NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-30 | 250375 | DTPC-118163 | Organize and sweep, Air Compressor room, Fire Pump room, LL South AHU room for exec visit. | 2017-03-30 - 10010 - Robert Bartels-Organize and sweep rooms - Robert Bartels | Organize and sweep, Air Compressor room, Fire Pump room, LL South AHU room for exec visit. 2017-03-30 - 10010 - Robert Bartels-Organize and sweep rooms - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-03-30 | 250387 | DTPC-118151 | Too Hot in 404. Also at Front Desk (400) The blower is very loud. Thank You | 2017-03-30 - 18290 - Robert Bartels-Check source of air flow to lobby, and lowered damper psi. Room 404 had no air flow, had to trace back supply air 1/2 the length of building to find cause of obstruction, a pneumatic damper actuator. Passed information on to building engineer. - Robert Bartels; 2017-04-03 - 18290 - Steve Skibbe-nothing over 76* sound not too bad Nancy said its been taken care of - Steve Skibbe | Too Hot in 404. Also at Front Desk (400) The blower is very loud. Thank You 2017-03-30 - 18290 - Robert Bartels-Check source of air flow to lobby, and lowered damper psi. Room 404 had no air flow, had to trace back supply air 1/2 the length of building to find cause of obstruction, a pneumatic damper actuator. Passed information on to building engineer. - Robert Bartels; 2017-04-03 - 18290 - Steve Skibbe-nothing over 76* sound not too bad Nancy said its been taken care of - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-31 | 165364 | RFMT-142967 | Please check noisy bathroom exhaust fan. | 2017-04-04 - 18010 - Salvatore Marasco Jr-Checked out exhaust to see where noise was coming from. It appeared that the motor was running too fast causing a loud humming. Need A.C. techs. to investigate and possibly change motor. - Salvatore Marasco Jr; 2017-04-10 - 18010 - Copied Simon Res. Life HVAC Lead. - Gregory Stetka | Please check noisy bathroom exhaust fan. 2017-04-04 - 18010 - Salvatore Marasco Jr-Checked out exhaust to see where noise was coming from. It appeared that the motor was running too fast causing a loud humming. Need A.C. techs. to investigate and possibly change motor. - Salvatore Marasco Jr; 2017-04-10 - 18010 - Copied Simon Res. Life HVAC Lead. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-31 | 165391 | RFMT-142940 | HC-Sofia G Mold on the carpet in dorm due to drips from the AC that was just fixed. Dispatched: Juan Rodarte Time: 6:38pm | 2017-03-31 - 14020 - Simon Fernandez-checked a/c unit found no leaks.spoke with student he just wanted his carpet cleaned. - Simon Fernandez | HC-Sofia G Mold on the carpet in dorm due to drips from the AC that was just fixed. Dispatched: Juan Rodarte Time: 6:38pm 2017-03-31 - 14020 - Simon Fernandez-checked a/c unit found no leaks.spoke with student he just wanted his carpet cleaned. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-03-31 | 165392 | RFMT-142939 | !! I have noticed that when I turn on my AC in the afternoon it blows out cool air just fine but if I leave it on throughout the night it eventually stops blowing out cold air and blows out warm air instead. I have noticed this on multiple occasions and I am not sure what causes it. 4O0EFH7 | 2017-03-31 - 18010 - Simon Fernandez-trouble-shoot a/c unit needed to rewire unit,rewired and replaced t-stat,klixon unit checks ok - Simon Fernandez; 2017-03-31 - 18010 - Thor Millsaps-trouble-shoot a/c unit needed to rewire unit,rewired and replaced t-stat,klixon unit checks ok - Simon Fernandez | !! I have noticed that when I turn on my AC in the afternoon it blows out cool air just fine but if I leave it on throughout the night it eventually stops blowing out cold air and blows out warm air instead. I have noticed this on multiple occasions and I am not sure what causes it. 4O0EFH7 2017-03-31 - 18010 - Simon Fernandez-trouble-shoot a/c unit needed to rewire unit,rewired and replaced t-stat,klixon unit checks ok - Simon Fernandez; 2017-03-31 - 18010 - Thor Millsaps-trouble-shoot a/c unit needed to rewire unit,rewired and replaced t-stat,klixon unit checks ok - Simon Fernandez | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-03-31 | 21399 | TMPE-228758 | !! ISTB-1 353G Details: We have an incubator that needs to be repaired. The temperature is not being regulated and it keeps increasing until the alarm sounds. I let it defrost for a few days and that didn't fix it. Currently, it is full of insects we are keeping and I still have it on but I have bee. . . | 2017-04-05 - 18010 - Zhi Yu-We got the Model # and S/N#. Will need todo little research. - Zhi Yu; 2017-04-07 - 18010 - Zhi Yu-We diagnose the system has restriction in the Cap-tube. The Compressor running very hot and in vacuum. System is contaminated. This system Cap-tube has been replaced once. We will need to completely flush out, replaced Compressor and Cap-tube. - Zhi Yu | !! ISTB-1 353G Details: We have an incubator that needs to be repaired. The temperature is not being regulated and it keeps increasing until the alarm sounds. I let it defrost for a few days and that didn't fix it. Currently, it is full of insects we are keeping and I still have it on but I have bee. . . 2017-04-05 - 18010 - Zhi Yu-We got the Model # and S/N#. Will need todo little research. - Zhi Yu; 2017-04-07 - 18010 - Zhi Yu-We diagnose the system has restriction in the Cap-tube. The Compressor running very hot and in vacuum. System is contaminated. This system Cap-tube has been replaced once. We will need to completely flush out, replaced Compressor and Cap-tube. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-01 | 1100 | WEST-110149 | HVAC-GENERAL-MA South Air Filters | 2017-03-29 - 18010 - Chad T Ball-Procured filters from stores warehouse and transported them to mechanical room for future installation. - Chad T Ball; 2017-04-05 - 18010 - Chad T Ball-Replaced filters. Disposed of old filters in compactor. - Chad T Ball | HVAC-GENERAL-MA South Air Filters 2017-03-29 - 18010 - Chad T Ball-Procured filters from stores warehouse and transported them to mechanical room for future installation. - Chad T Ball; 2017-04-05 - 18010 - Chad T Ball-Replaced filters. Disposed of old filters in compactor. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 1101 | WEST-110148 | HVAC-GENERAL-MA North Air Filters | 2017-03-29 - 18010 - Chad T Ball-Procured filters from stores warehouse and moved them to mechanical room for future installation. - Chad T Ball; 2017-04-05 - 18010 - Chad T Ball-Replaced air filters. Disposed of old filters in the compactor. - Chad T Ball | HVAC-GENERAL-MA North Air Filters 2017-03-29 - 18010 - Chad T Ball-Procured filters from stores warehouse and moved them to mechanical room for future installation. - Chad T Ball; 2017-04-05 - 18010 - Chad T Ball-Replaced air filters. Disposed of old filters in the compactor. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 1129 | WEST-110120 | Pump-CWP-002 | 2017-04-11 - 23100 - Joseph McCormick-Greased motor. Pump has no zerk fittings or drain plugs. Wiped down equipment, baseplate and piping. - Joseph McCormick | Pump-CWP-002 2017-04-11 - 23100 - Joseph McCormick-Greased motor. Pump has no zerk fittings or drain plugs. Wiped down equipment, baseplate and piping. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-01 | 1130 | WEST-110119 | Pump-CWP-001 | 2017-04-11 - 23100 - Joseph McCormick-Greased motor. Pump has no zerk fittings or drain plugs. Wiped down equipment, baseplate and piping. - Joseph McCormick | Pump-CWP-001 2017-04-11 - 23100 - Joseph McCormick-Greased motor. Pump has no zerk fittings or drain plugs. Wiped down equipment, baseplate and piping. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-01 | 22255 | TMPE-227902 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22256 | TMPE-227901 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22257 | TMPE-227900 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22258 | TMPE-227899 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22259 | TMPE-227898 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22260 | TMPE-227897 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22261 | TMPE-227896 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22262 | TMPE-227895 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22263 | TMPE-227894 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22264 | TMPE-227893 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22265 | TMPE-227892 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22266 | TMPE-227891 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22267 | TMPE-227890 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22269 | TMPE-227888 | Sidewalk condition and safety check-Monthly | NA | Sidewalk condition and safety check-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 22883 | TMPE-227274 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-01 | 22886 | TMPE-227271 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-01 | 22887 | TMPE-227270 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-01 | 23142 | TMPE-227015 | Vehicle Inspection-Monthly | 2017-04-18 - xPM-VEH-M - Derek Gittings-ac not working. - Derek Gittings | Vehicle Inspection-Monthly 2017-04-18 - xPM-VEH-M - Derek Gittings-ac not working. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-01 | 210487 | RACC-118123 | !! There is termite damage to part of the wall in the bathroom of unit C. I was told to contact maintenance to see about repairing it. 4NH4MG9 | NA | !! There is termite damage to part of the wall in the bathroom of unit C. I was told to contact maintenance to see about repairing it. 4NH4MG9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-02 | 165298 | RFMT-143033 | !! My air conditioner randomly started blowing out warm air instead of cool.Its Really hot in here and I would like it to be fixed ASAP please,please. 4NHGM38 | 2017-04-03 - 18010 - David Cates-Blowing out at 81 degrees in the room. Checked wiring up top, and Thor fixed burnt wires. Please create a TMA for him for this issue. - David Cates; 2017-04-10 - 18010 - Copied Thor per Davids results. - Gregory Stetka | !! My air conditioner randomly started blowing out warm air instead of cool.Its Really hot in here and I would like it to be fixed ASAP please,please. 4NHGM38 2017-04-03 - 18010 - David Cates-Blowing out at 81 degrees in the room. Checked wiring up top, and Thor fixed burnt wires. Please create a TMA for him for this issue. - David Cates; 2017-04-10 - 18010 - Copied Thor per Davids results. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-02 | 210467 | RACC-118143 | !! The Air Conditioning seemed to be making strange noises and was found to be leaking. 4NFHHM9 | NA | !! The Air Conditioning seemed to be making strange noises and was found to be leaking. 4NFHHM9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-02 | 210480 | RACC-118130 | AC not working, no cold air, filter needs to be replaced? Contact Name: Contact Phone Number: 4802522679 Contact Email: Attachment(s) 4NO87N3 | NA | AC not working, no cold air, filter needs to be replaced? Contact Name: Contact Phone Number: 4802522679 Contact Email: Attachment(s) 4NO87N3 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 854 | WEST-110395 | Solar hot water system is blowing fuses. Please troubleshoot. | 2017-04-03 - 18010 - Ronald Chaffee-Found DeltaSol MX controller had blown a fuse. Replaced fuse but blew again. Found a solenoid coil on the "heat Dump" line on the roof bad. In process of finding replacement coil. Went to store to buy fuses for controller. - Ronald Chaffee; 2017-04-04 - 18010 - David Valentine-Ron narrowed the problem down to a bad solenoid on the SDFC roof. - David Valentine; 2017-04-10 - 18010 - Ronald Chaffee-Had to use a puller to remove the old coil. Cleaned up solenoid stem. Mounted new coil, checked resistance on line(22ohms), started system and started to bleed off air. - Ronald Chaffee | Solar hot water system is blowing fuses. Please troubleshoot. 2017-04-03 - 18010 - Ronald Chaffee-Found DeltaSol MX controller had blown a fuse. Replaced fuse but blew again. Found a solenoid coil on the "heat Dump" line on the roof bad. In process of finding replacement coil. Went to store to buy fuses for controller. - Ronald Chaffee; 2017-04-04 - 18010 - David Valentine-Ron narrowed the problem down to a bad solenoid on the SDFC roof. - David Valentine; 2017-04-10 - 18010 - Ronald Chaffee-Had to use a puller to remove the old coil. Cleaned up solenoid stem. Mounted new coil, checked resistance on line(22ohms), started system and started to bleed off air. - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-03 | 165119 | RFMT-143212 | ASUHC-Agent: Kolby Hadden Description: Floor is wet in Palo Verde East, Room 305. In the corner of the room. Walls and ceiling above are dry, but show evidence of water damage. There is dripping sounds coming from the air vent. Who was dispatched: Joe Swan Time of dispatched: 18:22 Joe Swan stat. . . | 2017-04-05 - 23000 - Joe Swan-Offered them a blower for the carpet but it was turned down - Joe Swan | ASUHC-Agent: Kolby Hadden Description: Floor is wet in Palo Verde East, Room 305. In the corner of the room. Walls and ceiling above are dry, but show evidence of water damage. There is dripping sounds coming from the air vent. Who was dispatched: Joe Swan Time of dispatched: 18:22 Joe Swan stat. . . 2017-04-05 - 23000 - Joe Swan-Offered them a blower for the carpet but it was turned down - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 165172 | RFMT-143159 | ASUHC Agent: Terri Campos Description: Refrigerator defrosted creating a wet carpet. Request for water extraction and fan to aid in the drying of the floor. Who was dispatched:Joe Swan Who was dispatched: Olympus Time Dispatched: 6:35 | 2017-04-04 - 23000 - Joe Swan-had Olympus dispatched for water extraction also put blower to dry out carpet - Joe Swan | ASUHC Agent: Terri Campos Description: Refrigerator defrosted creating a wet carpet. Request for water extraction and fan to aid in the drying of the floor. Who was dispatched:Joe Swan Who was dispatched: Olympus Time Dispatched: 6:35 2017-04-04 - 23000 - Joe Swan-had Olympus dispatched for water extraction also put blower to dry out carpet - Joe Swan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 165186 | RFMT-143145 | Not sure what to put for the Room or Area of this request but the thermostat control panel is broken in the hallway of G2 North and there is also a broken Exit sign as well. I believe the Exit sign of H2 is broken right outside the elevator as well. 4NF8M98 | 2017-04-05 - 18010 - Scott Berndt-replaced exit sign and tstat on a/c... - Scott Berndt | Not sure what to put for the Room or Area of this request but the thermostat control panel is broken in the hallway of G2 North and there is also a broken Exit sign as well. I believe the Exit sign of H2 is broken right outside the elevator as well. 4NF8M98 2017-04-05 - 18010 - Scott Berndt-replaced exit sign and tstat on a/c... - Scott Berndt | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-04-03 | 165187 | RFMT-143144 | !! RL HVAC - Please check this heat pump. It is not cooling. 4NEI9DN | 2017-04-03 - 18010 - Thor Millsaps-Repaired wire at condenser and secured away from condenser fan blade. Checked inside room. System is up and running. - Thor Millsaps | !! RL HVAC - Please check this heat pump. It is not cooling. 4NEI9DN 2017-04-03 - 18010 - Thor Millsaps-Repaired wire at condenser and secured away from condenser fan blade. Checked inside room. System is up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-03 | 20392 | TMPE-229765 | drinking fountain chiller not working properly needs repair, Nelson fine arts next to room 36m1 | 2017-04-07 - 18080 - Gail Jackson-Found sewer drain lines corroded and leaking. Refrigeration unit R12 very old, and badly rusted, unit needs replaced, beyond repair. Larry in plumbing says they will size up for complete new unit. Removed old unit recovered frig, and recycled (junked). - Gail Jackson; 2017-04-07 - 18080 - Thomas Gibble-Found sewer drain lines corroded and leaking. Refrigeration unit R12 very old, and badly rusted, unit needs replaced, beyond repair. Larry in plumbing says they will size up for complete new unit. Removed old unit recovered frig, and recycled (junked). - Gail Jackson | drinking fountain chiller not working properly needs repair, Nelson fine arts next to room 36m1 2017-04-07 - 18080 - Gail Jackson-Found sewer drain lines corroded and leaking. Refrigeration unit R12 very old, and badly rusted, unit needs replaced, beyond repair. Larry in plumbing says they will size up for complete new unit. Removed old unit recovered frig, and recycled (junked). - Gail Jackson; 2017-04-07 - 18080 - Thomas Gibble-Found sewer drain lines corroded and leaking. Refrigeration unit R12 very old, and badly rusted, unit needs replaced, beyond repair. Larry in plumbing says they will size up for complete new unit. Removed old unit recovered frig, and recycled (junked). - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-03 | 20400 | TMPE-229757 | drinking fountain chiller not working properly needs repair, Nelson fine arts 1st floor next to elevator 3814 | 2017-05-03 - 18080 - Zhi Yu-We adjust the T/Sat. The water temp @52. - Zhi Yu | drinking fountain chiller not working properly needs repair, Nelson fine arts 1st floor next to elevator 3814 2017-05-03 - 18080 - Zhi Yu-We adjust the T/Sat. The water temp @52. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 20411 | TMPE-229746 | drinking fountain chiller not working properly, needs repair, Galvin playhouse lobby | 2017-05-11 - 18080 - Zhi Yu-Plumber department is replaced with new fountain. - Zhi Yu | drinking fountain chiller not working properly, needs repair, Galvin playhouse lobby 2017-05-11 - 18080 - Zhi Yu-Plumber department is replaced with new fountain. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 20415 | TMPE-229742 | drinking fountain chiller not working properly, needs repair, Galvin Playhouse lobby | 2017-05-02 - 18080 - Thomas Gibble-removed chillers and put them in the shop.removed refrigerant and compressor and throw them in dumpster. - Thomas Gibble; 2017-05-02 - 18080 - Gail Jackson-removed chillers and put them in the shop.removed refrigerant and compressor and throw them in dumpster. - Thomas Gibble | drinking fountain chiller not working properly, needs repair, Galvin Playhouse lobby 2017-05-02 - 18080 - Thomas Gibble-removed chillers and put them in the shop.removed refrigerant and compressor and throw them in dumpster. - Thomas Gibble; 2017-05-02 - 18080 - Gail Jackson-removed chillers and put them in the shop.removed refrigerant and compressor and throw them in dumpster. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-03 | 20418 | TMPE-229739 | drinking fountain chiller not working properly, needs repair Galvin Playhouse lobby | 2017-05-02 - 18080 - Gail Jackson-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson | drinking fountain chiller not working properly, needs repair Galvin Playhouse lobby 2017-05-02 - 18080 - Gail Jackson-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found unit down, rusted out, R12, unit needs replaced. Referred to Larry the plumber for replace. Removed condensing unit and jumper domestic water. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 20423 | TMPE-229734 | drinking fountain chiller not working properly needs repair, Galvin Playhouse lobby | 2017-05-02 - 18080 - Gail Jackson-Found condensing rusted out, not operational, due to age and condition needs replaced. Referred to Larry the plumber for replacement. Removed condensing unit and plumbed for domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found condensing rusted out, not operational, due to age and condition needs replaced. Referred to Larry the plumber for replacement. Removed condensing unit and plumbed for domestic water. - Gail Jackson | drinking fountain chiller not working properly needs repair, Galvin Playhouse lobby 2017-05-02 - 18080 - Gail Jackson-Found condensing rusted out, not operational, due to age and condition needs replaced. Referred to Larry the plumber for replacement. Removed condensing unit and plumbed for domestic water. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Found condensing rusted out, not operational, due to age and condition needs replaced. Referred to Larry the plumber for replacement. Removed condensing unit and plumbed for domestic water. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 20430 | TMPE-229727 | drinking fountain chiller not working properly, needs repair,next to room 36m1 | 2017-05-09 - 18080 - Jennifer Moyer-Time taken to locate unit. When I took the cover off, the refrigeration unit was missing. I discussed the matter with a co-worker and then my supervisor. Plumbing shop will be installing a new drinking fountain. The units are too old for repair. - Jennifer Moyer | drinking fountain chiller not working properly, needs repair,next to room 36m1 2017-05-09 - 18080 - Jennifer Moyer-Time taken to locate unit. When I took the cover off, the refrigeration unit was missing. I discussed the matter with a co-worker and then my supervisor. Plumbing shop will be installing a new drinking fountain. The units are too old for repair. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 20437 | TMPE-229720 | drinking fountain chiller not working properly needs repair,Nelson Fine Arts 1st floor next to elevator 3815 | 2017-05-09 - 18080 - Jennifer Moyer-Time taken to locate the unit. Tried to adjust the thermostat, but the adjustment screw was stripped. Discussed situation with supervisor and then plumbing shop. All water fountains in this building have a refrigerant that must be replaced and they are too old for part replacement. - Jennifer Moyer | drinking fountain chiller not working properly needs repair,Nelson Fine Arts 1st floor next to elevator 3815 2017-05-09 - 18080 - Jennifer Moyer-Time taken to locate the unit. Tried to adjust the thermostat, but the adjustment screw was stripped. Discussed situation with supervisor and then plumbing shop. All water fountains in this building have a refrigerant that must be replaced and they are too old for part replacement. - Jennifer Moyer | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-03 | 20438 | TMPE-229719 | drinking fountain chiller not working properly,needs repair,Nelson fine arts 1st floor next to elevator 3815 | 2017-05-09 - 18080 - This water fountain is attached to 048-DRFT-00185 - Jennifer Moyer | drinking fountain chiller not working properly,needs repair,Nelson fine arts 1st floor next to elevator 3815 2017-05-09 - 18080 - This water fountain is attached to 048-DRFT-00185 - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-03 | 210363 | RACC-118247 | New air filter is needed as the old one is very dirty. 4NJDA8K | NA | New air filter is needed as the old one is very dirty. 4NJDA8K NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-04 | 165151 | RFMT-143180 | Please replace the coil in the A/C unit Of Towers 411 Simon | 2017-04-06 - 18010 - Thor Millsaps-assisted in the removal and replacement of the fan coil unit. - Simon Fernandez; 2017-04-06 - 18010 - Simon Fernandez-assisted in the removal and replacement of the fan coil unit. - Simon Fernandez | Please replace the coil in the A/C unit Of Towers 411 Simon 2017-04-06 - 18010 - Thor Millsaps-assisted in the removal and replacement of the fan coil unit. - Simon Fernandez; 2017-04-06 - 18010 - Simon Fernandez-assisted in the removal and replacement of the fan coil unit. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-04 | 165167 | RFMT-143164 | !! The cover to the main AC vent in the room was popped off the wall. 4O1HM9K | 2017-04-05 - 18010 - John Romero-Put cover back onto A/C unit - John Romero | !! The cover to the main AC vent in the room was popped off the wall. 4O1HM9K 2017-04-05 - 18010 - John Romero-Put cover back onto A/C unit - John Romero | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-04 | 20192 | TMPE-229965 | HAV - POD: Please create a work order to remove the ice machine off the soda machine at the HAV POD MARKET COKE needs to fix the soda machine When it gets fixed we will need you to come back and reinstall the ice machine Please charge to ARAMARK | 2017-04-19 - 18210 - Thomas Gibble-put ice machine back on top of the coke machine - Thomas Gibble; 2017-04-25 - 18210 - Thomas Gibble-changed water filter for the ice machine - Thomas Gibble; 2017-04-25 - 18210 - Gail Jackson-changed water filter for the ice machine - Thomas Gibble | HAV - POD: Please create a work order to remove the ice machine off the soda machine at the HAV POD MARKET COKE needs to fix the soda machine When it gets fixed we will need you to come back and reinstall the ice machine Please charge to ARAMARK 2017-04-19 - 18210 - Thomas Gibble-put ice machine back on top of the coke machine - Thomas Gibble; 2017-04-25 - 18210 - Thomas Gibble-changed water filter for the ice machine - Thomas Gibble; 2017-04-25 - 18210 - Gail Jackson-changed water filter for the ice machine - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-04 | 20213 | TMPE-229944 | The bearings on the motor are bad causing the motor to seize. | 2017-04-18 - 18230 - Jennifer Moyer-Take blower assembly apart, clean it, pick up new motor from Johnstone Supply, pick up coil cleaner from maintenance stores, clean evaporator coil,pick up submarine cooler coating at Ace for the side condensate pan, reassemble motor assembly. - Jennifer Moyer; 2017-04-20 - 18230 - Jennifer Moyer-Removed motor assembly and tag out unit. - Jennifer Moyer; 2017-04-20 - 18230 - Jennifer Moyer-Clean coil with stronger coil cleaner (purple coil cleaner) and rinsed. Reinstall motor and vent grill.Wipe grease off outside cabinet and take drip pan back to shop to bead blast and coat with evap cooler coating to prevent rust. Delta T was 9.7. Return air was 71.6 and supply air was 61.9. Coil may still need to be water flushed. This unit was in bad shape for a long while. - Jennifer Moyer; 2017-05-03 - 18230 - unit was flushed when working with plumber. - Jennifer Moyer | The bearings on the motor are bad causing the motor to seize. 2017-04-18 - 18230 - Jennifer Moyer-Take blower assembly apart, clean it, pick up new motor from Johnstone Supply, pick up coil cleaner from maintenance stores, clean evaporator coil,pick up submarine cooler coating at Ace for the side condensate pan, reassemble motor assembly. - Jennifer Moyer; 2017-04-20 - 18230 - Jennifer Moyer-Removed motor assembly and tag out unit. - Jennifer Moyer; 2017-04-20 - 18230 - Jennifer Moyer-Clean coil with stronger coil cleaner (purple coil cleaner) and rinsed. Reinstall motor and vent grill.Wipe grease off outside cabinet and take drip pan back to shop to bead blast and coat with evap cooler coating to prevent rust. Delta T was 9.7. Return air was 71.6 and supply air was 61.9. Coil may still need to be water flushed. This unit was in bad shape for a long while. - Jennifer Moyer; 2017-05-03 - 18230 - unit was flushed when working with plumber. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-04-04 | 229925 | POLY-118273 | STEVE - PLEASE INVESTIGATE !! Hi there, For Classroom Building (CLRB) room number 139 on the ASU Polytechnic campus. In the back left corner of the room, above the sink, and above/behind the ceiling tile there is a persistent whining noise in (what I assume to be) the air conditioning or fume. . . | 2017-04-18 - 18010 - Steve Clark-2ND WORK ORDER WAS GENARATED FOR THIS COMPLIANT - ALL WORK DONE ON THAT TICKET - POLY-118474 - Steve Clark | STEVE - PLEASE INVESTIGATE !! Hi there, For Classroom Building (CLRB) room number 139 on the ASU Polytechnic campus. In the back left corner of the room, above the sink, and above/behind the ceiling tile there is a persistent whining noise in (what I assume to be) the air conditioning or fume. . . 2017-04-18 - 18010 - Steve Clark-2ND WORK ORDER WAS GENARATED FOR THIS COMPLIANT - ALL WORK DONE ON THAT TICKET - POLY-118474 - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-04 | 249950 | DTPC-118588 | soap dispenser not working room 661T1 | 2017-04-07 - 23000 - Thomas Klein-Pump motor broken on soap dispenser. Replaced dispenser. - Thomas Klein | soap dispenser not working room 661T1 2017-04-07 - 23000 - Thomas Klein-Pump motor broken on soap dispenser. Replaced dispenser. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-04-05 | 165070 | RFMT-143261 | !! My A/C unit won't turn on 4NO72MJ | 2017-04-06 - 18010 - Scott Berndt-replaced the a/c motor - Scott Berndt | !! My A/C unit won't turn on 4NO72MJ 2017-04-06 - 18010 - Scott Berndt-replaced the a/c motor - Scott Berndt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-05 | 165077 | RFMT-143254 | !! I've requested to have the air vents changed because I'm highly allergic to mold and I've been sick. There's mold in the shower and possibly under the carpet due to a previous leak. I'm on my way to the hospital for the 5th time. Please have someone come and check the room. CALLED TO DALE H . . . | 2017-04-06 - 18170 - Chester Duncan-Vacuumed A/C cabinet Replaced filter Restricted outside air intake Removed and cleaned bath exhaust vent and duct - Chester Duncan | !! I've requested to have the air vents changed because I'm highly allergic to mold and I've been sick. There's mold in the shower and possibly under the carpet due to a previous leak. I'm on my way to the hospital for the 5th time. Please have someone come and check the room. CALLED TO DALE H . . . 2017-04-06 - 18170 - Chester Duncan-Vacuumed A/C cabinet Replaced filter Restricted outside air intake Removed and cleaned bath exhaust vent and duct - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4
2017-04-05 | 20009 | TMPE-230148 | PSF F11 !! During recent installation of new humidifiers for PSF09 and Keck Lab, humidifier coil insulation was removed from area above ceiling in PSF11 (labelled "humidifier coil"). Steam from the humidifier coil rises to the cold air duct directly above. Resulting heavy condensation has destr. . . | 2017-04-10 - 18220 - Robert Dauscher-Found tiles that appear to have been water damaged. After inspecting on 2 different occasions there is NO ACTIVE LEAK. This area was not part of recent repair to humidifier system. Replaced the two damaged tiles - Robert Dauscher | PSF F11 !! During recent installation of new humidifiers for PSF09 and Keck Lab, humidifier coil insulation was removed from area above ceiling in PSF11 (labelled "humidifier coil"). Steam from the humidifier coil rises to the cold air duct directly above. Resulting heavy condensation has destr. . . 2017-04-10 - 18220 - Robert Dauscher-Found tiles that appear to have been water damaged. After inspecting on 2 different occasions there is NO ACTIVE LEAK. This area was not part of recent repair to humidifier system. Replaced the two damaged tiles - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 4
2017-04-05 | 20032 | TMPE-230125 | MOEUR 150U1 Add the HVAC Mechanical Shop for this issue as per. Pete Sandoval there is an issue with the oil Separator/Trap for the Air Compressor. This is urgent and please contact Ashly Toland here cc'd. !! Need water purging system serviced- currently pumping massive amounts of water and oi. . . | 2017-04-28 - 18030 - Derek Gittings-pured line ck monday - Derek Gittings; 2017-05-04 - 18030 - Derek Gittings-replaced oil,water sepor - Derek Gittings; 2017-05-08 - 18030 - Derek Gittings-replaced oil sepor,water sepor - Derek Gittings | MOEUR 150U1 Add the HVAC Mechanical Shop for this issue as per. Pete Sandoval there is an issue with the oil Separator/Trap for the Air Compressor. This is urgent and please contact Ashly Toland here cc'd. !! Need water purging system serviced- currently pumping massive amounts of water and oi. . . 2017-04-28 - 18030 - Derek Gittings-pured line ck monday - Derek Gittings; 2017-05-04 - 18030 - Derek Gittings-replaced oil,water sepor - Derek Gittings; 2017-05-08 - 18030 - Derek Gittings-replaced oil sepor,water sepor - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-05 | 20036 | TMPE-230121 | exhaust fan Y-7638. the blower wheel rubs.previously turned in on W/O #153587 Located N E roof.Questions call Mike Bauer 602-558-3959. | 2017-04-20 - 18160 - Robert Ecabert-I began disassembling the exhaust fan so i could move the blower wheel up on the shaft one quarter of an inch so the bottom of the blower wheel will not rub on the top of the blower housing. I have not completed this job as of today, but i will continue working on it tomorrow. - Robert Ecabert; 2017-04-20 - 18160 - Robert Ecabert-I moved the blower wheel up one quarter of an inch onto the shaft so that the bottom of the blower wheel would not rub on the top of the blower hosing. I also installed new seal tight flexible conduit because the blower wheel was rubbing against it. I also installed a new motor minder switch. - Robert Ecabert | exhaust fan Y-7638. the blower wheel rubs.previously turned in on W/O #153587 Located N E roof.Questions call Mike Bauer 602-558-3959. 2017-04-20 - 18160 - Robert Ecabert-I began disassembling the exhaust fan so i could move the blower wheel up on the shaft one quarter of an inch so the bottom of the blower wheel will not rub on the top of the blower housing. I have not completed this job as of today, but i will continue working on it tomorrow. - Robert Ecabert; 2017-04-20 - 18160 - Robert Ecabert-I moved the blower wheel up one quarter of an inch onto the shaft so that the bottom of the blower wheel would not rub on the top of the blower hosing. I also installed new seal tight flexible conduit because the blower wheel was rubbing against it. I also installed a new motor minder switch. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-05 | 20042 | TMPE-230115 | noisy motor bearings and motor base is out of alignment on return air fan 2A.Y-7632 located in roof penthouse. | NA | noisy motor bearings and motor base is out of alignment on return air fan 2A.Y-7632 located in roof penthouse. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-05 | 20046 | TMPE-230111 | noisy motor bearings on return air fan 2B.y-7633. computer commons-penthouse. | 2017-04-21 - 18050 - Robert Ecabert-I spent the day trying to get the information off of the data plate to this motor, it was very hard to get to since the motor data plate is up against the blower housing,but I was finally able to get all of information off of the data plate. - Robert Ecabert; 2017-04-21 - 18050 - Robert Ecabert-Robert Dauscher and I collected The sheave sizes for the motor and the blower wheel as well as the bushing sizes for the motor and for the blower wheel. The sheaves and the bushings I had to back order from Kaman Industrial Technology. I was able to purchase the bearings for this motor at the warehouse. - Robert Ecabert; 2017-04-21 - 18050 - Robert Dauscher-Robert Ecabert-Robert Dauscher and I collected The sheave sizes for the motor and the blower wheel as well as the bushing sizes for the motor and for the blower wheel. The sheaves and the bushings I had to back order from Kaman Industrial Technology. I was able to purchase the bearings for this motor at the warehouse. - Robert Ecabert | noisy motor bearings on return air fan 2B.y-7633. computer commons-penthouse. 2017-04-21 - 18050 - Robert Ecabert-I spent the day trying to get the information off of the data plate to this motor, it was very hard to get to since the motor data plate is up against the blower housing,but I was finally able to get all of information off of the data plate. - Robert Ecabert; 2017-04-21 - 18050 - Robert Ecabert-Robert Dauscher and I collected The sheave sizes for the motor and the blower wheel as well as the bushing sizes for the motor and for the blower wheel. The sheaves and the bushings I had to back order from Kaman Industrial Technology. I was able to purchase the bearings for this motor at the warehouse. - Robert Ecabert; 2017-04-21 - 18050 - Robert Dauscher-Robert Ecabert-Robert Dauscher and I collected The sheave sizes for the motor and the blower wheel as well as the bushing sizes for the motor and for the blower wheel. The sheaves and the bushings I had to back order from Kaman Industrial Technology. I was able to purchase the bearings for this motor at the warehouse. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-05 | 20104 | TMPE-230053 | wells fargo also known as Manzinita pit HVAC - CHW pump 3 Y# 06656 is a 100 HP pump that has a ruptured (cracked) Volute and is leaking severely. | 2017-04-05 - 23030 - Brian Qualls-Started #1 pump, faulted off due to VFD overtemp. Found VFD cooling fan defective. Rigged temporary fan to cool VFD, pump is running with no faults on VFD. #3 pump is off, valved off, and tagged if needs to be run in an emergency. #2 pump has a bad VFD but will run in by-pass. I would not recommend this as there is a leak on the suction side that is introducing air into pump causing cavitation. - Brian Qualls | wells fargo also known as Manzinita pit HVAC - CHW pump 3 Y# 06656 is a 100 HP pump that has a ruptured (cracked) Volute and is leaking severely. 2017-04-05 - 23030 - Brian Qualls-Started #1 pump, faulted off due to VFD overtemp. Found VFD cooling fan defective. Rigged temporary fan to cool VFD, pump is running with no faults on VFD. #3 pump is off, valved off, and tagged if needs to be run in an emergency. #2 pump has a bad VFD but will run in by-pass. I would not recommend this as there is a leak on the suction side that is introducing air into pump causing cavitation. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-04-05 | 20109 | TMPE-230048 | UNCTRB 3rd Flr: BT needs to transfer to HVAC - the A/C unit is running contantly and he believes this is causing the burning smell. Original request: There is a burning smell coming out of the air ducts. Please investigate right away. | 2017-04-05 - 18050 - Called to Steve P - Jeri Zappanti; 2017-04-05 - 18050 - Zhi Yu-During the investigate no smell was found. We check surrounding unit couple dirty air filter and all are direct drive. I have to reset 2 unit. I leave my number to Diana . - Zhi Yu; 2017-05-18 - 18050 - Zhi Yu-I when back for second follow-up no burn smell. - Zhi Yu | UNCTRB 3rd Flr: BT needs to transfer to HVAC - the A/C unit is running contantly and he believes this is causing the burning smell. Original request: There is a burning smell coming out of the air ducts. Please investigate right away. 2017-04-05 - 18050 - Called to Steve P - Jeri Zappanti; 2017-04-05 - 18050 - Zhi Yu-During the investigate no smell was found. We check surrounding unit couple dirty air filter and all are direct drive. I have to reset 2 unit. I leave my number to Diana . - Zhi Yu; 2017-05-18 - 18050 - Zhi Yu-I when back for second follow-up no burn smell. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-04-05 | 20120 | TMPE-230037 | Pump motor has bad bearing and needs repaired | 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-28 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-04 - 23100 - Jose Lopez-lock &amp; tag unit,remove motor,closed water.install new motor/coupling.realign motor to pump,put power to pump,check rotation,amperes,open water.unit running ok &amp; this time. - Jose Lopez | Pump motor has bad bearing and needs repaired 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-28 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-04 - 23100 - Jose Lopez-lock &amp; tag unit,remove motor,closed water.install new motor/coupling.realign motor to pump,put power to pump,check rotation,amperes,open water.unit running ok &amp; this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-04-05 | 20121 | TMPE-230036 | Pump is seized and needs repaired | 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-28 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-04 - 23100 - Jose Lopez-install new coupling,realine motor to pump.open water put power to unit,unit working @ this time. - Jose Lopez | Pump is seized and needs repaired 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-21 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-04-28 - 23100 - Jose Lopez-work in progress - Jose Lopez; 2017-05-04 - 23100 - Jose Lopez-install new coupling,realine motor to pump.open water put power to unit,unit working @ this time. - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-05 | 208408 | RAMA-100856 | Our air conditioner is not working. It makes an odd noise when turned on and the air is not cooling. 4NDCH4E | NA | Our air conditioner is not working. It makes an odd noise when turned on and the air is not cooling. 4NDCH4E NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-05 | 208409 | RAMA-100855 | !! The A/C in our dorm is not working properly, currently it is set on auto but it does not turn off periodically instead it stays on all day. Along with that the air is not cold, it is as if it is not blowing any air out. The main air duct which is located in the kitchen has been dripping water in. . . | NA | !! The A/C in our dorm is not working properly, currently it is set on auto but it does not turn off periodically instead it stays on all day. Along with that the air is not cold, it is as if it is not blowing any air out. The main air duct which is located in the kitchen has been dripping water in. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-04-06 | 165028 | RFMT-143303 | Adelphi Commons 2 West; E092201137; WDNM003398; WDNM051920 WDNM051925; WDNM051917; WDNM051928 WDNM051916;WDNM051922;X141969458;WDNM051886;. . . | 2017-04-07 - 18010 - Simon Fernandez-A/C UNIT;E092201137;Replaced condenser fan motor;35/5RC:A/C UNIT WDNM051920-Replaced 35/5RC:A/C UNIT WDNM049119 Replaced 80/5RC:A/C UNIT WDNM051924 Replaced contactor;A/C UNIT WDNM051872 Replaced 35/5RC;A/C UNIT WDNM051876 added 2lbs(r-22) - Simon Fernandez; 2017-04-07 - 18010 - Simon Fernandez-all other a/c units okay - Simon Fernandez | Adelphi Commons 2 West; E092201137; WDNM003398; WDNM051920 WDNM051925; WDNM051917; WDNM051928 WDNM051916;WDNM051922;X141969458;WDNM051886;. . . 2017-04-07 - 18010 - Simon Fernandez-A/C UNIT;E092201137;Replaced condenser fan motor;35/5RC:A/C UNIT WDNM051920-Replaced 35/5RC:A/C UNIT WDNM049119 Replaced 80/5RC:A/C UNIT WDNM051924 Replaced contactor;A/C UNIT WDNM051872 Replaced 35/5RC;A/C UNIT WDNM051876 added 2lbs(r-22) - Simon Fernandez; 2017-04-07 - 18010 - Simon Fernandez-all other a/c units okay - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-06 | 19816 | TMPE-230341 | Could you please check that there is the correct water flow feeding the roof coolers In ISTB2-101, ISTB2-103 and ISTB2-107? All the coolers seem to be blowing hot air without any cooling. Can you please spot check these 3 coolers for proper operation for the summer months? Thank you. 42ADNIM | 2017-05-13 - 18100 - Robert Dauscher-PM coolers on roof. Found 1 with disconnect off. water line from pump to pads broken. repaired the line by inserting copper fitting with two hose clamps. - Robert Dauscher | Could you please check that there is the correct water flow feeding the roof coolers In ISTB2-101, ISTB2-103 and ISTB2-107? All the coolers seem to be blowing hot air without any cooling. Can you please spot check these 3 coolers for proper operation for the summer months? Thank you. 42ADNIM 2017-05-13 - 18100 - Robert Dauscher-PM coolers on roof. Found 1 with disconnect off. water line from pump to pads broken. repaired the line by inserting copper fitting with two hose clamps. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-04-06 | 19842 | TMPE-230315 | HVAC Added, to check out HP-2-58 & HP-2-59. EMS adjusted temperature, both units calling for cooling, both units keep tripping off after being reset. It's 80 deg please contact Susana in RM 212 she will show you where the t-stat(s) and HP's are. HVAC WO# 230315 , EMS WO#225033 !! Hello. With . . . | 2017-04-12 - 18290 - Zhi Yu-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Mitchell Andrews-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Zhi Yu-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Mitchell Andrews-Going Back to the HP3-58. We Removed the back corner cubicle and set ladder. removed blower motor back to shop. We founded match one in the cage. We install Blower motor, cap, check pressure and split @ 20deg. I also responded Call in University center C Room 303 - Zhi Yu; 2017-04-12 - 18290 - Zhi Yu-Going Back to the HP3-58. We Removed the back corner cubicle and set ladder. removed blower motor back to shop. We founded match one in the cage. We install Blower motor, cap, check pressure and split @ 20deg. - Zhi Yu | HVAC Added, to check out HP-2-58 & HP-2-59. EMS adjusted temperature, both units calling for cooling, both units keep tripping off after being reset. It's 80 deg please contact Susana in RM 212 she will show you where the t-stat(s) and HP's are. HVAC WO# 230315 , EMS WO#225033 !! Hello. With . . . 2017-04-12 - 18290 - Zhi Yu-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Mitchell Andrews-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Zhi Yu-Unit HP3-39 completely plug-up. We back flush the unit, clean-out the circuit setter and install the Y strainer. HP 3-58 Bad blower motor. HP 3-57 the bad T/Sat. We have EMS order Novar Stat. - Zhi Yu; 2017-04-12 - 18290 - Mitchell Andrews-Going Back to the HP3-58. We Removed the back corner cubicle and set ladder. removed blower motor back to shop. We founded match one in the cage. We install Blower motor, cap, check pressure and split @ 20deg. I also responded Call in University center C Room 303 - Zhi Yu; 2017-04-12 - 18290 - Zhi Yu-Going Back to the HP3-58. We Removed the back corner cubicle and set ladder. removed blower motor back to shop. We founded match one in the cage. We install Blower motor, cap, check pressure and split @ 20deg. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-06 | 19851 | TMPE-230306 | install missing ceiling tiles and water damaged tiles. Remove all of the plastic tarps that are attached to the walls to cover the equipment needs to be done as soon as possible this is room classroom 142 | 2017-04-10 - 13000 - Joel Hansen-4/7/17 Found Mauricio and got tile took off plastic and replaced shadow tiles - Joel Hansen [Modified: 2017-04-11 Stephen Chisler]; 2017-04-19 - 13000 - Joel Hansen-4/10/17 Covered equipment with plastic Cut in tiles Drilled out rivots in wall angle to move tee's over to fit a full tile width @ 20* angle Cleaned up - Joel Hansen; 2017-04-19 - 13000 - Joel Hansen-4/18/17 R &amp; R several wires and tee's to fcilitate new till installation The duct work is literally resting on the mains in several spots There are plumbing and electrical pipes with 2" or so clearance which creates a labor intensive situation I took a pic and had it added to WO - Joel Hansen; 2017-04-24 - 13000 - Joel Hansen-4/19/17 Started eplacing all bad tiles Core removed and then re installed a huge section of the grid in the back room after we finished changing the bad ceiling tiles in that room I went through and covered computers, replaced hammered tiles, and swept entire suite changed tile in professors office too Tried cleaning the grid off but it was paint Put down all the metal tiles that were up - Joel Hansen [Modified: 2017-04-24 Joel Hansen]; 2017-04-24 - 13000 - Joel Hansen-4/20/17 Replaced the the last few tiles with the 3 boxes I ordered Put down all the metal tiles that were up again as Core's AC contractor came out and was in the ceiling again Cleaned up all, swept, etc Olympus is coming out to clean again - Joel Hansen [Modified: 2017-04-24 Joel Hansen] | install missing ceiling tiles and water damaged tiles. Remove all of the plastic tarps that are attached to the walls to cover the equipment needs to be done as soon as possible this is room classroom 142 2017-04-10 - 13000 - Joel Hansen-4/7/17 Found Mauricio and got tile took off plastic and replaced shadow tiles - Joel Hansen [Modified: 2017-04-11 Stephen Chisler]; 2017-04-19 - 13000 - Joel Hansen-4/10/17 Covered equipment with plastic Cut in tiles Drilled out rivots in wall angle to move tee's over to fit a full tile width @ 20* angle Cleaned up - Joel Hansen; 2017-04-19 - 13000 - Joel Hansen-4/18/17 R &amp; R several wires and tee's to fcilitate new till installation The duct work is literally resting on the mains in several spots There are plumbing and electrical pipes with 2" or so clearance which creates a labor intensive situation I took a pic and had it added to WO - Joel Hansen; 2017-04-24 - 13000 - Joel Hansen-4/19/17 Started eplacing all bad tiles Core removed and then re installed a huge section of the grid in the back room after we finished changing the bad ceiling tiles in that room I went through and covered computers, replaced hammered tiles, and swept entire suite changed tile in professors office too Tried cleaning the grid off but it was paint Put down all the metal tiles that were up - Joel Hansen [Modified: 2017-04-24 Joel Hansen]; 2017-04-24 - 13000 - Joel Hansen-4/20/17 Replaced the the last few tiles with the 3 boxes I ordered Put down all the metal tiles that were up again as Core's AC contractor came out and was in the ceiling again Cleaned up all, swept, etc Olympus is coming out to clean again - Joel Hansen [Modified: 2017-04-24 Joel Hansen] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-04-06 | 19857 | TMPE-230300 | ECE 115 The a/c unit for the room isn't working and it is very hot. | 2017-04-26 - 18290 - Called out to Brian Q to check on the status. Still 79 degrees in there. AT - Amanda Thomas; 2017-04-27 - 18290 - Thomas Gibble-changed run cap for compressor - Thomas Gibble; 2017-04-27 - 18290 - Gail Jackson-changed run cap for compressor - Thomas Gibble; 2017-05-11 - 18290 - Thomas Gibble-replaced bad cond motor. went to parts store to pick up - Thomas Gibble | ECE 115 The a/c unit for the room isn't working and it is very hot. 2017-04-26 - 18290 - Called out to Brian Q to check on the status. Still 79 degrees in there. AT - Amanda Thomas; 2017-04-27 - 18290 - Thomas Gibble-changed run cap for compressor - Thomas Gibble; 2017-04-27 - 18290 - Gail Jackson-changed run cap for compressor - Thomas Gibble; 2017-05-11 - 18290 - Thomas Gibble-replaced bad cond motor. went to parts store to pick up - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-06 | 19923 | TMPE-230234 | The swamp coolers were recently worked on. Now fan #2 is not operating and fan #4 leaks very bad when in use. Please have someone check this out asap. Please make sure to check in first with staff at Surplus. | 2017-04-06 - 18100 - CALLED TO ONER. - Monica Moraga; 2017-04-19 - 18100 - Roque Garcia-Repaired the distribution water line and drain pipe. - Roque Garcia | The swamp coolers were recently worked on. Now fan #2 is not operating and fan #4 leaks very bad when in use. Please have someone check this out asap. Please make sure to check in first with staff at Surplus. 2017-04-06 - 18100 - CALLED TO ONER. - Monica Moraga; 2017-04-19 - 18100 - Roque Garcia-Repaired the distribution water line and drain pipe. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-06 | 19948 | TMPE-230209 | Central Plant - Replace defective blower motor on Evap cooler 5. | 2017-04-06 - 30010 - Kevin Graves-Replaced blower motor. The pulley had become one with the motor shaft so the adjustable pulley was replaced also. Powered on to check rotation and amp draw. - Lisa Anderson | Central Plant - Replace defective blower motor on Evap cooler 5. 2017-04-06 - 30010 - Kevin Graves-Replaced blower motor. The pulley had become one with the motor shaft so the adjustable pulley was replaced also. Powered on to check rotation and amp draw. - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-06 | 19955 | TMPE-230202 | Please check out the AC ventilation in this restroom. There is no air. | NA | Please check out the AC ventilation in this restroom. There is no air. NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-06 | 210292 | RACC-118318 | Unit B4005 - Common Area Refrigerator freezer fan starting to stall?? Making grinding sound near the back. Listing at odd angle?? Louver blind in center window seizes up when attempting to raise blinds. Replacement Bar chair?? Woods starting to get ready to splinter. Dishwasher door clo. . . | NA | Unit B4005 - Common Area Refrigerator freezer fan starting to stall?? Making grinding sound near the back. Listing at odd angle?? Louver blind in center window seizes up when attempting to raise blinds. Replacement Bar chair?? Woods starting to get ready to splinter. Dishwasher door clo. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-06 | 210297 | RACC-118313 | Both sets of closet doors are not properly on tracks, and we can't figure out how to get them back on. Also air conditioning vent seems to be missing a screw so when the air conditioning is off it hangs down on one corner. 4NNKH3C | NA | Both sets of closet doors are not properly on tracks, and we can't figure out how to get them back on. Also air conditioning vent seems to be missing a screw so when the air conditioning is off it hangs down on one corner. 4NNKH3C NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-07 | 793 | WEST-110456 | There are four motor stands in the Central Plant basement that need to be welded on by the shop personnel so that they can be more easily aligned. The motors are for pumps #11, 12, 13 & 14. This is not a rush job. | NA | There are four motor stands in the Central Plant basement that need to be welded on by the shop personnel so that they can be more easily aligned. The motors are for pumps #11, 12, 13 & 14. This is not a rush job. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-07 | 19652 | TMPE-230505 | PSD D212 Air Handler 36-36 has one belt on and working, and one belt off. | 2017-04-07 - 18050 - Called out to Oner - Amanda Thomas; 2017-05-13 - 18050 - Robert Dauscher-1/2 of blower wheel came apart. Large air handler. Worked with EMS On call to lower speed of AH to allow for cooling to space; and to minimize the risk of complete failure of blower wheel. Only minor vibration. Monitored operation throughout the day. Notified both Steve and Oner. - Robert Dauscher | PSD D212 Air Handler 36-36 has one belt on and working, and one belt off. 2017-04-07 - 18050 - Called out to Oner - Amanda Thomas; 2017-05-13 - 18050 - Robert Dauscher-1/2 of blower wheel came apart. Large air handler. Worked with EMS On call to lower speed of AH to allow for cooling to space; and to minimize the risk of complete failure of blower wheel. Only minor vibration. Monitored operation throughout the day. Notified both Steve and Oner. - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-07 | 19765 | TMPE-230392 | FAC 34B ASU Art Museum Conservation Studio (RM 34B) The mini-split AC units in the Conservation Studio are not producing enough cold air. The Lab curator is requesting someone to come out and take a look at the system. She has asked for the filters to be cleaned. 42AB469 | 2017-05-03 - 18290 - Jennifer Moyer-Contact customer get access. - Jennifer Moyer; 2017-05-03 - 18290 - Jennifer Moyer-Charged with 410A 7lbs. 11oz.Unit working fine. - Jennifer Moyer; 2017-05-03 - 18290 - Model # MSZ-GE18NA serial# 2006238 had a refrigerant leak at the suction line flare fitting. It was tightened. - Jennifer Moyer | FAC 34B ASU Art Museum Conservation Studio (RM 34B) The mini-split AC units in the Conservation Studio are not producing enough cold air. The Lab curator is requesting someone to come out and take a look at the system. She has asked for the filters to be cleaned. 42AB469 2017-05-03 - 18290 - Jennifer Moyer-Contact customer get access. - Jennifer Moyer; 2017-05-03 - 18290 - Jennifer Moyer-Charged with 410A 7lbs. 11oz.Unit working fine. - Jennifer Moyer; 2017-05-03 - 18290 - Model # MSZ-GE18NA serial# 2006238 had a refrigerant leak at the suction line flare fitting. It was tightened. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-07 | 19768 | TMPE-230389 | MU - Main Kitchen: Please create a work order to check the walk in cooler near the dock door It is running a bit warm This is in the main kitchen of the MU BUILDING first floor Charge this to ARAMARK | 2017-04-18 - 18100 - Gail Jackson-Cleaned coil, checked start and run caps OK. - Gail Jackson; 2017-04-18 - 18100 - Gail Jackson-Clean 2 coils on 2 walk-ins, door gaskets coming loose on doors will return with silicone to repair. SAFETY HAZARD: on Y6187 walk-in (old # 4) no shut off for fans have to go to basement to shut off, not up to code. Turned in to Mgr. - Gail Jackson; 2017-04-18 - 18100 - Thomas Gibble-Clean 2 coils on 2 walk-ins, door gaskets coming loose on doors will return with silicone to repair. SAFETY HAZARD: on Y6187 walk-in (old # 4) no shut off for fans have to go to basement to shut off, not up to code. Turned in to Mgr. - Gail Jackson; 2017-04-20 - 18100 - Gail Jackson-Check sight glass on condensing unit in basement; no bubbles, appears to be moving heat, sealed with silicone 4 door gaskets where needed. - Gail Jackson | MU - Main Kitchen: Please create a work order to check the walk in cooler near the dock door It is running a bit warm This is in the main kitchen of the MU BUILDING first floor Charge this to ARAMARK 2017-04-18 - 18100 - Gail Jackson-Cleaned coil, checked start and run caps OK. - Gail Jackson; 2017-04-18 - 18100 - Gail Jackson-Clean 2 coils on 2 walk-ins, door gaskets coming loose on doors will return with silicone to repair. SAFETY HAZARD: on Y6187 walk-in (old # 4) no shut off for fans have to go to basement to shut off, not up to code. Turned in to Mgr. - Gail Jackson; 2017-04-18 - 18100 - Thomas Gibble-Clean 2 coils on 2 walk-ins, door gaskets coming loose on doors will return with silicone to repair. SAFETY HAZARD: on Y6187 walk-in (old # 4) no shut off for fans have to go to basement to shut off, not up to code. Turned in to Mgr. - Gail Jackson; 2017-04-20 - 18100 - Gail Jackson-Check sight glass on condensing unit in basement; no bubbles, appears to be moving heat, sealed with silicone 4 door gaskets where needed. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-07 | 208400 | RAMA-100864 | !! Repeat Request. air vent is leaking again! 4NKEH6O | NA | !! Repeat Request. air vent is leaking again! 4NKEH6O NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-07 | 229836 | POLY-118362 | **Called Allan to report issue - he was going to to check it out.** Received call that Academic center 145 was blowing hot air - they have student events Friday and Saturday April 7 and 8. | 2017-04-10 - 18290 - Allan Blair-Continuation of shift. - Gayle Swenson; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Darusman Amin-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Darusman Amin-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark | **Called Allan to report issue - he was going to to check it out.** Received call that Academic center 145 was blowing hot air - they have student events Friday and Saturday April 7 and 8. 2017-04-10 - 18290 - Allan Blair-Continuation of shift. - Gayle Swenson; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Darusman Amin-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Darusman Amin-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark; 2017-04-12 - 18290 - Allan Blair-found chiller low on r22, topped off, also found broken wire on contactor to compressor #2 - Steve Clark | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 7
2017-04-07 | 229854 | POLY-118344 | Remove old cooler's on the shop and install new master cool. 42BF1ON | NA | Remove old cooler's on the shop and install new master cool. 42BF1ON NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-07 | 249934 | DTPC-118604 | A/c for unit 300 a/c # 310 unit not working | 2017-04-10 - 18010 - Larry Smith-Unit not cooling or coming on Replaced control board and air handler fuse also replaced thermostat due to it breaking while trying to fix - Larry Smith; 2017-04-10 - 18010 - Bruce Pickford-Unit not cooling or coming on Replaced control board and air handler fuse also replaced thermostat due to it breaking while trying to fix - Larry Smith | A/c for unit 300 a/c # 310 unit not working 2017-04-10 - 18010 - Larry Smith-Unit not cooling or coming on Replaced control board and air handler fuse also replaced thermostat due to it breaking while trying to fix - Larry Smith; 2017-04-10 - 18010 - Bruce Pickford-Unit not cooling or coming on Replaced control board and air handler fuse also replaced thermostat due to it breaking while trying to fix - Larry Smith | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-08 | 164913 | RFMT-143418 | ASUHC-Daniel Description:A/C is out and will like to have someone come out Who was dispatched: Tommy Zambrano Time of dispatch:2:20 AM Will Have some one come out tomorrow morning | 2017-04-10 - 18010 - Thomas Zambrano-mike g. checked out ac. he said he had to clean return and install new filter. - Thomas Zambrano | ASUHC-Daniel Description:A/C is out and will like to have someone come out Who was dispatched: Tommy Zambrano Time of dispatch:2:20 AM Will Have some one come out tomorrow morning 2017-04-10 - 18010 - Thomas Zambrano-mike g. checked out ac. he said he had to clean return and install new filter. - Thomas Zambrano | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-08 | 20540 | TMPE-229617 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20541 | TMPE-229616 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20588 | TMPE-229569 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20593 | TMPE-229564 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20594 | TMPE-229563 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20595 | TMPE-229562 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20664 | TMPE-229493 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20665 | TMPE-229492 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20666 | TMPE-229491 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20667 | TMPE-229490 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20668 | TMPE-229489 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20669 | TMPE-229488 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20670 | TMPE-229487 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20671 | TMPE-229486 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 20773 | TMPE-229384 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20774 | TMPE-229383 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20775 | TMPE-229382 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20776 | TMPE-229381 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20777 | TMPE-229380 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20778 | TMPE-229379 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20779 | TMPE-229378 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20780 | TMPE-229377 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20781 | TMPE-229376 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20782 | TMPE-229375 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20783 | TMPE-229374 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20784 | TMPE-229373 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20785 | TMPE-229372 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 20786 | TMPE-229371 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-08 | 21065 | TMPE-229092 | Air Handler-Biannual | 2017-04-11 - xPM-0300.03-B - Michael Bauer-checked belt and operation.upon restarting this A/H fuses blew in disconnect at the unit (which I replaced) and also blew fuses in the control panel N W corner of building..I believe their is a motor problem! Central plant sent to mechanical shop.Condition at this time ..poor.. - Michael Bauer | Air Handler-Biannual 2017-04-11 - xPM-0300.03-B - Michael Bauer-checked belt and operation.upon restarting this A/H fuses blew in disconnect at the unit (which I replaced) and also blew fuses in the control panel N W corner of building..I believe their is a motor problem! Central plant sent to mechanical shop.Condition at this time ..poor.. - Michael Bauer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-04-08 | 21165 | TMPE-228992 | Evaporative Cooler- Biannual | 2017-04-14 - xPM-2000-B - Paul Renfrey-Reconnected water supply, and ran unit to check operation, and controls. Good working condition. - Paul Renfrey | Evaporative Cooler- Biannual 2017-04-14 - xPM-2000-B - Paul Renfrey-Reconnected water supply, and ran unit to check operation, and controls. Good working condition. - Paul Renfrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 21168 | TMPE-228989 | DX Equipment-Biannual | 2017-04-17 - xPM-1700-B - Matthew Smith-Washed the condenser and checked the capacitors, found the capacitors for the condenser fan and the indoor blower failing replaced both. Verified that the unit is working correctly. Found the relay for the heat strips had failed. Will bring a new relay when we come to do the preventive maintenance in Oct. - Matthew Smith | DX Equipment-Biannual 2017-04-17 - xPM-1700-B - Matthew Smith-Washed the condenser and checked the capacitors, found the capacitors for the condenser fan and the indoor blower failing replaced both. Verified that the unit is working correctly. Found the relay for the heat strips had failed. Will bring a new relay when we come to do the preventive maintenance in Oct. - Matthew Smith | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-04-08 | 21175 | TMPE-228982 | Drinking Fountain-Annual | 2017-04-14 - xPM-1500-A - Paul Renfrey-Units works but is difficult to operate. Poor condition, side buttons don't work, front button is temperamental. A new unit with attached bottle filler would be ideal. - Paul Renfrey | Drinking Fountain-Annual 2017-04-14 - xPM-1500-A - Paul Renfrey-Units works but is difficult to operate. Poor condition, side buttons don't work, front button is temperamental. A new unit with attached bottle filler would be ideal. - Paul Renfrey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-08 | 21179 | TMPE-228978 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 21196 | TMPE-228961 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-08 | 229888 | POLY-118310 | BILLED Equipment Room Inspection-Monthly BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) | NA | BILLED Equipment Room Inspection-Monthly BILL TO UPSI GN7 ACCOUNT (GN7-1203-02) NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-09 | 210239 | RACC-118371 | !! Repeat Request. The air conditioner does not work in the entire apartment 3093. It stopped working sometime yesterday, and the front desk was called twice as well as the CA on duty and still no one came to fix it. Last night it was hotter in the apartment than outside. Contact Name: Drew Worman. . . | NA | !! Repeat Request. The air conditioner does not work in the entire apartment 3093. It stopped working sometime yesterday, and the front desk was called twice as well as the CA on duty and still no one came to fix it. Last night it was hotter in the apartment than outside. Contact Name: Drew Worman. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-09 | 229835 | POLY-118363 | !! When the air conditioning is turned on, a very loud "chatter" is heard through the air vent between rooms A and C. That area is also where the air filter and its machine are located. Recent dust storms caused what sounded like something coming loose and blowing around on the roof, so that may hav. . . | NA | !! When the air conditioning is turned on, a very loud "chatter" is heard through the air vent between rooms A and C. That area is also where the air filter and its machine are located. Recent dust storms caused what sounded like something coming loose and blowing around on the roof, so that may hav. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-10 | 164883 | RFMT-143448 | Salvatore Marasco Jr-Checked out exhaust to see where noise was coming from. It appeared that the motor was running too fast causing a loud humming. Need A.C. techs. to investigate and possibly change motor.Please check noisy bathroom exhaust fan. | 2017-04-11 - 18010 - Simon Fernandez-c.a.r. - Simon Fernandez | Salvatore Marasco Jr-Checked out exhaust to see where noise was coming from. It appeared that the motor was running too fast causing a loud humming. Need A.C. techs. to investigate and possibly change motor.Please check noisy bathroom exhaust fan. 2017-04-11 - 18010 - Simon Fernandez-c.a.r. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-10 | 164889 | RFMT-143442 | David Cates-Blowing out at 81 degrees in the room. Checked wiring up top, and Thor fixed burnt wires. Please create a TMA for him for this issue.!! My air conditioner randomly started blowing out warm air instead of cool.Its Really hot in here and I would like it to be fixed ASAP please,please. 4NHGM38 | 2017-04-12 - 18010 - Thor Millsaps-Repaired condenser fan high voltage wire. System up and running. - Thor Millsaps | David Cates-Blowing out at 81 degrees in the room. Checked wiring up top, and Thor fixed burnt wires. Please create a TMA for him for this issue.!! My air conditioner randomly started blowing out warm air instead of cool.Its Really hot in here and I would like it to be fixed ASAP please,please. 4NHGM38 2017-04-12 - 18010 - Thor Millsaps-Repaired condenser fan high voltage wire. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-10 | 164909 | RFMT-143422 | Gabe, Please install the FRP to the wall behind the laundry machines in the 4th floor laundry room and contact Greg Stetka when completed. CSC will clean out exhaust vents and reinstall laundry machines when the FRP installation is completed. Thank you. | 2017-04-10 - 10010 - Gabriel Figueroa-Installed FRP behind washers. - Gabriel Figueroa | Gabe, Please install the FRP to the wall behind the laundry machines in the 4th floor laundry room and contact Greg Stetka when completed. CSC will clean out exhaust vents and reinstall laundry machines when the FRP installation is completed. Thank you. 2017-04-10 - 10010 - Gabriel Figueroa-Installed FRP behind washers. - Gabriel Figueroa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-10 | 18979 | TMPE-231178 | Please complete the following: Please thoroughly clean the HVAC system and remove the filters placed above the air vents Attachment(s) 42CBC2L | 2017-05-04 - 18170 - Jennifer Moyer-Called Deanna Morrison at 480-965-7673. I left a message for a return call. I located D109 and the occupant, James Burnette indicated that the issue had been resolved. - Jennifer Moyer | Please complete the following: Please thoroughly clean the HVAC system and remove the filters placed above the air vents Attachment(s) 42CBC2L 2017-05-04 - 18170 - Jennifer Moyer-Called Deanna Morrison at 480-965-7673. I left a message for a return call. I located D109 and the occupant, James Burnette indicated that the issue had been resolved. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-10 | 19027 | TMPE-231130 | Manzy Cafe: Needs someone to look at hood at Grill station - no one came out over the weekend - help desk dispatched to the incorrect department. Original Call:ASUHC Agent: Justin Neel Description: Hood at grill station not pulling smoke Called Jim Emmons, left message on machine Called Brya. . . | 2017-04-10 - 18190 - Brian Qualls-Found no voltage at fan. Went to controller on cook's line found HOA switch turned off. Voltage @ starter A-209v B-210 C-210. Turned on fan went to roof and started, running good. Back at starter, amp draws A-4.8 B-4.6 C-4.8, motor is rated 5.4a @ 208VAC. All is within spec. - Brian Qualls | Manzy Cafe: Needs someone to look at hood at Grill station - no one came out over the weekend - help desk dispatched to the incorrect department. Original Call:ASUHC Agent: Justin Neel Description: Hood at grill station not pulling smoke Called Jim Emmons, left message on machine Called Brya. . . 2017-04-10 - 18190 - Brian Qualls-Found no voltage at fan. Went to controller on cook's line found HOA switch turned off. Voltage @ starter A-209v B-210 C-210. Turned on fan went to roof and started, running good. Back at starter, amp draws A-4.8 B-4.6 C-4.8, motor is rated 5.4a @ 208VAC. All is within spec. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-10 | 19031 | TMPE-231126 | MU - Second floor for catering kitchen freezer: One fan working one fan not working. I approve this repair Charge the GN7 account for repair Thanks | 2017-04-28 - 18180 - Gail Jackson-Trip to ARS Tempe for evap fan motor. Install fan motor, observed condensate drain line froze up and pan full of ice. Request for electricians to install 208v receptacle for drain line heater. - Gail Jackson; 2017-04-28 - 18180 - Thomas Gibble-Trip to ARS Tempe for evap fan motor. Install fan motor, observed condensate drain line froze up and pan full of ice. Request for electricians to install 208v receptacle for drain line heater. - Gail Jackson; 2017-04-28 - 18180 - Gail Jackson-Install drain line heater, will need to repair leak in elbow and repair pan where broke loose from weight of ice. - Gail Jackson; 2017-04-28 - 18180 - Thomas Gibble-Install drain line heater, will need to repair leak in elbow and repair pan where broke loose from weight of ice. - Gail Jackson; 2017-05-01 - 18180 - Gail Jackson-Removed all necessary product from freezer to access work area. Removed condensate pan to remove ice/replaced and replaced screws where stripped out. Installed 230V heat tape and insulated. Flushed with hot water to check for leaks and drainage. Check operation, COMPLETE. - Gail Jackson; 2017-05-01 - 18180 - Thomas Gibble-Removed all necessary product from freezer to access work area. Removed condensate pan to remove ice/replaced and replaced screws where stripped out. Installed 230V heat tape and insulated. Flushed with hot water to check for leaks and drainage. Check operation, COMPLETE. - Gail Jackson | MU - Second floor for catering kitchen freezer: One fan working one fan not working. I approve this repair Charge the GN7 account for repair Thanks 2017-04-28 - 18180 - Gail Jackson-Trip to ARS Tempe for evap fan motor. Install fan motor, observed condensate drain line froze up and pan full of ice. Request for electricians to install 208v receptacle for drain line heater. - Gail Jackson; 2017-04-28 - 18180 - Thomas Gibble-Trip to ARS Tempe for evap fan motor. Install fan motor, observed condensate drain line froze up and pan full of ice. Request for electricians to install 208v receptacle for drain line heater. - Gail Jackson; 2017-04-28 - 18180 - Gail Jackson-Install drain line heater, will need to repair leak in elbow and repair pan where broke loose from weight of ice. - Gail Jackson; 2017-04-28 - 18180 - Thomas Gibble-Install drain line heater, will need to repair leak in elbow and repair pan where broke loose from weight of ice. - Gail Jackson; 2017-05-01 - 18180 - Gail Jackson-Removed all necessary product from freezer to access work area. Removed condensate pan to remove ice/replaced and replaced screws where stripped out. Installed 230V heat tape and insulated. Flushed with hot water to check for leaks and drainage. Check operation, COMPLETE. - Gail Jackson; 2017-05-01 - 18180 - Thomas Gibble-Removed all necessary product from freezer to access work area. Removed condensate pan to remove ice/replaced and replaced screws where stripped out. Installed 230V heat tape and insulated. Flushed with hot water to check for leaks and drainage. Check operation, COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 6
2017-04-10 | 19060 | TMPE-231097 | HVAC needs to transfer to EL - Assist Jose Lopez with power issue Original request: Pump is seized and needs repaired | NA | HVAC needs to transfer to EL - Assist Jose Lopez with power issue Original request: Pump is seized and needs repaired NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-11 | 18838 | TMPE-231319 | BT Coor hall restroom 3300T1 has an inoperable ADA door. 4O3HAEN | 2017-04-13 - 13070 - Bruno Lara-Complete The ADA door was inoperable. Tried the push buttons, but they did not work. Removed the panel cover and started to troubleshoot the unit. Was getting proper voltage to the PC board, but not getting voltage leaving the board. Found a fuse to be open. Removed the fuse and jumped the circuit across the fuse. The unit was now operating. Ordered the part and returned to complete the repairs. Tested the unit to ensure proper operation. 1.00 Materials - attic stock - 1 3.15A 250V fuse - Bruno Lara | BT Coor hall restroom 3300T1 has an inoperable ADA door. 4O3HAEN 2017-04-13 - 13070 - Bruno Lara-Complete The ADA door was inoperable. Tried the push buttons, but they did not work. Removed the panel cover and started to troubleshoot the unit. Was getting proper voltage to the PC board, but not getting voltage leaving the board. Found a fuse to be open. Removed the fuse and jumped the circuit across the fuse. The unit was now operating. Ordered the part and returned to complete the repairs. Tested the unit to ensure proper operation. 1.00 Materials - attic stock - 1 3.15A 250V fuse - Bruno Lara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-11 | 18897 | TMPE-231260 | 4/11/17 Please provide temporary spot cooling for PSD240 due to the recent air handler failure. Temp A/C will be required until repairs are complete. 42BBO8J | 2017-05-10 - 18010 - Jennifer Moyer-Contacted Chritine Roeger 480-965-3243/ occupant. She is still using the portable unit. - Jennifer Moyer | 4/11/17 Please provide temporary spot cooling for PSD240 due to the recent air handler failure. Temp A/C will be required until repairs are complete. 42BBO8J 2017-05-10 - 18010 - Jennifer Moyer-Contacted Chritine Roeger 480-965-3243/ occupant. She is still using the portable unit. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-11 | 18901 | TMPE-231256 | USE 170 !! Repeat Request. This service request is NOT done! Service Request # 267751 has been accepted as work order TMPE-228196 as of 03/28/2017. The action requested is as follows: !! Hello, We have an experiment, for our undergraduate classes, with a small ac unit, on which the compressor . . . | 2017-04-14 - 18290 - Thomas Gibble-we looked for the leak and found it .The flow meter has a leak inside it. they are getting a new one and we will put it in when it comes in. - Thomas Gibble; 2017-04-14 - 18290 - Gail Jackson-we looked for the leak and found it .The flow meter has a leak inside it. they are getting a new one and we will put it in when it comes in. - Thomas Gibble | USE 170 !! Repeat Request. This service request is NOT done! Service Request # 267751 has been accepted as work order TMPE-228196 as of 03/28/2017. The action requested is as follows: !! Hello, We have an experiment, for our undergraduate classes, with a small ac unit, on which the compressor . . . 2017-04-14 - 18290 - Thomas Gibble-we looked for the leak and found it .The flow meter has a leak inside it. they are getting a new one and we will put it in when it comes in. - Thomas Gibble; 2017-04-14 - 18290 - Gail Jackson-we looked for the leak and found it .The flow meter has a leak inside it. they are getting a new one and we will put it in when it comes in. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-11 | 229783 | POLY-118415 | BRUCE, EVANS AND JUAN - PLEASE TAKE CARE OF THESE PLUMBING, HVAC AND OTHER MAINTENANCE ISSUES (ALSO, I HAVE PUT ALL THE PEST CONTROL ISSUES ON THE LIST FOR TRULY NOLAN) Thanks. All 9 units are captured below. The following issues were witnessed this afternoon: Unit G: The light in the fridge . . . | NA | BRUCE, EVANS AND JUAN - PLEASE TAKE CARE OF THESE PLUMBING, HVAC AND OTHER MAINTENANCE ISSUES (ALSO, I HAVE PUT ALL THE PEST CONTROL ISSUES ON THE LIST FOR TRULY NOLAN) Thanks. All 9 units are captured below. The following issues were witnessed this afternoon: Unit G: The light in the fridge . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 164758 | RFMT-143573 | !! Room air-conditioning not working. Thermostat has been set to lowest setting in an attempt to cool off room, but the thermostat will read in the 80s regularly throughout the day without the AC kicking on. The hallways are generally about 10-15 degrees cooler than the room throughout the day, an. . . | 2017-04-17 - 18010 - Eric Miller-Checked unit in room, Thor changed motor. - Eric Miller | !! Room air-conditioning not working. Thermostat has been set to lowest setting in an attempt to cool off room, but the thermostat will read in the 80s regularly throughout the day without the AC kicking on. The hallways are generally about 10-15 degrees cooler than the room throughout the day, an. . . 2017-04-17 - 18010 - Eric Miller-Checked unit in room, Thor changed motor. - Eric Miller | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-12 | 164776 | RFMT-143555 | !! IRS B206 - AC unit not blowing out cold air, gets hot late at night. 4NGA63J | 2017-04-12 - 18010 - Eric Miller-Flushed coil with Sal. Temp at fan coil was 57. - Eric Miller | !! IRS B206 - AC unit not blowing out cold air, gets hot late at night. 4NGA63J 2017-04-12 - 18010 - Eric Miller-Flushed coil with Sal. Temp at fan coil was 57. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-12 | 18660 | TMPE-231497 | ECE E105 Please bring a portable AC unit to this lab so that the students and faculty can continue to work and meet deadlines. They are working in this area tonight possibly past 6PM. It is 79 degrees currently, and even hotter by some of the equipment. Thank you! | 2017-04-12 - 18290 - Called out to Steve... - Amanda Thomas; 2017-04-28 - 18290 - Michael Kelley-Delivered unit. installed in ceiling - Michael Kelley; 2017-04-28 - 18290 - Michael Kelley-Pick up unit took back to shop - Michael Kelley | ECE E105 Please bring a portable AC unit to this lab so that the students and faculty can continue to work and meet deadlines. They are working in this area tonight possibly past 6PM. It is 79 degrees currently, and even hotter by some of the equipment. Thank you! 2017-04-12 - 18290 - Called out to Steve... - Amanda Thomas; 2017-04-28 - 18290 - Michael Kelley-Delivered unit. installed in ceiling - Michael Kelley; 2017-04-28 - 18290 - Michael Kelley-Pick up unit took back to shop - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 18697 | TMPE-231460 | ECD 109 Inside of room 109, there's another room 102AB that the a/c unit duct has burst in the attic so half of it is missing. Please send someone from HVAC asap. | 2017-04-12 - 18250 - CALLED TO BRIAN Q. - Monica Moraga; 2017-04-13 - 18250 - Carl Karr-Locate damaged duct. Pick up materials. - Carl Karr; 2017-04-14 - 18250 - Carl Karr-Pick up material,install new duct. - Carl Karr | ECD 109 Inside of room 109, there's another room 102AB that the a/c unit duct has burst in the attic so half of it is missing. Please send someone from HVAC asap. 2017-04-12 - 18250 - CALLED TO BRIAN Q. - Monica Moraga; 2017-04-13 - 18250 - Carl Karr-Locate damaged duct. Pick up materials. - Carl Karr; 2017-04-14 - 18250 - Carl Karr-Pick up material,install new duct. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 18712 | TMPE-231445 | UCent C - 312: !! The AC in room 312 is extremely cold. However the rooms (302B and 302C) that share the units are comfortable. Can this be looked at to see make the working environment comfortable for all? Thank you for the AC teams hard work in this complicated maze of a building! 42B2DOL | 2017-04-14 - 18300 - Zhi Yu-This Call is responded by EMS. We spoke to Jennifer in Room 312. Temp is still little to cold for her. notice air blower directly on top of her. Will suggest an TMS312 diffuser Replacement. - Zhi Yu; 2017-04-18 - 18300 - Zhi Yu-We pickup the TMS diffuser from norman s Wright. We replaced TMS diffuser. - Zhi Yu | UCent C - 312: !! The AC in room 312 is extremely cold. However the rooms (302B and 302C) that share the units are comfortable. Can this be looked at to see make the working environment comfortable for all? Thank you for the AC teams hard work in this complicated maze of a building! 42B2DOL 2017-04-14 - 18300 - Zhi Yu-This Call is responded by EMS. We spoke to Jennifer in Room 312. Temp is still little to cold for her. notice air blower directly on top of her. Will suggest an TMS312 diffuser Replacement. - Zhi Yu; 2017-04-18 - 18300 - Zhi Yu-We pickup the TMS diffuser from norman s Wright. We replaced TMS diffuser. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 18720 | TMPE-231437 | The programming for the environmental growth chamber LSE S-24 appears to be set properly (on for twelve hours / off for twelve hours) but user reports the lighting is not turning off. Please initiate a work order for HVAC to inspect and service at the earliest opportunity. Thank you. 42BLHKH | 2017-04-18 - 18010 - Robert Ecabert-I replaced one bad solid state relay and I reprogrammed the lighting schedule so the lights are on from 8am to 8pm and the lights are off from 8pm until 8am. - Robert Ecabert | The programming for the environmental growth chamber LSE S-24 appears to be set properly (on for twelve hours / off for twelve hours) but user reports the lighting is not turning off. Please initiate a work order for HVAC to inspect and service at the earliest opportunity. Thank you. 42BLHKH 2017-04-18 - 18010 - Robert Ecabert-I replaced one bad solid state relay and I reprogrammed the lighting schedule so the lights are on from 8am to 8pm and the lights are off from 8pm until 8am. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 18732 | TMPE-231425 | !!On the outside dock- the 2 door freezer is not getting cold. Please check this out. | 2017-04-19 - 18010 - Thomas Gibble-cleaned coil and washed freezer - Thomas Gibble; 2017-04-19 - 18010 - Gail Jackson-cleaned coil and washed freezer - Thomas Gibble | !!On the outside dock- the 2 door freezer is not getting cold. Please check this out. 2017-04-19 - 18010 - Thomas Gibble-cleaned coil and washed freezer - Thomas Gibble; 2017-04-19 - 18010 - Gail Jackson-cleaned coil and washed freezer - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-12 | 18776 | TMPE-231381 | A/C Shop** Can we please get a HEPA filter for our office? Being that we have so much dust from the mulch in our area and people coming in and out all the time plus the pollen we are getting inundated with allergens in the office. Also, our air vents have black mold on them. Thanks so much, Lau. . . | 2017-04-19 - 18010 - Brian Qualls-As per the description this is a dusty environment. Filters in use are high quality 1" pleats. 'Black Mold' is actually just minor dust on registers. Coils and filters are clean, HEPA filters will not make a difference here. They will only plug quicker. Spoke with Laura she is aware. - Brian Qualls | A/C Shop** Can we please get a HEPA filter for our office? Being that we have so much dust from the mulch in our area and people coming in and out all the time plus the pollen we are getting inundated with allergens in the office. Also, our air vents have black mold on them. Thanks so much, Lau. . . 2017-04-19 - 18010 - Brian Qualls-As per the description this is a dusty environment. Filters in use are high quality 1" pleats. 'Black Mold' is actually just minor dust on registers. Coils and filters are clean, HEPA filters will not make a difference here. They will only plug quicker. Spoke with Laura she is aware. - Brian Qualls | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-12 | 210166 | RACC-118444 | !! In need of a clean air filter please. and while your doing that please check air flow 4O0D8J2 | NA | !! In need of a clean air filter please. and while your doing that please check air flow 4O0D8J2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 229768 | POLY-118430 | We are having trouble with our AC/Heating system. The control unit is not responsive. Also, the fan is continuously running without any response to the settings. 4NNFEK1 | NA | We are having trouble with our AC/Heating system. The control unit is not responsive. Also, the fan is continuously running without any response to the settings. 4NNFEK1 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-12 | 249813 | DTPC-118725 | Troubleshoot A/C unit 1-5F | 2017-04-13 - 18010 - Larry Smith-Checked unit and found bad run cap,and bad condenser fan motor. parts on order. - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Checked unit and found bad run cap,and bad condenser fan motor. parts on order. - Larry Smith; 2017-04-18 - 18010 - Larry Smith-Replaced run capacitor and condensing fan motor unit running fine now. - Larry Smith; 2017-04-18 - 18010 - James Hermann-Replaced run capacitor and condensing fan motor unit running fine now. - Larry Smith; 2017-04-21 - 18010 - Larry Smith-Removed and replaced condensing fan motor and capacitor,unit # is 1-5-F carrier 50hcqao7a2a6a0a0a0 model 0215p77772 serial - Larry Smith | Troubleshoot A/C unit 1-5F 2017-04-13 - 18010 - Larry Smith-Checked unit and found bad run cap,and bad condenser fan motor. parts on order. - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Checked unit and found bad run cap,and bad condenser fan motor. parts on order. - Larry Smith; 2017-04-18 - 18010 - Larry Smith-Replaced run capacitor and condensing fan motor unit running fine now. - Larry Smith; 2017-04-18 - 18010 - James Hermann-Replaced run capacitor and condensing fan motor unit running fine now. - Larry Smith; 2017-04-21 - 18010 - Larry Smith-Removed and replaced condensing fan motor and capacitor,unit # is 1-5-F carrier 50hcqao7a2a6a0a0a0 model 0215p77772 serial - Larry Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-12 | 249815 | DTPC-118723 | Troubleshoot A/C unit | 2017-04-13 - 18010 - Larry Smith-Found unit calling for cooling but running heat.Checked wiring at condenser and t stat. Ran out of time due to class starting in room, will come back tomorrow. - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Found unit calling for cooling but running heat.Checked wiring at condenser and t stat. Ran out of time due to class starting in room, will come back tomorrow. - Larry Smith; 2017-04-13 - 18010 - Larry Smith-Relocated wires to proper terminals on t stat reprogrammed to energize reversing valve in cooling mode - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Relocated wires to proper terminals on t stat reprogrammed to energize reversing valve in cooling mode - Larry Smith | Troubleshoot A/C unit 2017-04-13 - 18010 - Larry Smith-Found unit calling for cooling but running heat.Checked wiring at condenser and t stat. Ran out of time due to class starting in room, will come back tomorrow. - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Found unit calling for cooling but running heat.Checked wiring at condenser and t stat. Ran out of time due to class starting in room, will come back tomorrow. - Larry Smith; 2017-04-13 - 18010 - Larry Smith-Relocated wires to proper terminals on t stat reprogrammed to energize reversing valve in cooling mode - Larry Smith; 2017-04-13 - 18010 - Ross Hossack-Relocated wires to proper terminals on t stat reprogrammed to energize reversing valve in cooling mode - Larry Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-04-12 | 249822 | DTPC-118716 | Respond to classroom 300 in Mercado C as they have no AC. | 2017-04-12 - 18290 - James Hermann-Classroom was at 86 degrees. Found one t-stat turned off and another unit not working. I was able to cool classroom to 78 degrees and notified my supervisor of the needed repairs. - James Hermann; 2017-04-12 - 18290 - James Hermann-Unit had new parts installed by another technician, but still did not operate properly. I notified supervisor that the t-stat was not wired properly. - James Hermann | Respond to classroom 300 in Mercado C as they have no AC. 2017-04-12 - 18290 - James Hermann-Classroom was at 86 degrees. Found one t-stat turned off and another unit not working. I was able to cool classroom to 78 degrees and notified my supervisor of the needed repairs. - James Hermann; 2017-04-12 - 18290 - James Hermann-Unit had new parts installed by another technician, but still did not operate properly. I notified supervisor that the t-stat was not wired properly. - James Hermann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-13 | 784 | WEST-110465 | Air Compressor - Monthly Maintenance | 2017-04-19 - xPM-0100-M - Robert Gailey-checked fluid levels and tire pressure, operated compressor. - Robert Gailey | Air Compressor - Monthly Maintenance 2017-04-19 - xPM-0100-M - Robert Gailey-checked fluid levels and tire pressure, operated compressor. - Robert Gailey | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-13 | 164719 | RFMT-143612 | !! Room air-conditioning not working. Thermostat has been set to lowest setting in an attempt to cool off room, but the thermostat will read in the 80s regularly throughout the day without the AC kicking on. The hallways are generally about 10-15 degrees cooler than the room throughout the day, an. . . | 2017-04-14 - 18010 - Thor Millsaps-Replaced blower motor. Cleaned blower wheel and blower assembly, checked system. System up and running. - Thor Millsaps | !! Room air-conditioning not working. Thermostat has been set to lowest setting in an attempt to cool off room, but the thermostat will read in the 80s regularly throughout the day without the AC kicking on. The hallways are generally about 10-15 degrees cooler than the room throughout the day, an. . . 2017-04-14 - 18010 - Thor Millsaps-Replaced blower motor. Cleaned blower wheel and blower assembly, checked system. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-13 | 164725 | RFMT-143606 | !! Resident Tharps' air conditioning is blowing out hot air and wishes to get it fixed before it gets severely hot. Thank you Contact Name: Addison Tharp Contact Phone Number: 4803408916 Contact Email: addietharp@gmail.com 4NG6N0L | 2017-04-14 - 18010 - Thor Millsaps-Bypassed defrost control. Possible high pressure switch fault. Will monitor condenser fan motor for future problems but system is running properly at this time. - Thor Millsaps | !! Resident Tharps' air conditioning is blowing out hot air and wishes to get it fixed before it gets severely hot. Thank you Contact Name: Addison Tharp Contact Phone Number: 4803408916 Contact Email: addietharp@gmail.com 4NG6N0L 2017-04-14 - 18010 - Thor Millsaps-Bypassed defrost control. Possible high pressure switch fault. Will monitor condenser fan motor for future problems but system is running properly at this time. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-13 | 164731 | RFMT-143600 | !! CENTRAL PLANT SOUTH There's a/c issues at Central Plant South in the Communications Room (I believe it's room 105). It is extremely hot. I don' think the condenser is running. Please have someone check it out asap. PER TIM SMITH, RES LIFE HVAC WILL CHECK IT OUT. Submitted by 4NID637 | 2017-04-14 - 18010 - Thor Millsaps-Replaced thermostat. Wired thermostat so that batteries are not required and thermostat is powered by air handler transformer. - Thor Millsaps | !! CENTRAL PLANT SOUTH There's a/c issues at Central Plant South in the Communications Room (I believe it's room 105). It is extremely hot. I don' think the condenser is running. Please have someone check it out asap. PER TIM SMITH, RES LIFE HVAC WILL CHECK IT OUT. Submitted by 4NID637 2017-04-14 - 18010 - Thor Millsaps-Replaced thermostat. Wired thermostat so that batteries are not required and thermostat is powered by air handler transformer. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-13 | 164732 | RFMT-143599 | !! Resident Tharps' air conditioning is blowing out hot air and wishes to get it fixed before it gets severely hot. Thank you Contact Name: Addison Tharp Contact Phone Number: 4803408916 Contact Email: addietharp@gmail.com 4NG6N0L | 2017-04-13 - 18010 - David Cates-Vents were blowing warm air inside room, check unit on roof, and it wasn't running. Messaged Greg to ask for Thor to check it out. Thor checked unit and fixed wiring and unit fired up. - David Cates; 2017-04-14 - 18010 - Copied Res. Life a/c tech. Thor - Gregory Stetka | !! Resident Tharps' air conditioning is blowing out hot air and wishes to get it fixed before it gets severely hot. Thank you Contact Name: Addison Tharp Contact Phone Number: 4803408916 Contact Email: addietharp@gmail.com 4NG6N0L 2017-04-13 - 18010 - David Cates-Vents were blowing warm air inside room, check unit on roof, and it wasn't running. Messaged Greg to ask for Thor to check it out. Thor checked unit and fixed wiring and unit fired up. - David Cates; 2017-04-14 - 18010 - Copied Res. Life a/c tech. Thor - Gregory Stetka | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-13 | 164738 | RFMT-143593 | !! There are bees that come in and out of the vent that's attached to the window and I believe they are building a hive. Submitted by 4NID637 | 2017-04-13 - 19080 - Salvatore Marasco Jr-Checked inside room and inside A/C air vents. Did not see any bees or any signs of bees at the time of inspection. - Salvatore Marasco Jr | !! There are bees that come in and out of the vent that's attached to the window and I believe they are building a hive. Submitted by 4NID637 2017-04-13 - 19080 - Salvatore Marasco Jr-Checked inside room and inside A/C air vents. Did not see any bees or any signs of bees at the time of inspection. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-13 | 18451 | TMPE-231706 | ASUHD Carmen Waterman PE Building West room 239, AC is not on. the room is at 85 degrees even though the thermostat reads 67 degrees. Fan is on but not working. There is a dance class that is going to be held in the room till 8:45pm but the room is too hot. Ava is the instructor for the . . . | 2017-04-14 - 18290 - Thomas Gibble-we both got call in for the same work order. we changed the belt on the unit.everything is working good. - Thomas Gibble; 2017-04-14 - 18290 - Roque Garcia-we both got call in for the same work order. we changed the belt on the unit.everything is working good. - Thomas Gibble | ASUHD Carmen Waterman PE Building West room 239, AC is not on. the room is at 85 degrees even though the thermostat reads 67 degrees. Fan is on but not working. There is a dance class that is going to be held in the room till 8:45pm but the room is too hot. Ava is the instructor for the . . . 2017-04-14 - 18290 - Thomas Gibble-we both got call in for the same work order. we changed the belt on the unit.everything is working good. - Thomas Gibble; 2017-04-14 - 18290 - Roque Garcia-we both got call in for the same work order. we changed the belt on the unit.everything is working good. - Thomas Gibble | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-13 | 18491 | TMPE-231666 | ECE E105 Replace air filters at makeup air unit on the roof and add a spacer to fill in the approximately 2" gap where dirty air is bypassing the filters. 42B3D6J | 2017-05-02 - 18170 - Carl Karr-Did not find problem. Contacted Rick M. - Carl Karr; 2017-05-08 - 18170 - Carl Karr-Double checked air handler, did not find any gaps. Advised Rick M. - Carl Karr | ECE E105 Replace air filters at makeup air unit on the roof and add a spacer to fill in the approximately 2" gap where dirty air is bypassing the filters. 42B3D6J 2017-05-02 - 18170 - Carl Karr-Did not find problem. Contacted Rick M. - Carl Karr; 2017-05-08 - 18170 - Carl Karr-Double checked air handler, did not find any gaps. Advised Rick M. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-13 | 18508 | TMPE-231649 | Air handler #6 needs to have the humidifier looked at there was a lot of water on the floor we need to make sure the humidifier is working correctly. Thank you for your help 42DIMEB | 2017-04-20 - 18010 - Zhi Yu-The humidifier water shooting out bottom corner. We clean out the strainer and flush it.The problem is in the steam trap. We transfer to plumbing shop. - Zhi Yu | Air handler #6 needs to have the humidifier looked at there was a lot of water on the floor we need to make sure the humidifier is working correctly. Thank you for your help 42DIMEB 2017-04-20 - 18010 - Zhi Yu-The humidifier water shooting out bottom corner. We clean out the strainer and flush it.The problem is in the steam trap. We transfer to plumbing shop. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-13 | 18510 | TMPE-231647 | Repair evaporative cooler | NA | Repair evaporative cooler NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-13 | 18541 | TMPE-231616 | HVAC Entire building is warm. The A/C is blowing, but the air is not cool. Contact Name: Paul Iannone Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B | 2017-05-13 - 18290 - Robert Dauscher-found chiller tripped off... reset chiller - Robert Dauscher | HVAC Entire building is warm. The A/C is blowing, but the air is not cool. Contact Name: Paul Iannone Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B 2017-05-13 - 18290 - Robert Dauscher-found chiller tripped off... reset chiller - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-13 | 229734 | POLY-118464 | !! Good Morning, For the Santan Hall room 120U1. This room is too warm for the building communication equipment in that room. Can we have the A/C shop team check the TWO A/C units in that room and get the room temp lowered. Thank you 42B13D7 | 2017-05-01 - 18290 - Esli Arvizo-found both unit had broken blower wheels - ordered new - Steve Clark; 2017-05-01 - 18290 - Allan Blair-found both unit had broken blower wheels - ordered new - Steve Clark; 2017-05-01 - 18290 - Allan Blair-replaced blower wheels and checked operation - Steve Clark; 2017-05-01 - 18290 - Darusman Amin-replaced blower wheels and checked operation - Steve Clark | !! Good Morning, For the Santan Hall room 120U1. This room is too warm for the building communication equipment in that room. Can we have the A/C shop team check the TWO A/C units in that room and get the room temp lowered. Thank you 42B13D7 2017-05-01 - 18290 - Esli Arvizo-found both unit had broken blower wheels - ordered new - Steve Clark; 2017-05-01 - 18290 - Allan Blair-found both unit had broken blower wheels - ordered new - Steve Clark; 2017-05-01 - 18290 - Allan Blair-replaced blower wheels and checked operation - Steve Clark; 2017-05-01 - 18290 - Darusman Amin-replaced blower wheels and checked operation - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-04-13 | 249783 | DTPC-118755 | Meet with TDI and get all serial numbers off motors in all the AHU's | 2017-04-14 - 10110 - Thomas Klein-Took TDI to all AHU's and he recorded all the motors serial numbers. - Thomas Klein | Meet with TDI and get all serial numbers off motors in all the AHU's 2017-04-14 - 10110 - Thomas Klein-Took TDI to all AHU's and he recorded all the motors serial numbers. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-14 | 18328 | TMPE-231829 | NEEB 1ST FL BT TO HVAC - THE LEAK IS IN MULTIPLE AREAS AND COMING DOWN PRETTY STEADY. COULD BE COMING FROM THE HVAC SYSTEM. There's water dripping from a light fixture in the front lobby. | 2017-04-14 - 23000 - CALLED TO THE HD TO CONTACT HVAC STANDBY. MM TALKED TO ASHLEY AT THE HD. - Monica Moraga; 2017-04-26 - 23000 - Roque Garcia-Investigated issue and concern spoke with Gibble who was also dispatched and it was a building issue. - Roque Garcia | NEEB 1ST FL BT TO HVAC - THE LEAK IS IN MULTIPLE AREAS AND COMING DOWN PRETTY STEADY. COULD BE COMING FROM THE HVAC SYSTEM. There's water dripping from a light fixture in the front lobby. 2017-04-14 - 23000 - CALLED TO THE HD TO CONTACT HVAC STANDBY. MM TALKED TO ASHLEY AT THE HD. - Monica Moraga; 2017-04-26 - 23000 - Roque Garcia-Investigated issue and concern spoke with Gibble who was also dispatched and it was a building issue. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-14 | 18341 | TMPE-231816 | EMS to HVAC !! Repeat Request. Attention: HVAC Shop The exhaust fans are not working in L1-17 M1 or 117- M1 This has been an on going issue and submitted several times, these rest rooms smell really bad as a result please have some one address this and get it fixed asap. Thanks for your help in a. . . | 2017-04-14 - 18160 - Xfer to HVAC from EMS - Taylor Nava; 2017-04-20 - 18160 - Gail Jackson-Went to roof checked exhaust fans; work fine; source of odor is floor drains in bathrooms. Poured deodorizer down drain; this needs to be done on at least monthly basis, by cleaning crew. Checked operation of sump and sewage pumps, ok. - Gail Jackson; 2017-04-20 - 18160 - Thomas Gibble-Went to roof checked exhaust fans; work fine; source of odor is floor drains in bathrooms. Poured deodorizer down drain; this needs to be done on at least monthly basis, by cleaning crew. Checked operation of sump and sewage pumps, ok. - Gail Jackson | EMS to HVAC !! Repeat Request. Attention: HVAC Shop The exhaust fans are not working in L1-17 M1 or 117- M1 This has been an on going issue and submitted several times, these rest rooms smell really bad as a result please have some one address this and get it fixed asap. Thanks for your help in a. . . 2017-04-14 - 18160 - Xfer to HVAC from EMS - Taylor Nava; 2017-04-20 - 18160 - Gail Jackson-Went to roof checked exhaust fans; work fine; source of odor is floor drains in bathrooms. Poured deodorizer down drain; this needs to be done on at least monthly basis, by cleaning crew. Checked operation of sump and sewage pumps, ok. - Gail Jackson; 2017-04-20 - 18160 - Thomas Gibble-Went to roof checked exhaust fans; work fine; source of odor is floor drains in bathrooms. Poured deodorizer down drain; this needs to be done on at least monthly basis, by cleaning crew. Checked operation of sump and sewage pumps, ok. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-14 | 18365 | TMPE-231792 | MU - 2nd floor Catering kitchen: Cooler has been running warm 50 degrees the last two hours need someone to look at. | 2017-04-28 - 18100 - Thomas Gibble-adjusted refrigerant level and cleaned coil - Thomas Gibble; 2017-04-28 - 18100 - Mitchell Andrews-adjusted refrigerant level and cleaned coil - Thomas Gibble | MU - 2nd floor Catering kitchen: Cooler has been running warm 50 degrees the last two hours need someone to look at. 2017-04-28 - 18100 - Thomas Gibble-adjusted refrigerant level and cleaned coil - Thomas Gibble; 2017-04-28 - 18100 - Mitchell Andrews-adjusted refrigerant level and cleaned coil - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-14 | 18367 | TMPE-231790 | !! URGENT: Please test PSF basement sump pumps right away, and perform any required repairs. The failure of these pumps has previously led to a major flood in the PSF basement (May, 2016), and they must be checked for proper function on a regular basis. If further details are required, please cont. . . | 2017-04-21 - 23100 - Derek Gittings-ck pumps floats,ran teast. - Derek Gittings | !! URGENT: Please test PSF basement sump pumps right away, and perform any required repairs. The failure of these pumps has previously led to a major flood in the PSF basement (May, 2016), and they must be checked for proper function on a regular basis. If further details are required, please cont. . . 2017-04-21 - 23100 - Derek Gittings-ck pumps floats,ran teast. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-14 | 18390 | TMPE-231767 | !! In ECF130 the conference room 130FH, the heat gets very hot with the door closed. It needs to be switched to the A/C. Thank you, 4MNBAAN | 2017-05-19 - 18290 - Roque Garcia-Found Air Compressor tripped.... repaired and working ok - Roque Garcia | !! In ECF130 the conference room 130FH, the heat gets very hot with the door closed. It needs to be switched to the A/C. Thank you, 4MNBAAN 2017-05-19 - 18290 - Roque Garcia-Found Air Compressor tripped.... repaired and working ok - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-14 | 18423 | TMPE-231734 | PSD RM D232B Transferred to HVAC to install spot cooler to space until AH#3 blower motor fan replacement has been completed. EMS WO#231348, HVAC WO# 231734 !!Lab is too hot- after adjustments room is now too hot for experiments and is damaging. | 2017-04-14 - 18290 - Michael Kelley-We deliver the Portable A/C unit # 1007 - Zhi Yu; 2017-04-14 - 18290 - Zhi Yu-We deliver the Portable A/C unit # 1007 - Zhi Yu | PSD RM D232B Transferred to HVAC to install spot cooler to space until AH#3 blower motor fan replacement has been completed. EMS WO#231348, HVAC WO# 231734 !!Lab is too hot- after adjustments room is now too hot for experiments and is damaging. 2017-04-14 - 18290 - Michael Kelley-We deliver the Portable A/C unit # 1007 - Zhi Yu; 2017-04-14 - 18290 - Zhi Yu-We deliver the Portable A/C unit # 1007 - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-14 | 249768 | DTPC-118770 | Daily walk | 2017-04-14 - 10010 - Larry Smith-Walked property, checked Tempature's in rooms, checked for lights out checked out side for any trash, moved items stored in yellow taped areas out of area - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-No entrance road was closed - Larry Smith; 2017-04-17 - 10010 - Larry Smith-Sprayed weeds blew front of Grant and picked up trash,swept curbing walked property flushed toilets and checked for lights out - Larry Smith; 2017-04-17 - 10010 - Bruce Pickford-Cleaned up in front of grant street with broom and blower pulled weeds,sprayed for weeds, walked building for lights out, flushed toilets all ok at this time - Larry Smith; 2017-04-17 - 10010 - Larry Smith-Cleaned up in front of grant street with broom and blower pulled weeds,sprayed for weeds, walked building for lights out, flushed toilets all ok at this time - Larry Smith; 2017-04-18 - 10010 - Larry Smith-Walked Grant street checked for lights out and checked toilets - Larry Smith; 2017-04-18 - 10010 - James Hermann-Walked Grant street checked for lights out and checked toilets - Larry Smith; 2017-04-20 - 10010 - Larry Smith-Walked property picked up trash checked toilets and checked for lights out - Larry Smith; 2017-04-20 - 10010 - Larry Smith-walked property checked toilets checked for lights out picked up trash - Larry Smith; 2017-04-21 - 10010 - Larry Smith-Walked Grant street studios for lights out found some out but located switch and got it on checked toilets and ran them checked for weeds and trash - Larry Smith; 2017-04-21 - 10010 - Robert Bartels-Walked Grant street studios for lights out found some out but located switch and got it on checked toilets and ran them checked for weeds and trash - Larry Smith | Daily walk 2017-04-14 - 10010 - Larry Smith-Walked property, checked Tempature's in rooms, checked for lights out checked out side for any trash, moved items stored in yellow taped areas out of area - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-Walked building checking all t stats and toilets,checked outside for trash,checked for out lights - Larry Smith; 2017-04-14 - 10010 - Larry Smith-No entrance road was closed - Larry Smith; 2017-04-17 - 10010 - Larry Smith-Sprayed weeds blew front of Grant and picked up trash,swept curbing walked property flushed toilets and checked for lights out - Larry Smith; 2017-04-17 - 10010 - Bruce Pickford-Cleaned up in front of grant street with broom and blower pulled weeds,sprayed for weeds, walked building for lights out, flushed toilets all ok at this time - Larry Smith; 2017-04-17 - 10010 - Larry Smith-Cleaned up in front of grant street with broom and blower pulled weeds,sprayed for weeds, walked building for lights out, flushed toilets all ok at this time - Larry Smith; 2017-04-18 - 10010 - Larry Smith-Walked Grant street checked for lights out and checked toilets - Larry Smith; 2017-04-18 - 10010 - James Hermann-Walked Grant street checked for lights out and checked toilets - Larry Smith; 2017-04-20 - 10010 - Larry Smith-Walked property picked up trash checked toilets and checked for lights out - Larry Smith; 2017-04-20 - 10010 - Larry Smith-walked property checked toilets checked for lights out picked up trash - Larry Smith; 2017-04-21 - 10010 - Larry Smith-Walked Grant street studios for lights out found some out but located switch and got it on checked toilets and ran them checked for weeds and trash - Larry Smith; 2017-04-21 - 10010 - Robert Bartels-Walked Grant street studios for lights out found some out but located switch and got it on checked toilets and ran them checked for weeds and trash - Larry Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-15 | 19194 | TMPE-230963 | Chiller-Quarterly | 2017-05-15 - xPM-0900-Q - Thomas Gibble-transfer to the PM crew - Thomas Gibble | Chiller-Quarterly 2017-05-15 - xPM-0900-Q - Thomas Gibble-transfer to the PM crew - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-15 | 19206 | TMPE-230951 | Air Compressor-Biannual | NA | Air Compressor-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-15 | 19239 | TMPE-230918 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-15 | 19240 | TMPE-230917 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-15 | 19310 | TMPE-230847 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-15 | 19311 | TMPE-230846 | Walk-in Cooler-Biannual | NA | Walk-in Cooler-Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-16 | 18313 | TMPE-231844 | ASUHC-Agent:Laura Description: Neeb Hall. 300+ people. Church service. Doesn't feel like it is working. Hot inside. Who was dispatched:Tom Gibble Time of dispatch:12:00pm Josh called for update. Call was abandoned before we could relay information. - LN 11:49am | 2017-04-18 - 18290 - Thomas Gibble-outside contractors fixed water leak at 1:00 am and i don't know when they finished . when I got there nobody was there and the air handler and pump was running - Thomas Gibble | ASUHC-Agent:Laura Description: Neeb Hall. 300+ people. Church service. Doesn't feel like it is working. Hot inside. Who was dispatched:Tom Gibble Time of dispatch:12:00pm Josh called for update. Call was abandoned before we could relay information. - LN 11:49am 2017-04-18 - 18290 - Thomas Gibble-outside contractors fixed water leak at 1:00 am and i don't know when they finished . when I got there nobody was there and the air handler and pump was running - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-16 | 210075 | RACC-118535 | !! Air Conditioner is not working. 4O2JNG2 | NA | !! Air Conditioner is not working. 4O2JNG2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-16 | 210081 | RACC-118529 | !! In rooms C and D - the right side of the apartment the air conditioning is broken. It needs a new filter as well. It feels extremely humid and hot at the same at time. It honestly feels like I'm living in the south in the summer time. The other side of the apartment is fine in terms of air condit. . . | NA | !! In rooms C and D - the right side of the apartment the air conditioning is broken. It needs a new filter as well. It feels extremely humid and hot at the same at time. It honestly feels like I'm living in the south in the summer time. The other side of the apartment is fine in terms of air condit. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-04-17 | 613 | WEST-110636 | Please repair / replace runner pump as required. Must be completed by Thursday 04/20/2017 42BL7O6 | 2017-04-28 - 23100 - Darrel Counts-put pump back in - Darrel Counts; 2017-04-28 - 23100 - Darrel Counts-removed bad pump - Darrel Counts; 2017-05-05 - 23100 - Darrel Counts-fixed and running good - Darrel Counts | Please repair / replace runner pump as required. Must be completed by Thursday 04/20/2017 42BL7O6 2017-04-28 - 23100 - Darrel Counts-put pump back in - Darrel Counts; 2017-04-28 - 23100 - Darrel Counts-removed bad pump - Darrel Counts; 2017-05-05 - 23100 - Darrel Counts-fixed and running good - Darrel Counts | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-17 | 614 | WEST-110635 | Blower motor failed provide cost for replacement. 4/21 emailed quote tmp 4/24 approved DN1 1003 emailed tw tmp 4/30/17 Billed JC2II008448 tmp | 2017-04-25 - 18010 - Thomas Wienand-Received approval, parts on order - Thomas Wienand; 2017-05-02 - 18010 - Chad T Ball-Travel to/from Rock art center. Replace defective blower motor on roof top air handler. Replaced fuses. Verify proper operation of replacement fan motor. - Chad T Ball; 2017-05-02 - 18010 - Donald Miller-Assisted Chad - Thomas Wienand | Blower motor failed provide cost for replacement. 4/21 emailed quote tmp 4/24 approved DN1 1003 emailed tw tmp 4/30/17 Billed JC2II008448 tmp 2017-04-25 - 18010 - Thomas Wienand-Received approval, parts on order - Thomas Wienand; 2017-05-02 - 18010 - Chad T Ball-Travel to/from Rock art center. Replace defective blower motor on roof top air handler. Replaced fuses. Verify proper operation of replacement fan motor. - Chad T Ball; 2017-05-02 - 18010 - Donald Miller-Assisted Chad - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-17 | 162937 | RFMT-145394 | !! Our toilet paper holder is broken and there is mold in our bathroom that we are breathing in due to the nasty air vent in the bathrooms as well. Need to get rid of the mold, and replac the air vent. Contact Name: Nicolas Ferrara Contact Phone Number: 6029086294 Contact Email: 4NFCNCE | 2017-04-18 - 10010 - Chester Duncan-repaired toilet paper holder cleaned bathroom vent left note that walls and ceiling in bath looked good but that shower needed to be cleaned with a soap and scum remover which was the resident's responsibility - Chester Duncan | !! Our toilet paper holder is broken and there is mold in our bathroom that we are breathing in due to the nasty air vent in the bathrooms as well. Need to get rid of the mold, and replac the air vent. Contact Name: Nicolas Ferrara Contact Phone Number: 6029086294 Contact Email: 4NFCNCE 2017-04-18 - 10010 - Chester Duncan-repaired toilet paper holder cleaned bathroom vent left note that walls and ceiling in bath looked good but that shower needed to be cleaned with a soap and scum remover which was the resident's responsibility - Chester Duncan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-04-17 | 162938 | RFMT-145393 | ASUHC Lisa Daley The bathroom light does not stay on when switched on, the lights blink off and on. The AC also does not work at all. Dispatched to Joe Swan time of dispatch 10:30 pm | 2017-04-20 - 10010 - Repaired a/c unit and replaced lamp. - Gregory Stetka | ASUHC Lisa Daley The bathroom light does not stay on when switched on, the lights blink off and on. The AC also does not work at all. Dispatched to Joe Swan time of dispatch 10:30 pm 2017-04-20 - 10010 - Repaired a/c unit and replaced lamp. - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-17 | 163053 | RFMT-145278 | Weekly Building PM Inspection. | 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas ,and made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas ,and made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Replaced A/C motor in men's restroom.. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas,and made repairs as needed. Replaced exit sign by the south west end of the building. - John Romero; 2017-04-24 - 50051 - John Romero-Room 18 bathroom door sticking and not closing.Removed and repaired door, - John Romero; 2017-04-24 - 50051 - John Romero-walked the building and grounds,checked all common areas,made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas,made repairs as needed. - John Romero | Weekly Building PM Inspection. 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas ,and made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas ,and made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Replaced A/C motor in men's restroom.. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas,and made repairs as needed. Replaced exit sign by the south west end of the building. - John Romero; 2017-04-24 - 50051 - John Romero-Room 18 bathroom door sticking and not closing.Removed and repaired door, - John Romero; 2017-04-24 - 50051 - John Romero-walked the building and grounds,checked all common areas,made repairs as needed. - John Romero; 2017-04-24 - 50051 - John Romero-Walked the building and grounds,checked all common areas,made repairs as needed. - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-17 | 18129 | TMPE-232028 | PSYN 103 There is a leak in the compressed air line. Very loud, lots of air coming out of the end of the hose. The end of the hose is also frayed and bulging. Thank you. | 2017-04-17 - 18030 - Called out to Brian - Amanda Thomas; 2017-04-20 - 18030 - Brian Qualls-Hose is leaking at air nozzle at point of service, customer is responsible at this point. HVAC shop is responsible for the compressor and any filtration at compressor. E-mailed customer same. - Brian Qualls | PSYN 103 There is a leak in the compressed air line. Very loud, lots of air coming out of the end of the hose. The end of the hose is also frayed and bulging. Thank you. 2017-04-17 - 18030 - Called out to Brian - Amanda Thomas; 2017-04-20 - 18030 - Brian Qualls-Hose is leaking at air nozzle at point of service, customer is responsible at this point. HVAC shop is responsible for the compressor and any filtration at compressor. E-mailed customer same. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-17 | 18151 | TMPE-232006 | SCOB 338D BT to HVAC- The leak has been traced to AH A444 up on the roof. There's spots on the ceiling tile. I can hear a drip above the tile. Please send someone to check this leak. | 2017-04-17 - 18050 - Called out to Steve P. - Amanda Thomas; 2017-04-28 - 18050 - Michael Kelley-found problem on air vent discharge line. Controlled leek. Put a hose in the 1/4 inch discharge line. - Michael Kelley; 2017-04-28 - 18050 - Chad Hargrave-found problem on air vent discharge line. Controlled leek. Put a hose in the 1/4 inch discharge line. - Michael Kelley; 2017-04-28 - 18050 - Michael Kelley-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley; 2017-04-28 - 18050 - Roque Garcia-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley; 2017-04-28 - 18050 - Roque Garcia-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley | SCOB 338D BT to HVAC- The leak has been traced to AH A444 up on the roof. There's spots on the ceiling tile. I can hear a drip above the tile. Please send someone to check this leak. 2017-04-17 - 18050 - Called out to Steve P. - Amanda Thomas; 2017-04-28 - 18050 - Michael Kelley-found problem on air vent discharge line. Controlled leek. Put a hose in the 1/4 inch discharge line. - Michael Kelley; 2017-04-28 - 18050 - Chad Hargrave-found problem on air vent discharge line. Controlled leek. Put a hose in the 1/4 inch discharge line. - Michael Kelley; 2017-04-28 - 18050 - Michael Kelley-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley; 2017-04-28 - 18050 - Roque Garcia-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley; 2017-04-28 - 18050 - Roque Garcia-replaced quarter inch discharge line. On AHU 7 and 6 for Air vents. - Michael Kelley | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-17 | 18172 | TMPE-231985 | ADD: ELECTRICIANS Please add electricians to this work order. They will need to provide a power receptacle near the fan coil in this walk in to accommodate a drain line heater. Please see Gail Jackson to explain *original message** MU - Second floor for catering kitchen freezer: One fan w. . . | 2017-04-28 - 18180 - Joel Chavira-Installed 240 volt receptacle. - Samuel Gladden; 2017-04-28 - 18180 - Samuel Gladden-Installed 240 volt receptacle. - Samuel Gladden | ADD: ELECTRICIANS Please add electricians to this work order. They will need to provide a power receptacle near the fan coil in this walk in to accommodate a drain line heater. Please see Gail Jackson to explain *original message** MU - Second floor for catering kitchen freezer: One fan w. . . 2017-04-28 - 18180 - Joel Chavira-Installed 240 volt receptacle. - Samuel Gladden; 2017-04-28 - 18180 - Samuel Gladden-Installed 240 volt receptacle. - Samuel Gladden | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-17 | 18209 | TMPE-231948 | !!A/C register is leaking a steady stream | 2017-04-17 - 14000 - When the tech called it in, he said that custodial was already onsite - Amanda Thomas; 2017-04-17 - 14000 - Carlos Felix-This is a duplicate. Transferred to plumbing. - Carlos Felix | !!A/C register is leaking a steady stream 2017-04-17 - 14000 - When the tech called it in, he said that custodial was already onsite - Amanda Thomas; 2017-04-17 - 14000 - Carlos Felix-This is a duplicate. Transferred to plumbing. - Carlos Felix | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-17 | 210056 | RACC-118554 | !! Repeat Request. The AC on the side of the room with the washer and dryer no longer works. This started after the last filter change. The air will run but no matter how low the AC is set on cool, temperature will sit at outside temperature of 75-85 degrees. Please send someone to fix our AC. Con. . . | NA | !! Repeat Request. The AC on the side of the room with the washer and dryer no longer works. This started after the last filter change. The air will run but no matter how low the AC is set on cool, temperature will sit at outside temperature of 75-85 degrees. Please send someone to fix our AC. Con. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-17 | 210066 | RACC-118544 | !! Our air conditioning is broken as of last night. Air is still blowing out of vents, but the air is not cold and the temperature is not changing. 4NM400O | NA | !! Our air conditioning is broken as of last night. Air is still blowing out of vents, but the air is not cold and the temperature is not changing. 4NM400O NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-04-17 | 229651 | POLY-118547 | CALLED STEVE !! A/C is not working. The temperature is above 85 degrees F. I think the capacitors are bad. It is urgent, research material is dying from excess heat. Thank you 42C52C1 | 2017-05-01 - 18290 - Steve Clark-duplicate w/o - see POLY-118540 - Steve Clark | CALLED STEVE !! A/C is not working. The temperature is above 85 degrees F. I think the capacitors are bad. It is urgent, research material is dying from excess heat. Thank you 42C52C1 2017-05-01 - 18290 - Steve Clark-duplicate w/o - see POLY-118540 - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-18 | 161260 | RFMT-147071 | !! University Housing is requesting for maintenance to look at the ceiling tile in HAV F218 closest to the office door. It is all discolored and we think it could be a leak. Thank you. 42BD24N | 2017-04-20 - 13050 - Chester Duncan-Located a/c line leak at valve Simon inspected and will handle installed new ceiling tiles and cleaned - Chester Duncan | !! University Housing is requesting for maintenance to look at the ceiling tile in HAV F218 closest to the office door. It is all discolored and we think it could be a leak. Thank you. 42BD24N 2017-04-20 - 13050 - Chester Duncan-Located a/c line leak at valve Simon inspected and will handle installed new ceiling tiles and cleaned - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3
2017-04-18 | 162956 | RFMT-145375 | Basement Eq. Rm. Buildings HVAC air handler pleated filter check. Rick, Please record the air handle units y #, filter size/type and the amount of filters needed for a filter change in the results. Thanks, Greg | 2017-04-24 - 18010 - Eric Miller-Changed out 18 (20x20x2) filters. - Eric Miller | Basement Eq. Rm. Buildings HVAC air handler pleated filter check. Rick, Please record the air handle units y #, filter size/type and the amount of filters needed for a filter change in the results. Thanks, Greg 2017-04-24 - 18010 - Eric Miller-Changed out 18 (20x20x2) filters. - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-18 | 17848 | TMPE-232309 | Send to HVAC shop. AHU-9 in EQ rm U2, Level B1 SAF & RAF will not run. Please check them out. Thanks. 42C3NC4 | 2017-04-20 - 18050 - Brian Qualls-Found SAF9 O/L tripped. Nut and bolted starters for SAF and RAF in bucket, 1/4 to 1/2 turn on all line connections. Restart unit. Amp check A-5.2 B-5.1 C5.4, motor rated 7amps @ 460vac. OK. - Brian Qualls | Send to HVAC shop. AHU-9 in EQ rm U2, Level B1 SAF & RAF will not run. Please check them out. Thanks. 42C3NC4 2017-04-20 - 18050 - Brian Qualls-Found SAF9 O/L tripped. Nut and bolted starters for SAF and RAF in bucket, 1/4 to 1/2 turn on all line connections. Restart unit. Amp check A-5.2 B-5.1 C5.4, motor rated 7amps @ 460vac. OK. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-18 | 18026 | TMPE-232131 | Cooler #4 on loading dock needs to have a switch installed in the evaporator section for fan shut-off.This is needed for technician to service unit. Electrical Shop. Have electricians contact HVAC Tech Wes Jackson for specifics. | NA | Cooler #4 on loading dock needs to have a switch installed in the evaporator section for fan shut-off.This is needed for technician to service unit. Electrical Shop. Have electricians contact HVAC Tech Wes Jackson for specifics. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-18 | 18051 | TMPE-232106 | BT to HVAC Ceiling leak is leaking onto chiller lines !! There is a leak in the hallway ceiling outside of and to the right of A211's doorway. The leak has made the ceiling tile bow out, but has not quite made it through yet. No leak on the floor, but we need to catch this before it does land . . . | 2017-04-18 - 18080 - Xfer from BT to HVAC per Bryan LaForais - Taylor Nava; 2017-04-25 - 18080 - Thomas Gibble-2" pipe was leaking.tranfer to plumbing - Thomas Gibble; 2017-04-25 - 18080 - Gail Jackson-2" pipe was leaking.tranfer to plumbing - Thomas Gibble | BT to HVAC Ceiling leak is leaking onto chiller lines !! There is a leak in the hallway ceiling outside of and to the right of A211's doorway. The leak has made the ceiling tile bow out, but has not quite made it through yet. No leak on the floor, but we need to catch this before it does land . . . 2017-04-18 - 18080 - Xfer from BT to HVAC per Bryan LaForais - Taylor Nava; 2017-04-25 - 18080 - Thomas Gibble-2" pipe was leaking.tranfer to plumbing - Thomas Gibble; 2017-04-25 - 18080 - Gail Jackson-2" pipe was leaking.tranfer to plumbing - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-18 | 18094 | TMPE-232063 | HVAC to EL VFD Screen does not work. please check ORIG REQUEST 2" Air Filter Replacement-Bimonthly | 2017-04-19 - 15100 - Gary Conover-Located and replaced keypad - Gary Conover | HVAC to EL VFD Screen does not work. please check ORIG REQUEST 2" Air Filter Replacement-Bimonthly 2017-04-19 - 15100 - Gary Conover-Located and replaced keypad - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 160133 | RFMT-148198 | The AC is not cold at all. The different settings are messed up and don't blow enough air to make the room cold. 4NK2ANN | 2017-04-21 - 18010 - Salvatore Marasco Jr-This room's A/C is connected to the broken chilled water pipe that broke a few weeks ago and has been valved off due to the pipe leak. Broke loose painted closed window, installed portable A/C unit. - Salvatore Marasco Jr [Modified: 2017-04-21 Salvatore Marasco Jr] | The AC is not cold at all. The different settings are messed up and don't blow enough air to make the room cold. 4NK2ANN 2017-04-21 - 18010 - Salvatore Marasco Jr-This room's A/C is connected to the broken chilled water pipe that broke a few weeks ago and has been valved off due to the pipe leak. Broke loose painted closed window, installed portable A/C unit. - Salvatore Marasco Jr [Modified: 2017-04-21 Salvatore Marasco Jr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 5
2017-04-19 | 160170 | RFMT-148161 | Greg I also need work orders for Best A air handler filters and Best B filters | 2017-04-19 - 18010 - Eric Miller-Replaced A/H filters (24) 20x25x2 - Eric Miller | Greg I also need work orders for Best A air handler filters and Best B filters 2017-04-19 - 18010 - Eric Miller-Replaced A/H filters (24) 20x25x2 - Eric Miller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 17681 | TMPE-232476 | SS 107C This unit is blowing very hard and freezing cold air constantly. Health hazard for occupants, also interfering with work. FYI, you must go through 107 to get to 107C. Thank you! | 2017-04-25 - 18300 - Robert Ecabert- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert; 2017-04-25 - 18300 - Robert Ecabert- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert; 2017-04-25 - 18300 - Robert Dauscher- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert | SS 107C This unit is blowing very hard and freezing cold air constantly. Health hazard for occupants, also interfering with work. FYI, you must go through 107 to get to 107C. Thank you! 2017-04-25 - 18300 - Robert Ecabert- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert; 2017-04-25 - 18300 - Robert Ecabert- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert; 2017-04-25 - 18300 - Robert Dauscher- This was called in as to cold call. This unit is mini spit. When I arrived at this room it was very cool in there and I ask the supervisor where the remote control is at for the air conditioner was at and she told me that she has never seen the remote control in the 3 years that she has worked there,so I looked around the room for 5 minutes and found the remote on the ground between the desk and some chairs,I gave the remote to the supervisor and she will make sure that it will not go missing again. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-19 | 17697 | TMPE-232460 | !! HVAC delivered and set up some portable AC units to A210. The units located outside of A210A and A210B1 have stopped working and will not turn on. Both are plugged into two different outlets that are on opposite sides of one wall. Please have staff check on these. Staff can contact Elisabeth in. . . | 2017-04-20 - 18010 - Jennifer Moyer-Deliver smaller portable units and bring back the larger ones. - Jennifer Moyer; 2017-04-20 - 18010 - Derek Gittings-Deliver smaller portable units and bring back the larger ones. - Jennifer Moyer; 2017-04-20 - 18010 - Jennifer Moyer-Went back to job site to see if the units installed were running correctly and to install some ceiling tile beside the exhaust vent. - Jennifer Moyer | !! HVAC delivered and set up some portable AC units to A210. The units located outside of A210A and A210B1 have stopped working and will not turn on. Both are plugged into two different outlets that are on opposite sides of one wall. Please have staff check on these. Staff can contact Elisabeth in. . . 2017-04-20 - 18010 - Jennifer Moyer-Deliver smaller portable units and bring back the larger ones. - Jennifer Moyer; 2017-04-20 - 18010 - Derek Gittings-Deliver smaller portable units and bring back the larger ones. - Jennifer Moyer; 2017-04-20 - 18010 - Jennifer Moyer-Went back to job site to see if the units installed were running correctly and to install some ceiling tile beside the exhaust vent. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 17727 | TMPE-232430 | ADD: CA shop *original message* SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Propo. . . | NA | ADD: CA shop *original message* SPECIAL FUNDING: replace eight evaporative coolers on the roof of PE West. Currently the coolers drain and bleed off to the roof drains which discharge on to the ground on two sides of the building causing standing water in the landscape and walking paths. Propo. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 17728 | TMPE-232429 | USB - 2nd floor: The A/C unit is making a loud noise - was told it was a bearing noise. Please have someone check the unit that services the CAD area and the Service Center area. | 2017-05-13 - 18050 - Robert Dauscher-found bad motor... No suitable replacement motor in stock. need to order motor and cap - Robert Dauscher; 2017-05-13 - 18050 - Robert Dauscher-picked up and replaced motor and cap - Robert Dauscher | USB - 2nd floor: The A/C unit is making a loud noise - was told it was a bearing noise. Please have someone check the unit that services the CAD area and the Service Center area. 2017-05-13 - 18050 - Robert Dauscher-found bad motor... No suitable replacement motor in stock. need to order motor and cap - Robert Dauscher; 2017-05-13 - 18050 - Robert Dauscher-picked up and replaced motor and cap - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 17785 | TMPE-232372 | Air conditioner making loud noises! It is still working to my knowledge, but I think something might be wrong. Thanks! 4NFDMB2 | NA | Air conditioner making loud noises! It is still working to my knowledge, but I think something might be wrong. Thanks! 4NFDMB2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-19 | 17803 | TMPE-232354 | It is reported, "Starting to get really warm in my office (LSC 488D) and it doesn't feel like the vent / AC is working. Please inspect and service accordingly. Thank you. 42BLHKH | 2017-05-04 - 18290 - John Holloway-This issue has been addressed in the past. The supply air duct from the doorway down to and including 488D needs insulation on the supply duct. I need to create a MWO for HVAC - John Holloway | It is reported, "Starting to get really warm in my office (LSC 488D) and it doesn't feel like the vent / AC is working. Please inspect and service accordingly. Thank you. 42BLHKH 2017-05-04 - 18290 - John Holloway-This issue has been addressed in the past. The supply air duct from the doorway down to and including 488D needs insulation on the supply duct. I need to create a MWO for HVAC - John Holloway | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-04-19 | 17806 | TMPE-232351 | ADD TO HVAC assistance with temporary units and working with fan coils repair/ replacement for 4 units for 2nd floor of interdisciplinary A. *original message* Please Transfer WO 232098 to HVAC. Leak is coming from chiller line at a coupling. I have the tile removed and a bucket underneath *. . . | 2017-04-19 - 18010 - Brian Qualls-Installed temporary cooling units in the following locations: Rm 212- Outside Rm 212A " " - Outside Rm 212B Rm 210- Outside Rm 210A Rm 210B- Outside Rm 210B1 Rm 210C- Outside Rm 210C1 - Brian Qualls; 2017-04-19 - 18010 - Jennifer Moyer-Installed temporary cooling units in the following locations: Rm 212- Outside Rm 212A " " - Outside Rm 212B Rm 210- Outside Rm 210A Rm 210B- Outside Rm 210B1 Rm 210C- Outside Rm 210C1 - Brian Qualls; 2017-05-03 - 18010 - Jennifer Moyer-Gathered 5 portable a/c units to be returned to the shop. - Jennifer Moyer; 2017-05-03 - 18010 - Derek Gittings-Gathered 5 portable a/c units to be returned to the shop. - Jennifer Moyer | ADD TO HVAC assistance with temporary units and working with fan coils repair/ replacement for 4 units for 2nd floor of interdisciplinary A. *original message* Please Transfer WO 232098 to HVAC. Leak is coming from chiller line at a coupling. I have the tile removed and a bucket underneath *. . . 2017-04-19 - 18010 - Brian Qualls-Installed temporary cooling units in the following locations: Rm 212- Outside Rm 212A " " - Outside Rm 212B Rm 210- Outside Rm 210A Rm 210B- Outside Rm 210B1 Rm 210C- Outside Rm 210C1 - Brian Qualls; 2017-04-19 - 18010 - Jennifer Moyer-Installed temporary cooling units in the following locations: Rm 212- Outside Rm 212A " " - Outside Rm 212B Rm 210- Outside Rm 210A Rm 210B- Outside Rm 210B1 Rm 210C- Outside Rm 210C1 - Brian Qualls; 2017-05-03 - 18010 - Jennifer Moyer-Gathered 5 portable a/c units to be returned to the shop. - Jennifer Moyer; 2017-05-03 - 18010 - Derek Gittings-Gathered 5 portable a/c units to be returned to the shop. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-04-19 | 17808 | TMPE-232349 | !! A/C unit in back cooking area at Pei Wei is not working. The A//C unit is on the back dock on top of a walk in cooler. Temperatures are very hot in the back cooking area. Please repair unit. Thanks Submitted by 4O33E90 | 2017-04-25 - 18010 - Gail Jackson-Found Tstat with cooking grease running out; we observed in past this unit condenser on loading dock cooler has not ran for months. Tstat is poorly placed on stainless steel wail but in area it serves, how long will Braeburn last, maybe grease proof. Found A/H in ceiling area over Einstein Bagels. Test Run COMPLETE. - Gail Jackson; 2017-04-25 - 18010 - Thomas Gibble-Found Tstat with cooking grease running out; we observed in past this unit condenser on loading dock cooler has not ran for months. Tstat is poorly placed on stainless steel wail but in area it serves, how long will Braeburn last, maybe grease proof. Found A/H in ceiling area over Einstein Bagels. Test Run COMPLETE. - Gail Jackson | !! A/C unit in back cooking area at Pei Wei is not working. The A//C unit is on the back dock on top of a walk in cooler. Temperatures are very hot in the back cooking area. Please repair unit. Thanks Submitted by 4O33E90 2017-04-25 - 18010 - Gail Jackson-Found Tstat with cooking grease running out; we observed in past this unit condenser on loading dock cooler has not ran for months. Tstat is poorly placed on stainless steel wail but in area it serves, how long will Braeburn last, maybe grease proof. Found A/H in ceiling area over Einstein Bagels. Test Run COMPLETE. - Gail Jackson; 2017-04-25 - 18010 - Thomas Gibble-Found Tstat with cooking grease running out; we observed in past this unit condenser on loading dock cooler has not ran for months. Tstat is poorly placed on stainless steel wail but in area it serves, how long will Braeburn last, maybe grease proof. Found A/H in ceiling area over Einstein Bagels. Test Run COMPLETE. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-19 | 229594 | POLY-118604 | GREASE THE FOLLOWING: NORTH ROOF (1) EXHAUST FAN AHU #1 & #2 MEZZANIE (2) AIR COMPRESSOR MOTORS LAB EXHAUST FAN #1 & #2 (2) HEAT RECOVERY PUMPS AHU #3 MAU #2 CHILLER AREA (2) WATER PUMPS 4O216EO | 2017-05-01 - 18010 - Allan Blair-greased - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-greased - Steve Clark | GREASE THE FOLLOWING: NORTH ROOF (1) EXHAUST FAN AHU #1 & #2 MEZZANIE (2) AIR COMPRESSOR MOTORS LAB EXHAUST FAN #1 & #2 (2) HEAT RECOVERY PUMPS AHU #3 MAU #2 CHILLER AREA (2) WATER PUMPS 4O216EO 2017-05-01 - 18010 - Allan Blair-greased - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-greased - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6
2017-04-19 | 229610 | POLY-118588 | GREASE: (10) EXHAUST FANS (3) A/H BLOWER SHAFTS (1) CIRCULATION PUMP (1) VACUUM PUMP MOTOR 4O216EO | 2017-05-01 - 18010 - Allan Blair-greased items - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-greased items - Steve Clark | GREASE: (10) EXHAUST FANS (3) A/H BLOWER SHAFTS (1) CIRCULATION PUMP (1) VACUUM PUMP MOTOR 4O216EO 2017-05-01 - 18010 - Allan Blair-greased items - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-greased items - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-20 | 17545 | TMPE-232612 | !! Hello, The air compressor for the building's air supply in USE 168A has sprung a very loud leak. I can hear and feel high pressure air escaping, so i manually shut off the breaker switch for the compressor. Can someone please come take a look at it? Thank you. 42A89JG | 2017-05-04 - 18030 - Derek Gittings-replacing drier fillter. - Derek Gittings; 2017-05-08 - 18030 - Derek Gittings-repiping and replacing regulater - Derek Gittings; 2017-05-10 - 18030 - Derek Gittings-replaced oil seporater pipe work. - Derek Gittings | !! Hello, The air compressor for the building's air supply in USE 168A has sprung a very loud leak. I can hear and feel high pressure air escaping, so i manually shut off the breaker switch for the compressor. Can someone please come take a look at it? Thank you. 42A89JG 2017-05-04 - 18030 - Derek Gittings-replacing drier fillter. - Derek Gittings; 2017-05-08 - 18030 - Derek Gittings-repiping and replacing regulater - Derek Gittings; 2017-05-10 - 18030 - Derek Gittings-replaced oil seporater pipe work. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
2017-04-20 | 17572 | TMPE-232585 | PSB B330U2 Pump #502 leaking almost to the hallway, please address urgently. Thank you! | 2017-04-20 - 23100 - Called out to Oner - Amanda Thomas; 2017-05-16 - 23100 - Derek Gittings-removing and rebuiling pump - Derek Gittings; 2017-05-17 - 23100 - Derek Gittings-removing and rebuilding pump. - Derek Gittings | PSB B330U2 Pump #502 leaking almost to the hallway, please address urgently. Thank you! 2017-04-20 - 23100 - Called out to Oner - Amanda Thomas; 2017-05-16 - 23100 - Derek Gittings-removing and rebuiling pump - Derek Gittings; 2017-05-17 - 23100 - Derek Gittings-removing and rebuilding pump. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-20 | 17577 | TMPE-232580 | Need a Scheduled WO for TS to Troubleshoot and air leak in the 1st floor pre-action fire sprinkling system at Goldwater. 42A1LA1 | 2017-04-20 - 17000 - Kevin Cunningham-Checked for leaks on pre-action valve and all related plumbing in the same room. Found and repaired a couple small leaks. Did not resolve problem of air loss we timed the time between the start of the compressor... it comes on every 22.5 minutes (approx.) suspect leaks in the field. Also the pump stops at 30PSI and comes on at 20PSI. - Kevin Cunningham; 2017-04-20 - 17000 - James Burley-Checked for leaks on pre-action valve and all related plumbing in the same room. Found and repaired a couple small leaks. Did not resolve problem of air loss we timed the time between the start of the compressor... it comes on every 22.5 minutes (approx.) suspect leaks in the field. Also the pump stops at 30PSI and comes on at 20PSI. - Kevin Cunningham; 2017-05-04 - 17000 - James Burley-assisted contractor with job layout - James Burley | Need a Scheduled WO for TS to Troubleshoot and air leak in the 1st floor pre-action fire sprinkling system at Goldwater. 42A1LA1 2017-04-20 - 17000 - Kevin Cunningham-Checked for leaks on pre-action valve and all related plumbing in the same room. Found and repaired a couple small leaks. Did not resolve problem of air loss we timed the time between the start of the compressor... it comes on every 22.5 minutes (approx.) suspect leaks in the field. Also the pump stops at 30PSI and comes on at 20PSI. - Kevin Cunningham; 2017-04-20 - 17000 - James Burley-Checked for leaks on pre-action valve and all related plumbing in the same room. Found and repaired a couple small leaks. Did not resolve problem of air loss we timed the time between the start of the compressor... it comes on every 22.5 minutes (approx.) suspect leaks in the field. Also the pump stops at 30PSI and comes on at 20PSI. - Kevin Cunningham; 2017-05-04 - 17000 - James Burley-assisted contractor with job layout - James Burley | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-04-20 | 17641 | TMPE-232516 | for Ac/me shop-sewage ejection pump-talked to Brian Qualls..ASUHC-Agent Brandon Gillespie Description Alarm sounding from MU basement door 82. Not a fire alarm?!? Who was dispatched Kevin Cunningham Time of dispatch 7:44pm | 2017-04-20 - 23100 - Brian Qualls-Found alarm float had slipped below lead float causing alarm to sound prematurely. Raised float and secured. Also found pumps not alternating. Relay coil is open. Replacement on order. - Brian Qualls; 2017-04-20 - 23100 - Derek Gittings-Found alarm float had slipped below lead float causing alarm to sound prematurely. Raised float and secured. Also found pumps not alternating. Relay coil is open. Replacement on order. - Brian Qualls | for Ac/me shop-sewage ejection pump-talked to Brian Qualls..ASUHC-Agent Brandon Gillespie Description Alarm sounding from MU basement door 82. Not a fire alarm?!? Who was dispatched Kevin Cunningham Time of dispatch 7:44pm 2017-04-20 - 23100 - Brian Qualls-Found alarm float had slipped below lead float causing alarm to sound prematurely. Raised float and secured. Also found pumps not alternating. Relay coil is open. Replacement on order. - Brian Qualls; 2017-04-20 - 23100 - Derek Gittings-Found alarm float had slipped below lead float causing alarm to sound prematurely. Raised float and secured. Also found pumps not alternating. Relay coil is open. Replacement on order. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-20 | 17648 | TMPE-232509 | Please have the HVAC Shop perform a pre-summer maintenance on fan coil units, Ice machine and refrigerators of the Suites Michael Crows Suite. Walk needs to be completed by 5/12/17. PO is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.. . . | 2017-05-04 - 18010 - Robert Ecabert-Cleaned and sanitized one ice machine. This ice machine is running now and making ice just fine. - Robert Ecabert; 2017-05-04 - 18010 - Robert Ecabert-Cleaned and sanitized the second ice machine. This ice machine is running and making ice just fine. The first refrigerator is running fine and maintaining the temperature at 37 degrees farenheit. The second refrigerator in this room had the evaporator section all frozen up so i defrosted it with a heat gun and i unplugged the unit so it will finish defrosting over night. I will stop back tomorrow to see if it has defrosted completely. I checked the 3 fan coil units in this room and they are running fine. - Robert Ecabert; 2017-05-04 - 18010 - Robert Ecabert-Cleaned the second ice machine in this room. The second ice machine in this room is up and running now. The first refrigerator I checked in this room is at 37 degrees and running fine. On the second refrigerator in this room the door was left ajar and the evaporator section was a frozen solid block of ice. So I defrosted it with a heat gun and turned the refrigerator back on. The reason the door was left ajar on the refrigerator was because somebody bent the tab on the bottom of the door not allowing it to close. I fixed the tab on the bottom of the door and now it closes just fine. I checked all 3 fan coil units in this room and all 3 running. - Robert Ecabert | Please have the HVAC Shop perform a pre-summer maintenance on fan coil units, Ice machine and refrigerators of the Suites Michael Crows Suite. Walk needs to be completed by 5/12/17. PO is YG202004971. Thank you. Contact Name: Pete Wozniak Contact Phone Number: 602-723-0715 Contact Email: Peter.. . . 2017-05-04 - 18010 - Robert Ecabert-Cleaned and sanitized one ice machine. This ice machine is running now and making ice just fine. - Robert Ecabert; 2017-05-04 - 18010 - Robert Ecabert-Cleaned and sanitized the second ice machine. This ice machine is running and making ice just fine. The first refrigerator is running fine and maintaining the temperature at 37 degrees farenheit. The second refrigerator in this room had the evaporator section all frozen up so i defrosted it with a heat gun and i unplugged the unit so it will finish defrosting over night. I will stop back tomorrow to see if it has defrosted completely. I checked the 3 fan coil units in this room and they are running fine. - Robert Ecabert; 2017-05-04 - 18010 - Robert Ecabert-Cleaned the second ice machine in this room. The second ice machine in this room is up and running now. The first refrigerator I checked in this room is at 37 degrees and running fine. On the second refrigerator in this room the door was left ajar and the evaporator section was a frozen solid block of ice. So I defrosted it with a heat gun and turned the refrigerator back on. The reason the door was left ajar on the refrigerator was because somebody bent the tab on the bottom of the door not allowing it to close. I fixed the tab on the bottom of the door and now it closes just fine. I checked all 3 fan coil units in this room and all 3 running. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-04-20 | 229559 | POLY-118639 | GREASE 35 DIFFERENT MOTORS, SHAFT BEARNINGS, PUMPS AND EXHAUST FANS 4O216EO | 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark | GREASE 35 DIFFERENT MOTORS, SHAFT BEARNINGS, PUMPS AND EXHAUST FANS 4O216EO 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Allan Blair-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark; 2017-05-01 - 18230 - Darusman Amin-greased fitting on building - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-20 | 249651 | DTPC-118887 | Help TDI change out AHU 1 exhaust motor #1 | 2017-04-21 - 18050 - Thomas Klein-Helped TDI, Shut down AHU 1 and re-started when work was completed. - Thomas Klein | Help TDI change out AHU 1 exhaust motor #1 2017-04-21 - 18050 - Thomas Klein-Helped TDI, Shut down AHU 1 and re-started when work was completed. - Thomas Klein | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-20 | 249676 | DTPC-118862 | PM Air Compressor | 2017-04-20 - xPM-0100-B - Robert Bartels-Check volts, amps, belts, filter, oil - Robert Bartels | PM Air Compressor 2017-04-20 - xPM-0100-B - Robert Bartels-Check volts, amps, belts, filter, oil - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-21 | 160050 | RFMT-148281 | !! There is no air coming out of the vents, and a very foul smell is filling the room. Please address urgently, thank you. Submitted by 4O077C3 | 2017-04-21 - 18010 - Rene Arrieta-replace a/c filter - Rene Arrieta | !! There is no air coming out of the vents, and a very foul smell is filling the room. Please address urgently, thank you. Submitted by 4O077C3 2017-04-21 - 18010 - Rene Arrieta-replace a/c filter - Rene Arrieta | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-21 | 17389 | TMPE-232768 | !! Air conditioning was broken in March and repaired, but seems to not be working again. It is 84 degrees and rising. Help!!! 4N0J2L9 | 2017-05-01 - 18290 - Robert Borucki-Checked A/H6A status, down for repairs. - Robert Borucki | !! Air conditioning was broken in March and repaired, but seems to not be working again. It is 84 degrees and rising. Help!!! 4N0J2L9 2017-05-01 - 18290 - Robert Borucki-Checked A/H6A status, down for repairs. - Robert Borucki | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-04-21 | 17418 | TMPE-232739 | PLUMBING Drinking fountains on third AND fourth floor don't work properly. This is a repeated problem. Could we have them switched out to push button bubblers? Contact Name: Paul Iannone Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B | 2017-04-25 - 23080 - Bruno Lara-Complete The push lever was very loose indicating that it had separated from the mounting bracket. Opened the panel and found the lever was out of place. Inserted a snap ring onto the base of the lever to prevent it from being pulled out of place. Adjusted the nut to regulate the amount of water flow. Cleaned the condenser and fan motor along with the fan blades. Repeated the same process for the 4th fl. water fountain. 1.50 Materials - none - Bruno Lara | PLUMBING Drinking fountains on third AND fourth floor don't work properly. This is a repeated problem. Could we have them switched out to push button bubblers? Contact Name: Paul Iannone Contact Phone Number: 480.323.6325 Contact Email: 42B1A9B 2017-04-25 - 23080 - Bruno Lara-Complete The push lever was very loose indicating that it had separated from the mounting bracket. Opened the panel and found the lever was out of place. Inserted a snap ring onto the base of the lever to prevent it from being pulled out of place. Adjusted the nut to regulate the amount of water flow. Cleaned the condenser and fan motor along with the fan blades. Repeated the same process for the 4th fl. water fountain. 1.50 Materials - none - Bruno Lara | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-04-21 | 17420 | TMPE-232737 | Need a Routine WO for TS to troubleshoot an open circuit trouble condition on the Fire System at PSC. 42A1LA1 | 2017-04-28 - 17000 - Terence Welsh-Trbl shoot open ckt. Traced to CR modules in 3rd floor fan room that had water dripping on them from an improperly installed condensate line from an AHU in the room. HVAC to return to reroute the line before we can replace the modules. - Terence Welsh | Need a Routine WO for TS to troubleshoot an open circuit trouble condition on the Fire System at PSC. 42A1LA1 2017-04-28 - 17000 - Terence Welsh-Trbl shoot open ckt. Traced to CR modules in 3rd floor fan room that had water dripping on them from an improperly installed condensate line from an AHU in the room. HVAC to return to reroute the line before we can replace the modules. - Terence Welsh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-21 | 17441 | TMPE-232716 | The condenser fan motor is seized. | 2017-05-18 - 18290 - Zhi Yu-This unit condenser fan motor is been change by other technician. - Zhi Yu | The condenser fan motor is seized. 2017-05-18 - 18290 - Zhi Yu-This unit condenser fan motor is been change by other technician. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-21 | 229538 | POLY-118660 | Palo Blanco\\u2019s air conditioning is being reported as not working for the entire building. **STEVE - oil pump not building sufficient pressure during pre lub cycle - per Juan. Please see Juan for any questions Can we please have someone investigate and repair. Thank you, George Vasquez . . . | 2017-05-03 - 18290 - Suresh Nair-TOPPED OFF CHARGE, UNIT NEEDS ADDITIONAL WORK - REPLACE OIL FILTERS - Steve Clark; 2017-05-03 - 18290 - Esli Arvizo-TOPPED OFF CHARGE, UNIT NEEDS ADDITIONAL WORK - REPLACE OIL FILTERS - Steve Clark | Palo Blanco\\u2019s air conditioning is being reported as not working for the entire building. **STEVE - oil pump not building sufficient pressure during pre lub cycle - per Juan. Please see Juan for any questions Can we please have someone investigate and repair. Thank you, George Vasquez . . . 2017-05-03 - 18290 - Suresh Nair-TOPPED OFF CHARGE, UNIT NEEDS ADDITIONAL WORK - REPLACE OIL FILTERS - Steve Clark; 2017-05-03 - 18290 - Esli Arvizo-TOPPED OFF CHARGE, UNIT NEEDS ADDITIONAL WORK - REPLACE OIL FILTERS - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-21 | 249641 | DTPC-118897 | Air conditioner not cooling 3-8 | 2017-04-21 - 18010 - Jose Acero-A/C not cooling troubleshoot unit and found fan motor and capacitor not working - Jose Acero | Air conditioner not cooling 3-8 2017-04-21 - 18010 - Jose Acero-A/C not cooling troubleshoot unit and found fan motor and capacitor not working - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-22 | 17083 | TMPE-233074 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-22 | 17084 | TMPE-233073 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-22 | 17136 | TMPE-233021 | DX Equipment-Biannual | 2017-04-26 - xPM-1700-B - Matthew Smith-Found the unit shut off. Call the AC shop and found that they had submitted bids to replace the unit as it is leaking refrigerant and is unable to locate the leaks. - Matthew Smith [Modified: 2017-04-26 Matthew Smith]; 2017-04-26 - xPM-1700-B - Michael Bauer-Found the unit shut off. Call the AC shop and found that they had submitted bids to replace the unit as it is leaking refrigerant and is unable to locate the leaks. - Matthew Smith [Modified: 2017-04-26 Matthew Smith] | DX Equipment-Biannual 2017-04-26 - xPM-1700-B - Matthew Smith-Found the unit shut off. Call the AC shop and found that they had submitted bids to replace the unit as it is leaking refrigerant and is unable to locate the leaks. - Matthew Smith [Modified: 2017-04-26 Matthew Smith]; 2017-04-26 - xPM-1700-B - Michael Bauer-Found the unit shut off. Call the AC shop and found that they had submitted bids to replace the unit as it is leaking refrigerant and is unable to locate the leaks. - Matthew Smith [Modified: 2017-04-26 Matthew Smith] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-22 | 17256 | TMPE-232901 | Exhaust Fan-Biannual | 2017-04-28 - xPM-2100.01-B - Michael Bauer- Found a bad motor ..needs replaced. I believe this unit and motor came from graingers.. unit is in the attic of room # 422 - Michael Bauer; 2017-04-28 - xPM-2100.01-B - Michael Bauer-found bad motor..Needs replaced.Access from room #422 - Michael Bauer | Exhaust Fan-Biannual 2017-04-28 - xPM-2100.01-B - Michael Bauer- Found a bad motor ..needs replaced. I believe this unit and motor came from graingers.. unit is in the attic of room # 422 - Michael Bauer; 2017-04-28 - xPM-2100.01-B - Michael Bauer-found bad motor..Needs replaced.Access from room #422 - Michael Bauer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-23 | 564 | WEST-110685 | Portable Generator Maintenance-Monthly | NA | Portable Generator Maintenance-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-23 | 16876 | TMPE-233281 | ASU Agent: Laura Bennett Description: Air Handler has a bad motor. Needs to be replaced. Dispatched: Robert Dauscher Time of Dispatch: 12:25p Location: A wing | 2017-04-25 - 18230 - Roque Garcia-replaced motor,rewire.line up belts. - Derek Gittings; 2017-04-25 - 18230 - Roque Garcia-replaced motor,rewire.line up belts. - Derek Gittings; 2017-04-26 - 18230 - Derek Gittings-replaced motor. - Derek Gittings | ASU Agent: Laura Bennett Description: Air Handler has a bad motor. Needs to be replaced. Dispatched: Robert Dauscher Time of Dispatch: 12:25p Location: A wing 2017-04-25 - 18230 - Roque Garcia-replaced motor,rewire.line up belts. - Derek Gittings; 2017-04-25 - 18230 - Roque Garcia-replaced motor,rewire.line up belts. - Derek Gittings; 2017-04-26 - 18230 - Derek Gittings-replaced motor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-23 | 229528 | POLY-118670 | !! Air conditioning is not working. Have had the thermostat set to 74 degrees all day and the temperature of the house stays at approximately 83 degrees. 4NJF5L1 | NA | !! Air conditioning is not working. Have had the thermostat set to 74 degrees all day and the temperature of the house stays at approximately 83 degrees. 4NJF5L1 NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-24 | 16718 | TMPE-233438 | BIKE LOCK CUT - the bike is located in the front of Noble Library. | 2017-04-27 - 11010 - Derek Gittings-cut lock off. - Derek Gittings | BIKE LOCK CUT - the bike is located in the front of Noble Library. 2017-04-27 - 11010 - Derek Gittings-cut lock off. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2017-04-24 | 16741 | TMPE-233415 | BDA WO for HVAC Shop Please provide 156 (one hundred fifty six) 24 " x 24 " x 4 " pre filters which equates to 26 boxes ....We are out of filters for changing out in the penthouse! Can deliver in reasonable quantities considering size of order Thanks Jeffrey 4N00ABB | 2017-04-27 - 18170 - Jose Mazon-FILTERS DELEVIRY DONE. - Jose Mazon; 2017-04-27 - 18170 - Austen Jackson-job done - Jose Mazon | BDA WO for HVAC Shop Please provide 156 (one hundred fifty six) 24 " x 24 " x 4 " pre filters which equates to 26 boxes ....We are out of filters for changing out in the penthouse! Can deliver in reasonable quantities considering size of order Thanks Jeffrey 4N00ABB 2017-04-27 - 18170 - Jose Mazon-FILTERS DELEVIRY DONE. - Jose Mazon; 2017-04-27 - 18170 - Austen Jackson-job done - Jose Mazon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-24 | 16746 | TMPE-233410 | ADD AC to assist: add Jennifer Moyer Please have the Plumbing Shop repair the leaking shower head in 112W1 at SDSP. PO is YG202004938. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF | 2017-04-25 - 23130 - Jennifer Moyer-Made sure restroom was clear of women. - Jennifer Moyer | ADD AC to assist: add Jennifer Moyer Please have the Plumbing Shop repair the leaking shower head in 112W1 at SDSP. PO is YG202004938. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF 2017-04-25 - 23130 - Jennifer Moyer-Made sure restroom was clear of women. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-24 | 16820 | TMPE-233337 | HAV - POD Market: Please create a work order to fix the freezer inside the HAV POD MARKET It currently is running very warm Thanks Jim Emmons | 2017-05-05 - 18180 - Gail Jackson-Leak check unit, found leak in low side pressure line at head; suspect there are more; compressor very noisy; rattles at start up. Added 15 lbs 404A. - Gail Jackson; 2017-05-05 - 18180 - Thomas Gibble-Leak check unit, found leak in low side pressure line at head; suspect there are more; compressor very noisy; rattles at start up. Added 15 lbs 404A. - Gail Jackson | HAV - POD Market: Please create a work order to fix the freezer inside the HAV POD MARKET It currently is running very warm Thanks Jim Emmons 2017-05-05 - 18180 - Gail Jackson-Leak check unit, found leak in low side pressure line at head; suspect there are more; compressor very noisy; rattles at start up. Added 15 lbs 404A. - Gail Jackson; 2017-05-05 - 18180 - Thomas Gibble-Leak check unit, found leak in low side pressure line at head; suspect there are more; compressor very noisy; rattles at start up. Added 15 lbs 404A. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-24 | 16827 | TMPE-233330 | Install new electrical panel to service 8 new cart charging stations on the East side of building on concrete pad next to air compressor. | NA | Install new electrical panel to service 8 new cart charging stations on the East side of building on concrete pad next to air compressor. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 16864 | TMPE-233293 | AC seems to not be working completely. We've been adjusting the thermostat but there only a small breeze of cooler air that comes into the rooms: 154, 155, 156. This is not enough to cool the rooms down though and it shows that it is 5 degrees warmer than what the setting is. Thank you for your help. . . | 2017-04-28 - 18290 - Gail Jackson-Found condensing unit out on high head; old RUUD , pressed reset. Washed all three coils, compressors have all been replaced in these units, nearing end of service life. Checked duck work for obstructions. Complete. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found condensing unit out on high head; old RUUD , pressed reset. Washed all three coils, compressors have all been replaced in these units, nearing end of service life. Checked duck work for obstructions. Complete. - Gail Jackson | AC seems to not be working completely. We've been adjusting the thermostat but there only a small breeze of cooler air that comes into the rooms: 154, 155, 156. This is not enough to cool the rooms down though and it shows that it is 5 degrees warmer than what the setting is. Thank you for your help. . . 2017-04-28 - 18290 - Gail Jackson-Found condensing unit out on high head; old RUUD , pressed reset. Washed all three coils, compressors have all been replaced in these units, nearing end of service life. Checked duck work for obstructions. Complete. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found condensing unit out on high head; old RUUD , pressed reset. Washed all three coils, compressors have all been replaced in these units, nearing end of service life. Checked duck work for obstructions. Complete. - Gail Jackson | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-04-24 | 16911 | TMPE-233246 | ECD 101U1 Air Compressor continually running, and there is possibly a leak as you can hear a hissing sound. | 2017-04-25 - 18030 - Dispatched Steve Palombo 4/24 (FF) - Francesca Fernandez; 2017-04-25 - 18030 - Brian Qualls-Pressure safety valve on back-up compressor was blowing off at only 100psi. Replaced valve and tank pressure gauge. Check ops, all OK. - Brian Qualls | ECD 101U1 Air Compressor continually running, and there is possibly a leak as you can hear a hissing sound. 2017-04-25 - 18030 - Dispatched Steve Palombo 4/24 (FF) - Francesca Fernandez; 2017-04-25 - 18030 - Brian Qualls-Pressure safety valve on back-up compressor was blowing off at only 100psi. Replaced valve and tank pressure gauge. Check ops, all OK. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4
2017-04-24 | 159811 | RFMT-148520 | Weekly Building PM Inspection. | 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | Weekly Building PM Inspection. 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 159815 | RFMT-148516 | Weekly Building PM Inspection. | 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | Weekly Building PM Inspection. 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 159816 | RFMT-148515 | Weekly Building PM Inspection. | 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | Weekly Building PM Inspection. 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 159817 | RFMT-148514 | Weekly Building PM Inspection. | 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | Weekly Building PM Inspection. 2017-04-28 - 50051 - Salvatore Marasco Jr-Walked and checked building. Inventoried a/c filters and staged filters for room turns in storage closets. - Salvatore Marasco Jr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 159818 | RFMT-148513 | Weekly Building PM Inspection. | 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas, and made repairs as needed - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds checked all common areas,and made repairs as needed. - John Romero; 2017-05-01 - 50051 - John Romero-Removed fan blower motor from bathroom 100W1 - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas making repairs as needed. Replace outlet cover plate E-127 - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas, and making repairs as needed. - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds,checked all common areas, making repairs as needed - John Romero | Weekly Building PM Inspection. 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas, and made repairs as needed - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds checked all common areas,and made repairs as needed. - John Romero; 2017-05-01 - 50051 - John Romero-Removed fan blower motor from bathroom 100W1 - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas making repairs as needed. Replace outlet cover plate E-127 - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds, checked all common areas, and making repairs as needed. - John Romero; 2017-05-01 - 50051 - John Romero-Walked the building and grounds,checked all common areas, making repairs as needed - John Romero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-24 | 159933 | RFMT-148398 | !! Our AC is broken. It started making weird screeching noises while is was on and now it doesn't push out air and it randomly switched on and off Contact Name: Cassidy Brown Contact Phone Number: 8603248845 Contact Email: 4NOONC5 | 2017-04-25 - 18010 - Chester Duncan-Replaced blower motor and cap run replaced bulbs - Chester Duncan | !! Our AC is broken. It started making weird screeching noises while is was on and now it doesn't push out air and it randomly switched on and off Contact Name: Cassidy Brown Contact Phone Number: 8603248845 Contact Email: 4NOONC5 2017-04-25 - 18010 - Chester Duncan-Replaced blower motor and cap run replaced bulbs - Chester Duncan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-04-24 | 209824 | RACC-118786 | !! Fixing the cool air on the air conditioning unit. The cool air does not turn on, regardless of the settings on the thermostat. 4O1KHB4 | NA | !! Fixing the cool air on the air conditioning unit. The cool air does not turn on, regardless of the settings on the thermostat. 4O1KHB4 NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-24 | 209854 | RACC-118756 | The air conditioner/fan/vent on the C/D side of the apartment isn't working properly. When we set it to a cooler temperature, it doesn't really blow cool air and the temperature of the room stays pretty high. We set it to cool and the desired temperature to 70 degrees but it never got below 76 degre. . . | 2017-04-26 - 10010 - replaced fuse Aaron - Jim Deal | The air conditioner/fan/vent on the C/D side of the apartment isn't working properly. When we set it to a cooler temperature, it doesn't really blow cool air and the temperature of the room stays pretty high. We set it to cool and the desired temperature to 70 degrees but it never got below 76 degre. . . 2017-04-26 - 10010 - replaced fuse Aaron - Jim Deal | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-04-24 | 249586 | DTPC-118952 | help ti contractors locate chase for new duct work on second and third floor | 2017-04-24 - 10000 - Steve Skibbe-located shaft we believe to be the right one for ti exhaust - Steve Skibbe; 2017-04-28 - 10000 - Steve Skibbe-duct work found this is complete - Steve Skibbe | help ti contractors locate chase for new duct work on second and third floor 2017-04-24 - 10000 - Steve Skibbe-located shaft we believe to be the right one for ti exhaust - Steve Skibbe; 2017-04-28 - 10000 - Steve Skibbe-duct work found this is complete - Steve Skibbe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 11555 | TMPE-238601 | Naumann Hobbs Located unit and found 4 valve stems needed. Removed tires and replaced valve stems. Reassembled tires and installed on cart. total: 176.62 | NA | Naumann Hobbs Located unit and found 4 valve stems needed. Removed tires and replaced valve stems. Reassembled tires and installed on cart. total: 176.62 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2017-04-25 | 11656 | TMPE-238500 | Naumann Hobbs Diagnosed that unit need turn signal switch. total: 35.33 | NA | Naumann Hobbs Diagnosed that unit need turn signal switch. total: 35.33 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 16539 | TMPE-233617 | WTF 110 !! Two of the three AC units at Wrestling are not working. The circuit breaker keeps tripping after it is re-set. PO is YG202004954. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF | 2017-05-11 - 18010 - Roque Garcia-The AC units where previous serviced by an outside contractor. The outside contractor replaced R22 with R438. I called Steve and he was going to care of the WO - Roque Garcia | WTF 110 !! Two of the three AC units at Wrestling are not working. The circuit breaker keeps tripping after it is re-set. PO is YG202004954. Thank you. Contact Name: Eric Voelz Contact Phone Number: 734-778-1844 Contact Email: Eric.Voelz@asu.edu 42BDEDF 2017-05-11 - 18010 - Roque Garcia-The AC units where previous serviced by an outside contractor. The outside contractor replaced R22 with R438. I called Steve and he was going to care of the WO - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-25 | 16589 | TMPE-233567 | Chamber 354 not holding temp. assigned to Duane Rider | 2017-05-05 - 18140 - Duane Rider-Replaced TXV and Compressor oil - Duane Rider; 2017-05-05 - 18140 - Duane Rider-Recovered refrigerant and replaced two dryers - Duane Rider; 2017-05-05 - 18140 - Duane Rider-Recovered refrigerant and replaced two dryers - Duane Rider | Chamber 354 not holding temp. assigned to Duane Rider 2017-05-05 - 18140 - Duane Rider-Replaced TXV and Compressor oil - Duane Rider; 2017-05-05 - 18140 - Duane Rider-Recovered refrigerant and replaced two dryers - Duane Rider; 2017-05-05 - 18140 - Duane Rider-Recovered refrigerant and replaced two dryers - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-25 | 16617 | TMPE-233539 | Hello, The Air conditioning is not working in the computer lab, USE 170A. Can someone please take a look at it? Thank you. 42A89JG | 2017-04-28 - 18290 - Gail Jackson-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson | Hello, The Air conditioning is not working in the computer lab, USE 170A. Can someone please take a look at it? Thank you. 42A89JG 2017-04-28 - 18290 - Gail Jackson-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson; 2017-04-28 - 18290 - Thomas Gibble-Found blower motor burned out; unit frosted up back to compressor on roof. Retrieved 10 ft ladder from Phycology BLDG basement to complete work. Trip to ARS Tempe and shop for motor and RC. Install motor run test COMPLETE. Return ladder to basement at Phycology BLDG. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-25 | 16624 | TMPE-233532 | !! Danforth Chapel was reserved over this past weekend for a wedding (4-22-17). The air conditioner was set to 65 degrees when they arrived; however, no air conditioning unit ever turned on. Apparently it is not working at all. 4O52D5K | 2017-05-04 - 18290 - Thomas Gibble-found unit empty. TXV bulb and equalizer was leaking. two trips to part store. - Thomas Gibble; 2017-05-04 - 18290 - Gail Jackson-found unit empty. TXV bulb and equalizer was leaking. two trips to part store. - Thomas Gibble | !! Danforth Chapel was reserved over this past weekend for a wedding (4-22-17). The air conditioner was set to 65 degrees when they arrived; however, no air conditioning unit ever turned on. Apparently it is not working at all. 4O52D5K 2017-05-04 - 18290 - Thomas Gibble-found unit empty. TXV bulb and equalizer was leaking. two trips to part store. - Thomas Gibble; 2017-05-04 - 18290 - Gail Jackson-found unit empty. TXV bulb and equalizer was leaking. two trips to part store. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-25 | 16629 | TMPE-233527 | ADD EMS - Lost communication from thermostat to unit. Zhi Yu is the HVAC contact. My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. I currently do not have any AC in my office and it is starting to get warm. Is there a way. . . | 2017-04-26 - 18290 - 04.26.17 Left voice message for customer, letting her know I would be there after 13:00 today to check the thermostat. - Cheryl St. John; 2017-05-08 - 18290 - Cheryl St. John-04.25.17 HVAC installed a new HP at UCENT RM 303, EMS didn't know until after the fact. T -stat wouldn't work with new heat pump, EMS determined it was a bad t-stat, EMS ordered new style sensor, waiting on new style thermostat to come in (Novar 1010 old style). - Cheryl St. John | ADD EMS - Lost communication from thermostat to unit. Zhi Yu is the HVAC contact. My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. I currently do not have any AC in my office and it is starting to get warm. Is there a way. . . 2017-04-26 - 18290 - 04.26.17 Left voice message for customer, letting her know I would be there after 13:00 today to check the thermostat. - Cheryl St. John; 2017-05-08 - 18290 - Cheryl St. John-04.25.17 HVAC installed a new HP at UCENT RM 303, EMS didn't know until after the fact. T -stat wouldn't work with new heat pump, EMS determined it was a bad t-stat, EMS ordered new style sensor, waiting on new style thermostat to come in (Novar 1010 old style). - Cheryl St. John | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-25 | 16641 | TMPE-233515 | for the HVAC Shop LSE S10 Vents clogged | NA | for the HVAC Shop LSE S10 Vents clogged NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 16644 | TMPE-233512 | LSE B63 for the HVAC Shop LSE B63 Vents clogged | NA | LSE B63 for the HVAC Shop LSE B63 Vents clogged NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 16646 | TMPE-233510 | for the HVAC Shop LSE S04 Vents clogged | NA | for the HVAC Shop LSE S04 Vents clogged NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 16675 | TMPE-233481 | FOR TOM TO FINISH REPAIRS. ASUHC Agent: Spencer Leisy Description: AC in the ceiling made a loud noise and then completely shut off. Who was dispatched: Tom Gibble Time of Dispatch: 21:10 | 2017-04-25 - 18050 - Thomas Gibble-adjusted puller on motor. adjusted t-stat - Thomas Gibble; 2017-04-25 - 18050 - Gail Jackson-adjusted puller on motor. adjusted t-stat - Thomas Gibble | FOR TOM TO FINISH REPAIRS. ASUHC Agent: Spencer Leisy Description: AC in the ceiling made a loud noise and then completely shut off. Who was dispatched: Tom Gibble Time of Dispatch: 21:10 2017-04-25 - 18050 - Thomas Gibble-adjusted puller on motor. adjusted t-stat - Thomas Gibble; 2017-04-25 - 18050 - Gail Jackson-adjusted puller on motor. adjusted t-stat - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 16681 | TMPE-233475 | ECD, Air Handler 1 is not starting Please create a MWO for the Electricians to troubleshoot the electrical system. Possible bad contactor Air Handler 1 located on the roof, D wing, East end 42DIM5O | 2017-04-25 - 18050 - Semeon Haile-Reset static pressure switch and PM the VFD. Noticed dirty filter need to be addressed HVAC shop - Semeon Haile | ECD, Air Handler 1 is not starting Please create a MWO for the Electricians to troubleshoot the electrical system. Possible bad contactor Air Handler 1 located on the roof, D wing, East end 42DIM5O 2017-04-25 - 18050 - Semeon Haile-Reset static pressure switch and PM the VFD. Noticed dirty filter need to be addressed HVAC shop - Semeon Haile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-25 | 16686 | TMPE-233470 | Matthews Hall - 101: Please contact me about servicing the ac units in MH101. One of them is making noise and we have discontinued use of it. We need it repaired or replaced before the intense heat of the summer. Please email or call my mobile phone, 602.400.4383. | 2017-05-11 - 18050 - Gail Jackson-Washed condenser coils in 3 window units, run test the 1 she called noisy; no unusual noise found, made 3 attempts to call, did not return calls. - Gail Jackson; 2017-05-11 - 18050 - Thomas Gibble-Washed condenser coils in 3 window units, run test the 1 she called noisy; no unusual noise found, made 3 attempts to call, did not return calls. - Gail Jackson | Matthews Hall - 101: Please contact me about servicing the ac units in MH101. One of them is making noise and we have discontinued use of it. We need it repaired or replaced before the intense heat of the summer. Please email or call my mobile phone, 602.400.4383. 2017-05-11 - 18050 - Gail Jackson-Washed condenser coils in 3 window units, run test the 1 she called noisy; no unusual noise found, made 3 attempts to call, did not return calls. - Gail Jackson; 2017-05-11 - 18050 - Thomas Gibble-Washed condenser coils in 3 window units, run test the 1 she called noisy; no unusual noise found, made 3 attempts to call, did not return calls. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 159884 | RFMT-148447 | Please meet with FACMAN Mechanical Dept.in Best C basement regarding the chilled water pumps. Thank you. | 2017-04-26 - 18010 - Thor Millsaps-Met with Jose from FACMAN in Best C basement. Forwarded report to Greg. Report is as follows: Best C Field Report Spoke with Jose L about chilled water pumps 1 and 2 in Best C basement. Jose is finished installing pump 2 but check valve in chilled water line is bad so pump will run backwards when no power is applied. Jose said he must leave pump 2 off until check valve is replaced by plumbers. Pump 1 is running but alignment is off which has likely damaged the motor. Jose will align pump 1 and use it as the only chilled water pump until check valve on pump 2 is replaced. Also, contactor for pump 1 is bad. The coil will not close the contacts. The contactor must be manually pressed in to start pump 1. Jose will tell electricians to replace contactor on pump 1. Jose will manually start pump 1 after he is done with alignment but if contacts open, they will not close again automatically and pump 1 will not start up until contactor is manually pressed. - Thor Millsaps | Please meet with FACMAN Mechanical Dept.in Best C basement regarding the chilled water pumps. Thank you. 2017-04-26 - 18010 - Thor Millsaps-Met with Jose from FACMAN in Best C basement. Forwarded report to Greg. Report is as follows: Best C Field Report Spoke with Jose L about chilled water pumps 1 and 2 in Best C basement. Jose is finished installing pump 2 but check valve in chilled water line is bad so pump will run backwards when no power is applied. Jose said he must leave pump 2 off until check valve is replaced by plumbers. Pump 1 is running but alignment is off which has likely damaged the motor. Jose will align pump 1 and use it as the only chilled water pump until check valve on pump 2 is replaced. Also, contactor for pump 1 is bad. The coil will not close the contacts. The contactor must be manually pressed in to start pump 1. Jose will tell electricians to replace contactor on pump 1. Jose will manually start pump 1 after he is done with alignment but if contacts open, they will not close again automatically and pump 1 will not start up until contactor is manually pressed. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5
2017-04-25 | 229488 | POLY-118710 | Received call that the AC was not working in AGBC room 160. It was cold in the hallway but not in the room. | 2017-05-01 - 18010 - Allan Blair-found and replaced bad damper motor - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-found and replaced bad damper motor - Steve Clark | Received call that the AC was not working in AGBC room 160. It was cold in the hallway but not in the room. 2017-05-01 - 18010 - Allan Blair-found and replaced bad damper motor - Steve Clark; 2017-05-01 - 18010 - Darusman Amin-found and replaced bad damper motor - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-25 | 249560 | DTPC-118978 | Heat pump 3-8 | 2017-04-25 - 18010 - Jose Acero-Diagnose unit due to lack of air flow removed fan motor and Capacitor - Jose Acero | Heat pump 3-8 2017-04-25 - 18010 - Jose Acero-Diagnose unit due to lack of air flow removed fan motor and Capacitor - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-26 | 16407 | TMPE-233749 | noisy motor bearings..SAF#3..y-5786. | NA | noisy motor bearings..SAF#3..y-5786. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-26 | 16431 | TMPE-233725 | Need bike lock cut please - the bike is located at Forrest and Apache. | 2017-04-26 - 11010 - Derek Gittings-cut bike lock. - Derek Gittings | Need bike lock cut please - the bike is located at Forrest and Apache. 2017-04-26 - 11010 - Derek Gittings-cut bike lock. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
2017-04-26 | 16464 | TMPE-233692 | ISTB-4 Room 511 refrigerator not working. When You walk in the room, it's the one straight ahead. Hilairy # is 4807033069. Thanks, | 2017-05-05 - 18240 - Duane Rider-Inspected refrigerator, bad compressor, - Duane Rider | ISTB-4 Room 511 refrigerator not working. When You walk in the room, it's the one straight ahead. Hilairy # is 4807033069. Thanks, 2017-05-05 - 18240 - Duane Rider-Inspected refrigerator, bad compressor, - Duane Rider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-26 | 16496 | TMPE-233660 | ECD - 131: A/H #1 needs the filters changed - the pre-filters and Hi-E filters are extremely dirty causing the A/H to trip off. Before shutting off A/H please contact Jonathan Klane 480-329-8880 to coordinate with him as this is a clean room. | 2017-04-26 - 18170 - Jose Mazon-JOB IN PROGRESS.. CHANGE THE PRE-FILTERS AND DO IT THE HI. BY...4/27/17..AH.1 FOR ROOM D131. - Jose Mazon; 2017-04-26 - 18170 - Austen Jackson-JOB IN PROGRESS.. - Jose Mazon; 2017-04-27 - 18170 - Jose Mazon-HI, CHANGE AT UNIT. #1 AH. JOB DONE..NOTE. THIS UNIT NEED BETTER CARE FILTERS NEED CHANGE MORE OFTHEN..EVERY TWO MONTHS..THE COILS ARE READY DIRTY. - Jose Mazon; 2017-04-27 - 18170 - Austen Jackson-JOB DONE.. - Jose Mazon | ECD - 131: A/H #1 needs the filters changed - the pre-filters and Hi-E filters are extremely dirty causing the A/H to trip off. Before shutting off A/H please contact Jonathan Klane 480-329-8880 to coordinate with him as this is a clean room. 2017-04-26 - 18170 - Jose Mazon-JOB IN PROGRESS.. CHANGE THE PRE-FILTERS AND DO IT THE HI. BY...4/27/17..AH.1 FOR ROOM D131. - Jose Mazon; 2017-04-26 - 18170 - Austen Jackson-JOB IN PROGRESS.. - Jose Mazon; 2017-04-27 - 18170 - Jose Mazon-HI, CHANGE AT UNIT. #1 AH. JOB DONE..NOTE. THIS UNIT NEED BETTER CARE FILTERS NEED CHANGE MORE OFTHEN..EVERY TWO MONTHS..THE COILS ARE READY DIRTY. - Jose Mazon; 2017-04-27 - 18170 - Austen Jackson-JOB DONE.. - Jose Mazon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-27 | 16235 | TMPE-233921 | add the Electric shop: Electrician Eddie Howell is already assisting Jennifer Moyer to replace the conduit to a motor. The motor is seized on the exhaust fan. Motor data: HP 1/4; 120v; 1725 rpm; FR48 | 2017-05-01 - 15000 - Edward Howell-Replaced wire for the motor. - Edward Howell | add the Electric shop: Electrician Eddie Howell is already assisting Jennifer Moyer to replace the conduit to a motor. The motor is seized on the exhaust fan. Motor data: HP 1/4; 120v; 1725 rpm; FR48 2017-05-01 - 15000 - Edward Howell-Replaced wire for the motor. - Edward Howell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-27 | 16240 | TMPE-233916 | ERC SEF-2 HVAC to replace 3 belts on SEF-2 (Y#8730). | 2017-05-04 - 18160 - Zhi Yu-We replaced belt (3) B56. Will need to coordinate with EMS to start SEF#2 do to critical solvent room. - Zhi Yu | ERC SEF-2 HVAC to replace 3 belts on SEF-2 (Y#8730). 2017-05-04 - 18160 - Zhi Yu-We replaced belt (3) B56. Will need to coordinate with EMS to start SEF#2 do to critical solvent room. - Zhi Yu | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-27 | 16261 | TMPE-233895 | Description: Life Sciences A Building, L1-73, Freezer Alarm is going off, Ultra Lo, 056A-ULFRZ-01005,specimens in machine, potential emergency | 2017-04-27 - 18180 - Dispatched Brian Qualls (FF) - Francesca Fernandez; 2017-04-27 - 18180 - Judy Swartz notified of the request (FF) - Francesca Fernandez; 2017-04-28 - 18180 - Robert Ecabert-I had the plumber repair a drain line in room L1-73 and that job is complete. I also ordered a new motorized valve for this fan coil unit that serves this room and I will try to get it installed next week. - Robert Ecabert; 2017-05-04 - 18180 - Robert Ecabert-Chad Hardgrave and I replaced a bad belimo valve, and now the chilled water belimo valve is cycling from the thermostat the way it should be. - Robert Ecabert; 2017-05-04 - 18180 - Chad Hargrave-Chad Hardgrave and I replaced a bad belimo valve, and now the chilled water belimo valve is cycling from the thermostat the way it should be. - Robert Ecabert; 2017-05-17 - 18180 - Robert Ecabert-The SO-Low unit Will not pull down to temperature. Only the high stage compressor will run and the low stage compressor will not run. After Judy talked to SO-Low they told her that the unit has a bad circuit board that is not bringing on the low stage and So-Low said they will come out to Arizona State University and fix the So-Low unit. - Robert Ecabert | Description: Life Sciences A Building, L1-73, Freezer Alarm is going off, Ultra Lo, 056A-ULFRZ-01005,specimens in machine, potential emergency 2017-04-27 - 18180 - Dispatched Brian Qualls (FF) - Francesca Fernandez; 2017-04-27 - 18180 - Judy Swartz notified of the request (FF) - Francesca Fernandez; 2017-04-28 - 18180 - Robert Ecabert-I had the plumber repair a drain line in room L1-73 and that job is complete. I also ordered a new motorized valve for this fan coil unit that serves this room and I will try to get it installed next week. - Robert Ecabert; 2017-05-04 - 18180 - Robert Ecabert-Chad Hardgrave and I replaced a bad belimo valve, and now the chilled water belimo valve is cycling from the thermostat the way it should be. - Robert Ecabert; 2017-05-04 - 18180 - Chad Hargrave-Chad Hardgrave and I replaced a bad belimo valve, and now the chilled water belimo valve is cycling from the thermostat the way it should be. - Robert Ecabert; 2017-05-17 - 18180 - Robert Ecabert-The SO-Low unit Will not pull down to temperature. Only the high stage compressor will run and the low stage compressor will not run. After Judy talked to SO-Low they told her that the unit has a bad circuit board that is not bringing on the low stage and So-Low said they will come out to Arizona State University and fix the So-Low unit. - Robert Ecabert | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 9
2017-04-27 | 16354 | TMPE-233802 | motor sheave is bad.Unit is not able to run without repair.sheave is aluminum..manufacturer is congress..4 1/2 x3/4 shaft. access from SE stairwell to south roof or use extension ladder. | 2017-05-08 - 18160 - Jennifer Moyer-Correct parts request, incorrect part received. Had to make a trip back to Grainger to get correct part. Had part shipped to maintenance stores. - Jennifer Moyer; 2017-05-08 - 18160 - Austen Jackson-Correct parts request, incorrect part received. Had to make a trip back to Grainger to get correct part. Had part shipped to maintenance stores. - Jennifer Moyer; 2017-05-09 - 18160 - Jennifer Moyer-Time taken to locate exhaust fan. This fan is located outside a vented window, down a ladder and onto a secondary roof. - Jennifer Moyer | motor sheave is bad.Unit is not able to run without repair.sheave is aluminum..manufacturer is congress..4 1/2 x3/4 shaft. access from SE stairwell to south roof or use extension ladder. 2017-05-08 - 18160 - Jennifer Moyer-Correct parts request, incorrect part received. Had to make a trip back to Grainger to get correct part. Had part shipped to maintenance stores. - Jennifer Moyer; 2017-05-08 - 18160 - Austen Jackson-Correct parts request, incorrect part received. Had to make a trip back to Grainger to get correct part. Had part shipped to maintenance stores. - Jennifer Moyer; 2017-05-09 - 18160 - Jennifer Moyer-Time taken to locate exhaust fan. This fan is located outside a vented window, down a ladder and onto a secondary roof. - Jennifer Moyer | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-27 | 229341 | POLY-118857 | !! EMERGENCY: A/C unit is not working; resident reports fan blowing very little air. Thermostat is set to seventy degrees, but house is at about 88 degrees. 4NFAFM4 | NA | !! EMERGENCY: A/C unit is not working; resident reports fan blowing very little air. Thermostat is set to seventy degrees, but house is at about 88 degrees. 4NFAFM4 NA | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-28 | 15120 | TMPE-235036 | Send to EMS Robert Zaller: Picked up pneumatic valves from United Refrigeration for pipe repair and replacement. 42C3NC4 | 2017-05-01 - 18010 - Robert Zaller-Picked up pneumatic valves from United Refrigeration for pipe repair and replacement. - Robert Zaller | Send to EMS Robert Zaller: Picked up pneumatic valves from United Refrigeration for pipe repair and replacement. 42C3NC4 2017-05-01 - 18010 - Robert Zaller-Picked up pneumatic valves from United Refrigeration for pipe repair and replacement. - Robert Zaller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-04-28 | 16126 | TMPE-234030 | direct drive bad motor.. this ex fan unit was installed 4-5 years ago.this unit came from graingers.access from room 422. 8 foot ladder needed. | 2017-04-28 - 18160 - Please, cancel work order #'s 234030 &amp; 234032; Mike Bauer on the PM Team was not aware that Res-Life get the first call and or reviews their own work orders first. Thanks, Oner Munoz - Juliana Blusiewicz | direct drive bad motor.. this ex fan unit was installed 4-5 years ago.this unit came from graingers.access from room 422. 8 foot ladder needed. 2017-04-28 - 18160 - Please, cancel work order #'s 234030 &amp; 234032; Mike Bauer on the PM Team was not aware that Res-Life get the first call and or reviews their own work orders first. Thanks, Oner Munoz - Juliana Blusiewicz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-28 | 16138 | TMPE-234018 | At the HAV Market we have an air screen cooler that is dripping water on the floor Will you have someone fix this | 2017-05-13 - 18010 - Robert Dauscher-checked air screen units in Market..... nothing found to be leaking. Checked with Staff who also said nothing had been leaking from either unit - Robert Dauscher | At the HAV Market we have an air screen cooler that is dripping water on the floor Will you have someone fix this 2017-05-13 - 18010 - Robert Dauscher-checked air screen units in Market..... nothing found to be leaking. Checked with Staff who also said nothing had been leaking from either unit - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-28 | 16167 | TMPE-233989 | ADD: EMS shop to meet Robert Ecabert to replace a defective Belimo Actuator on chilled water valve for fan coil unit/ in LSA L173 A. *original message* Description: Life Sciences A Building, L1-73, Freezer Alarm is going off, Ultra Lo, 056A-ULFRZ-01005,specimens in machine, potential emergency | 2017-05-11 - 18180 - no time charged HVAC shop equip. - John Holloway | ADD: EMS shop to meet Robert Ecabert to replace a defective Belimo Actuator on chilled water valve for fan coil unit/ in LSA L173 A. *original message* Description: Life Sciences A Building, L1-73, Freezer Alarm is going off, Ultra Lo, 056A-ULFRZ-01005,specimens in machine, potential emergency 2017-05-11 - 18180 - no time charged HVAC shop equip. - John Holloway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6
2017-04-28 | 16179 | TMPE-233977 | Good mornig we need to increase the air flow to 253L we just installed hepa filters in the room and need room to be positive. Please forward this work order to Guy Boyd and I can help him Thank you 42DIMEB | NA | Good mornig we need to increase the air flow to 253L we just installed hepa filters in the room and need room to be positive. Please forward this work order to Guy Boyd and I can help him Thank you 42DIMEB NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-28 | 16181 | TMPE-233975 | USE 100U1 The only exhaust fan in this room has a blown motor. It is extremely hot as there are large compressors and other equipment. Please address asap, you will need at least a 10 ft ladder. Thank you. | NA | USE 100U1 The only exhaust fan in this room has a blown motor. It is extremely hot as there are large compressors and other equipment. Please address asap, you will need at least a 10 ft ladder. Thank you. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-04-28 | 16184 | TMPE-233972 | Domestic hot recirc pump is missing motor needs repair, ASU PD Rm 130u1 | 2017-05-08 - 23100 - Thomas Gibble-replaced pump motor that was missing.motor was on shelf. - Thomas Gibble; 2017-05-08 - 23100 - Gail Jackson-replaced pump motor that was missing.motor was on shelf. - Thomas Gibble | Domestic hot recirc pump is missing motor needs repair, ASU PD Rm 130u1 2017-05-08 - 23100 - Thomas Gibble-replaced pump motor that was missing.motor was on shelf. - Thomas Gibble; 2017-05-08 - 23100 - Gail Jackson-replaced pump motor that was missing.motor was on shelf. - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-28 | 159710 | RFMT-148621 | The baseboards under the AC vent, and on the right side of the window are peeling away from the wall. 4O3DM39 | 2017-05-01 - 13000 - Scott Berndt-reglued - Scott Berndt | The baseboards under the AC vent, and on the right side of the window are peeling away from the wall. 4O3DM39 2017-05-01 - 13000 - Scott Berndt-reglued - Scott Berndt | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-04-28 | 209524 | RACC-119086 | !! The battery on the A/C is getting low and blinking. 4O0D8J2 | NA | !! The battery on the A/C is getting low and blinking. 4O0D8J2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-28 | 209613 | RACC-118997 | !! !!Event with Dr. Crowe this upcoming Monday & in this room there is an A"C unit on the east wall that causes the entire wall to shake. Can we please fix this asap? Called to on call maintenance- josh Submitted by 4N80G0G | NA | !! !!Event with Dr. Crowe this upcoming Monday & in this room there is an A"C unit on the east wall that causes the entire wall to shake. Can we please fix this asap? Called to on call maintenance- josh Submitted by 4N80G0G NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-04-28 | 229312 | POLY-118886 | FULL SERVICE ON AIR COMPRESSOR AND FILTER SYSTEM 4O216EO | NA | FULL SERVICE ON AIR COMPRESSOR AND FILTER SYSTEM 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-04-30 | 337 | WEST-110912 | ADA Door Weekly Inspection | 2017-05-02 - xPM-WC-ADADOOR - Tim Jowers-the doors are working correctly,the compressor on the east side is going to need replacement soon.pulled down the unit from above the west side desk, but it is a tank less unit. - Tim Jowers | ADA Door Weekly Inspection 2017-05-02 - xPM-WC-ADADOOR - Tim Jowers-the doors are working correctly,the compressor on the east side is going to need replacement soon.pulled down the unit from above the west side desk, but it is a tank less unit. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 350 | WEST-110899 | HVAC-GENERAL-MA South Filters | 2017-05-04 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | HVAC-GENERAL-MA South Filters 2017-05-04 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-01 | 351 | WEST-110898 | HVAC-GENERAL-MA North Filters | 2017-05-04 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | HVAC-GENERAL-MA North Filters 2017-05-04 - 18010 - Chad T Ball-Inspected condition of filters. Replacement not necessary at this time. - Chad T Ball | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-01 | 393 | WEST-110856 | Air Compressor-SAC-001 | 2017-05-05 - 18030 - Joseph McCormick-Inspected belts, air filter, belt guard and compressor sump oil. Tightened all electrical lugs. Readings as follows: A-B A-C B-C 485 485 485 280 280 275 7.7 8.2 7.9 Drained condensate from tank. - Joseph McCormick | Air Compressor-SAC-001 2017-05-05 - 18030 - Joseph McCormick-Inspected belts, air filter, belt guard and compressor sump oil. Tightened all electrical lugs. Readings as follows: A-B A-C B-C 485 485 485 280 280 275 7.7 8.2 7.9 Drained condensate from tank. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-01 | 394 | WEST-110855 | Air Compressor-CAC-002 | 2017-05-05 - 18030 - Joseph McCormick-Inspected belt, air filter and belt guard. Took electrical readings as follows: A-B A-C B-C 205 205 205 118 118 117 13.5 13.4 13.3 All terminal lugs tightened. - Joseph McCormick | Air Compressor-CAC-002 2017-05-05 - 18030 - Joseph McCormick-Inspected belt, air filter and belt guard. Took electrical readings as follows: A-B A-C B-C 205 205 205 118 118 117 13.5 13.4 13.3 All terminal lugs tightened. - Joseph McCormick | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-01 | 395 | WEST-110854 | Air Compressor-CAC-001 | NA | Air Compressor-CAC-001 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 14904 | TMPE-235252 | Music - L2: Send to HVAC shop. There is a plastic filter or separator that is leaking air. But the overall problem is that the upper floors are not getting full control air pressure. they are running at 12 to 15psi. Please check it out. Thanks. 42C3NC4 | 2017-05-03 - 18010 - Michael Kelley-Air dryer with Air Compressor 5898 Had moisture dripping from the separator. Tightened nut on separator. Could not find air leek on compressor. Did find leek in room E193 behind wall. see WO TMPE 235248 - Michael Kelley | Music - L2: Send to HVAC shop. There is a plastic filter or separator that is leaking air. But the overall problem is that the upper floors are not getting full control air pressure. they are running at 12 to 15psi. Please check it out. Thanks. 42C3NC4 2017-05-03 - 18010 - Michael Kelley-Air dryer with Air Compressor 5898 Had moisture dripping from the separator. Tightened nut on separator. Could not find air leek on compressor. Did find leek in room E193 behind wall. see WO TMPE 235248 - Michael Kelley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-01 | 14909 | TMPE-235247 | LSE - 649 !! The alarm is sounding on the LSE 649 environmental growth chamber. Please initiate a work order for HVAC to inspect and service as quickly as possible. Thank you. 42BLHKH | 2017-05-15 - 18140 - Robert Dauscher-condenser water flow problems....... reset manual limit switch - Robert Dauscher | LSE - 649 !! The alarm is sounding on the LSE 649 environmental growth chamber. Please initiate a work order for HVAC to inspect and service as quickly as possible. Thank you. 42BLHKH 2017-05-15 - 18140 - Robert Dauscher-condenser water flow problems....... reset manual limit switch - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 15005 | TMPE-235151 | MU 87 ADD: electric shop Their assistance is needed to repair a burnt motor starter and wiring for this chilled water pump. HVAC Tech is Derek Gittings *original message** !! The motor/starter for chilled water pump #2 went off on electrical faults. Wires burned inside the starter, and all thre. . . | 2017-05-03 - 15000 - Gary Conover-Troubleshoot control problem - Gary Conover; 2017-05-03 - 15000 - Semeon Haile-Troubleshoot control problem - Gary Conover; 2017-05-09 - 15000 - Gary Conover-Parts on order for a new starter - Gary Conover; 2017-05-09 - 15000 - Semeon Haile-Need to order new starter - Gary Conover; 2017-05-10 - 15000 - Gary Conover-Job in progress - Gary Conover | MU 87 ADD: electric shop Their assistance is needed to repair a burnt motor starter and wiring for this chilled water pump. HVAC Tech is Derek Gittings *original message** !! The motor/starter for chilled water pump #2 went off on electrical faults. Wires burned inside the starter, and all thre. . . 2017-05-03 - 15000 - Gary Conover-Troubleshoot control problem - Gary Conover; 2017-05-03 - 15000 - Semeon Haile-Troubleshoot control problem - Gary Conover; 2017-05-09 - 15000 - Gary Conover-Parts on order for a new starter - Gary Conover; 2017-05-09 - 15000 - Semeon Haile-Need to order new starter - Gary Conover; 2017-05-10 - 15000 - Gary Conover-Job in progress - Gary Conover | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-01 | 15018 | TMPE-235138 | SCOB 310C Please remove the cooling unit from the office 310C. It should no longer be needed in this room. 42BH802 | 2017-05-08 - 18010 - Derek Gittings-removed ac unit. - Derek Gittings | SCOB 310C Please remove the cooling unit from the office 310C. It should no longer be needed in this room. 42BH802 2017-05-08 - 18010 - Derek Gittings-removed ac unit. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-01 | 15042 | TMPE-235114 | BT to HVAC Noise is coming from an air handler Hayden Library: There is a loud, continuous noise that seems to be coming from the Hayden Library north side moat-level mechanical room. This is not a typical or normal noise. Please investigate thanks | 2017-05-01 - 18010 - HVAC- please see Carlos so he can point you in the right direction. - Taylor Nava; 2017-05-17 - 18010 - Derek Gittings-swith motor. - Derek Gittings | BT to HVAC Noise is coming from an air handler Hayden Library: There is a loud, continuous noise that seems to be coming from the Hayden Library north side moat-level mechanical room. This is not a typical or normal noise. Please investigate thanks 2017-05-01 - 18010 - HVAC- please see Carlos so he can point you in the right direction. - Taylor Nava; 2017-05-17 - 18010 - Derek Gittings-swith motor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 15063 | TMPE-235093 | PSF F766 Air Handler #00779 is running extremely loud, possibly cracked belts? Please service asap, thank you. | 2017-05-11 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 18050 - need to schedule shutdown - Melanie Lamm; 2017-05-15 - 18050 - Jose Lopez-work in progress waiting for parts - Jose Lopez | PSF F766 Air Handler #00779 is running extremely loud, possibly cracked belts? Please service asap, thank you. 2017-05-11 - 18050 - Jose Lopez-work in progress - Jose Lopez; 2017-05-12 - 18050 - need to schedule shutdown - Melanie Lamm; 2017-05-15 - 18050 - Jose Lopez-work in progress waiting for parts - Jose Lopez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-01 | 15083 | TMPE-235073 | MU 87 !! The motor/starter for chilled water pump #2 went off on electrical faults. Wires burned inside the starter, and all three fuses in the disconnect switch opened. Please check and repair damage as needed. 42AI0GO | 2017-05-01 - 23100 - Derek Gittings-replacing motor. - Derek Gittings; 2017-05-11 - 23100 - Carl Karr-Retro fit motor control switch. - Carl Karr | MU 87 !! The motor/starter for chilled water pump #2 went off on electrical faults. Wires burned inside the starter, and all three fuses in the disconnect switch opened. Please check and repair damage as needed. 42AI0GO 2017-05-01 - 23100 - Derek Gittings-replacing motor. - Derek Gittings; 2017-05-11 - 23100 - Carl Karr-Retro fit motor control switch. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-05-01 | 15090 | TMPE-235066 | HVAC Check operation of Chiller. It has needed to be reset several times since last week and possibly low on refrigerant. | 2017-05-01 - 18080 - Gail Jackson-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Chad Hargrave-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Zhi Yu-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Gail Jackson-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-02 - 18080 - Gail Jackson-Check chiller operation, no reset needed, #2 chiller was running; no alarms in either one. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Check chiller operation, no reset needed, #2 chiller was running; no alarms in either one. - Gail Jackson; 2017-05-11 - 18080 - Gail Jackson-Added 11 lbs of R22; still did not clear sight glass, leak tested; found none, leak could be in barrel. EPA regulation leak of greater than 15% and charge of 50 or more lbs to be shut down and tagged out if not repaired in 30 days. Unit holds 90 lbs. - Gail Jackson; 2017-05-11 - 18080 - Thomas Gibble-Added 11 lbs of R22; still did not clear sight glass, leak tested; found none, leak could be in barrel. EPA regulation leak of greater than 15% and charge of 50 or more lbs to be shut down and tagged out if not repaired in 30 days. Unit holds 90 lbs. - Gail Jackson | HVAC Check operation of Chiller. It has needed to be reset several times since last week and possibly low on refrigerant. 2017-05-01 - 18080 - Gail Jackson-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Chad Hargrave-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Zhi Yu-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-01 - 18080 - Gail Jackson-found UNIT OUT ON ALARM, reset; check pressures and temps, found cooling tower H20 tempset at 55F. Adjusted temps at chiller to enter 77 and leave 84 to cooling tower. - Gail Jackson; 2017-05-02 - 18080 - Gail Jackson-Check chiller operation, no reset needed, #2 chiller was running; no alarms in either one. - Gail Jackson; 2017-05-02 - 18080 - Thomas Gibble-Check chiller operation, no reset needed, #2 chiller was running; no alarms in either one. - Gail Jackson; 2017-05-11 - 18080 - Gail Jackson-Added 11 lbs of R22; still did not clear sight glass, leak tested; found none, leak could be in barrel. EPA regulation leak of greater than 15% and charge of 50 or more lbs to be shut down and tagged out if not repaired in 30 days. Unit holds 90 lbs. - Gail Jackson; 2017-05-11 - 18080 - Thomas Gibble-Added 11 lbs of R22; still did not clear sight glass, leak tested; found none, leak could be in barrel. EPA regulation leak of greater than 15% and charge of 50 or more lbs to be shut down and tagged out if not repaired in 30 days. Unit holds 90 lbs. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-01 | 15137 | TMPE-235019 | ECD - D101U1: The air leak on the compressor is back and is worse than before. | 2017-05-01 - 18030 - Called to Brian Q. - Jeri Zappanti; 2017-05-10 - 18030 - Cleaned up pressure control contacts and hinge mechanism. Adjusted switch up and down. Working good now. - Brian Qualls | ECD - D101U1: The air leak on the compressor is back and is worse than before. 2017-05-01 - 18030 - Called to Brian Q. - Jeri Zappanti; 2017-05-10 - 18030 - Cleaned up pressure control contacts and hinge mechanism. Adjusted switch up and down. Working good now. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-01 | 15143 | TMPE-235013 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 15144 | TMPE-235012 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 15347 | TMPE-234809 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 15348 | TMPE-234808 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 154612 | RFMT-153719 | !! Res Life Insurance Claim - Contractor needed to fix the return air duct as well as the drop ceiling in the loading dock. 4NEI9DN | NA | !! Res Life Insurance Claim - Contractor needed to fix the return air duct as well as the drop ceiling in the loading dock. 4NEI9DN NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-05-01 | 154614 | RFMT-153717 | !! The air conditioning vent from the ceiling is leaking 4N9BA4O | 2017-05-01 - 18010 - Joe Swan-occupant cleaned up water from up stairs toilet over flow. That was the A/C vent leak - Joe Swan | !! The air conditioning vent from the ceiling is leaking 4N9BA4O 2017-05-01 - 18010 - Joe Swan-occupant cleaned up water from up stairs toilet over flow. That was the A/C vent leak - Joe Swan | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 154640 | RFMT-153691 | !! Our air conditioner is broken 4NE2A3M | 2017-05-01 - 18010 - David Cates-replaced fuses and tstat - David Cates | !! Our air conditioner is broken 4NE2A3M 2017-05-01 - 18010 - David Cates-replaced fuses and tstat - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-05-01 | 160007 | RFMT-148324 | GMM's Administration Time Weekly | 2017-05-01 - 50035 - Thomas Zambrano-install life saving device back to wall. drive time,email,walk grounds,move furniture to room 124 and 420, - Thomas Zambrano; 2017-05-02 - 50035 - Thomas Zambrano-tma input,drive time,walk grounds,check timer on volleyball court,dump trash,check laundry rooms,change filter on elevator room ac unit. - Thomas Zambrano; 2017-05-03 - 50035 - Thomas Zambrano-tma input, check email,throw trash,seperate and inventory parts for turn,check laundry,check lounges, - Thomas Zambrano; 2017-05-04 - 50035 - Thomas Zambrano-tma input,dump trash,walk grounds,check email.drive time. - Thomas Zambrano | GMM's Administration Time Weekly 2017-05-01 - 50035 - Thomas Zambrano-install life saving device back to wall. drive time,email,walk grounds,move furniture to room 124 and 420, - Thomas Zambrano; 2017-05-02 - 50035 - Thomas Zambrano-tma input,drive time,walk grounds,check timer on volleyball court,dump trash,check laundry rooms,change filter on elevator room ac unit. - Thomas Zambrano; 2017-05-03 - 50035 - Thomas Zambrano-tma input, check email,throw trash,seperate and inventory parts for turn,check laundry,check lounges, - Thomas Zambrano; 2017-05-04 - 50035 - Thomas Zambrano-tma input,dump trash,walk grounds,check email.drive time. - Thomas Zambrano | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 229261 | POLY-118937 | CALLED STEVE !! AC does not work Contact Name: Cahit OZTURK Contact Phone Number: 4804349242 Contact Email: Cahit.ozturk@asu.edu 4N0F461 | 2017-05-15 - 18010 - Esli Arvizo-5/2 FOUND UNITS WITH BAD T'STATS - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/2 FOUND UNITS WITH BAD T'STATS - Steve Clark; 2017-05-15 - 18010 - Esli Arvizo-5/5 REPLACE T'SATS AND NOITICED 1 UNIT NOT COOLING - FOUND BAD COMPRESSOR - WILL NEED TO REPLACE - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/5 REPLACE T'SATS AND NOITICED 1 UNIT NOT COOLING - FOUND BAD COMPRESSOR - WILL NEED TO REPLACE - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/10 - REPLACED COMPRESSOR - Steve Clark; 2017-05-15 - 18010 - Darusman Amin-5/10 - REPLACED COMPRESSOR - Steve Clark | CALLED STEVE !! AC does not work Contact Name: Cahit OZTURK Contact Phone Number: 4804349242 Contact Email: Cahit.ozturk@asu.edu 4N0F461 2017-05-15 - 18010 - Esli Arvizo-5/2 FOUND UNITS WITH BAD T'STATS - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/2 FOUND UNITS WITH BAD T'STATS - Steve Clark; 2017-05-15 - 18010 - Esli Arvizo-5/5 REPLACE T'SATS AND NOITICED 1 UNIT NOT COOLING - FOUND BAD COMPRESSOR - WILL NEED TO REPLACE - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/5 REPLACE T'SATS AND NOITICED 1 UNIT NOT COOLING - FOUND BAD COMPRESSOR - WILL NEED TO REPLACE - Steve Clark; 2017-05-15 - 18010 - Suresh Nair-5/10 - REPLACED COMPRESSOR - Steve Clark; 2017-05-15 - 18010 - Darusman Amin-5/10 - REPLACED COMPRESSOR - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 229277 | POLY-118921 | replace pump/motor coupling on unit #SCHWP-3 4O216EO | 2017-05-03 - 18230 - Allan Blair-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Darusman Amin-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Darusman Amin-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Allan Blair-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark | replace pump/motor coupling on unit #SCHWP-3 4O216EO 2017-05-03 - 18230 - Allan Blair-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Darusman Amin-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Darusman Amin-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark; 2017-05-03 - 18230 - Allan Blair-REINSTALLED PUMP COUPLING, SHIMMING MOTOR TO LEVEL SHAFT - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 229281 | POLY-118917 | Frank, Please repair the Backhoe tractor, it will not start. Thanks 4NF4KMJ | 2017-05-02 - 26000 - Frank Calderon Jr-5/1 - Frank charged the battery on the backhoe. - Gayle Swenson | Frank, Please repair the Backhoe tractor, it will not start. Thanks 4NF4KMJ 2017-05-02 - 26000 - Frank Calderon Jr-5/1 - Frank charged the battery on the backhoe. - Gayle Swenson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 249340 | DTPC-119198 | Air Compressor | 2017-05-15 - 18030 - James Hermann-Performed a full pm inspection of the air compressor. - Keith Griffin | Air Compressor 2017-05-15 - 18030 - James Hermann-Performed a full pm inspection of the air compressor. - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-01 | 301 | WEST-110948 | Repairs needed to van. Was leaking fuel. National Automotive replaced fuel pump gasket and an engine motor mount. | NA | Repairs needed to van. Was leaking fuel. National Automotive replaced fuel pump gasket and an engine motor mount. NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-02 | 14759 | TMPE-235397 | It is reported regarding Chamber #7 in LSE S-29, "I can't get the growth chamber temperature to go below 25C but I need it to go down to 10 or 15C. I turned the lights off and set the temperature. The lights went off fine but the temperature will not get as low as I want it to." Please inspect and. . . | 2017-05-10 - 18010 - 05/09 Robert Ecabert-After trouble shooting the unit I discovered the growth chamber has a defective metering device. I went to Arizona refrigeration supply and bought new parts, and I will install the new metering device on this growth chamber tomorrow. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-10 - 18010 - 05/10 Robert Ecabert-After trouble shooting the unit I discovered the growth chamber has a defective metering device. I went to Arizona refrigeration supply and bought new parts, and I will install the new metering device on this growth chamber tomorrow. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-12 - 18010 - 05/11 Robert Ecabert-Chad and I recovered 3LBS 8 ounces of R-22 refrigerant into recovery cylinder tank A146230. We replaced the defective TXV with a new one and we also replaced the liquid line drier. We leak checked our welds with nitrogen and soap bubbles and there were no leaks, so we put the growth chamber on the vacuum pump and pulled the unit down to 300 microns and it held the vacuum at 300 microns. We then added 3LBS 8 ounces of new R-22 refrigerant from cylinder drum JS160216-22 and the unit pulled down to the set point of 10.0 degrees celcius and the unit is cycling the way it is supposed to. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-12 - 18010 - Chad Hargrave-We went back to the job site and picked up our tools and put the panels back on the unit and insulated the suction line and the job is complete. - Robert Ecabert; 2017-05-12 - 18010 - Robert Ecabert-We went back to the job site and picked up our tools and put the panels back on the unit and insulated the suction line and the job is complete. - Robert Ecabert | It is reported regarding Chamber #7 in LSE S-29, "I can't get the growth chamber temperature to go below 25C but I need it to go down to 10 or 15C. I turned the lights off and set the temperature. The lights went off fine but the temperature will not get as low as I want it to." Please inspect and. . . 2017-05-10 - 18010 - 05/09 Robert Ecabert-After trouble shooting the unit I discovered the growth chamber has a defective metering device. I went to Arizona refrigeration supply and bought new parts, and I will install the new metering device on this growth chamber tomorrow. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-10 - 18010 - 05/10 Robert Ecabert-After trouble shooting the unit I discovered the growth chamber has a defective metering device. I went to Arizona refrigeration supply and bought new parts, and I will install the new metering device on this growth chamber tomorrow. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-12 - 18010 - 05/11 Robert Ecabert-Chad and I recovered 3LBS 8 ounces of R-22 refrigerant into recovery cylinder tank A146230. We replaced the defective TXV with a new one and we also replaced the liquid line drier. We leak checked our welds with nitrogen and soap bubbles and there were no leaks, so we put the growth chamber on the vacuum pump and pulled the unit down to 300 microns and it held the vacuum at 300 microns. We then added 3LBS 8 ounces of new R-22 refrigerant from cylinder drum JS160216-22 and the unit pulled down to the set point of 10.0 degrees celcius and the unit is cycling the way it is supposed to. - Robert Ecabert [Modified: 2017-05-12 Robert Ecabert]; 2017-05-12 - 18010 - Chad Hargrave-We went back to the job site and picked up our tools and put the panels back on the unit and insulated the suction line and the job is complete. - Robert Ecabert; 2017-05-12 - 18010 - Robert Ecabert-We went back to the job site and picked up our tools and put the panels back on the unit and insulated the suction line and the job is complete. - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-02 | 14761 | TMPE-235395 | !! Please have the HVAC Shop perform PM on the units at the Gymnastics training Facility on a monthly basis starting with May. We will be having camps throughout the summer, so there will be more chalk build up than normal. Please coordinate times with Eric. PO is YG202004934. Thank you. Conta. . . | 2017-05-04 - 18010 - Zhi Yu-Coordinate with Eric and schedule service tomorrow. - Zhi Yu; 2017-05-09 - 18010 - Zhi Yu-We PM all 3 unit. We founded problem to hp 1 ,need contactor, and cap. HP2 needs ODM . - Zhi Yu; 2017-05-11 - 18010 - Gail Jackson-Replaced filters, cleaned registrars, replaced condenser fan motor and run cap, trip to ARS Tempe for parts. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Replaced filters, cleaned registrars, replaced condenser fan motor and run cap, trip to ARS Tempe for parts. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Replaced contractor and run cap in unit on N. E. and filters and cleaned grill. - Gail Jackson | !! Please have the HVAC Shop perform PM on the units at the Gymnastics training Facility on a monthly basis starting with May. We will be having camps throughout the summer, so there will be more chalk build up than normal. Please coordinate times with Eric. PO is YG202004934. Thank you. Conta. . . 2017-05-04 - 18010 - Zhi Yu-Coordinate with Eric and schedule service tomorrow. - Zhi Yu; 2017-05-09 - 18010 - Zhi Yu-We PM all 3 unit. We founded problem to hp 1 ,need contactor, and cap. HP2 needs ODM . - Zhi Yu; 2017-05-11 - 18010 - Gail Jackson-Replaced filters, cleaned registrars, replaced condenser fan motor and run cap, trip to ARS Tempe for parts. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Replaced filters, cleaned registrars, replaced condenser fan motor and run cap, trip to ARS Tempe for parts. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Replaced contractor and run cap in unit on N. E. and filters and cleaned grill. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-05-02 | 14762 | TMPE-235394 | ERC South cooling tower Y#08854. Motor or fan bearings are very loud. Tower is currently out of service. Tower is for ERC but is physical located on Engineering Center roof. Ken Kamptner is HVAC contact. | 2017-05-04 - 18010 - Zhi Yu-We diagnose the Motor bearing is bad. - Zhi Yu; 2017-05-11 - 18010 - Gail Jackson-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Roque Garcia-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Michael Kelley-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Gail Jackson-Clean up, haul all equipment back to shop. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Clean up, haul all equipment back to shop. - Gail Jackson | ERC South cooling tower Y#08854. Motor or fan bearings are very loud. Tower is currently out of service. Tower is for ERC but is physical located on Engineering Center roof. Ken Kamptner is HVAC contact. 2017-05-04 - 18010 - Zhi Yu-We diagnose the Motor bearing is bad. - Zhi Yu; 2017-05-11 - 18010 - Gail Jackson-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Roque Garcia-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Michael Kelley-Removed old and installed new blower motor. replaced 120B belts and new motor pulley. Replaced 3 30/600v fuses in ERC basement. Made adjustments and wired motor. Test run EMS put in auto too much cooling in hand control. Motor in N tower very load needs replaced. - Gail Jackson; 2017-05-11 - 18010 - Gail Jackson-Clean up, haul all equipment back to shop. - Gail Jackson; 2017-05-11 - 18010 - Zhi Yu-Clean up, haul all equipment back to shop. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-05-02 | 14810 | TMPE-235346 | USB - 2131 (HP53): The room is very warm Call transferred to HVAC, Cooling & Heating set points lowered, once changes were made, the reversing vlv went into cooling, and both compressors came on, fan is still showing off after 15 minutes. HVAC to check fan on HP53 for RM 2131. | 2017-05-16 - 18290 - Thomas Gibble-room was at temp. Checked unit and everything OK - Thomas Gibble; 2017-05-16 - 18290 - Gail Jackson-room was at temp. Checked unit and everything OK - Thomas Gibble | USB - 2131 (HP53): The room is very warm Call transferred to HVAC, Cooling & Heating set points lowered, once changes were made, the reversing vlv went into cooling, and both compressors came on, fan is still showing off after 15 minutes. HVAC to check fan on HP53 for RM 2131. 2017-05-16 - 18290 - Thomas Gibble-room was at temp. Checked unit and everything OK - Thomas Gibble; 2017-05-16 - 18290 - Gail Jackson-room was at temp. Checked unit and everything OK - Thomas Gibble | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-02 | 14812 | TMPE-235344 | !! Please turn the fountain off, on Tuesday May 9th at 8AM We will be having an event in the atrium, and the fountain makes it too difficult to hear speakers Thank you! 4NDCIJF | 2017-05-05 - 23080 - Michael Kelley-contacted Sara. Informed he that the fountain is down due to leek. Stopped and checked out fountain with Michael Longton. Found leak. Shut down pump. - Michael Kelley | !! Please turn the fountain off, on Tuesday May 9th at 8AM We will be having an event in the atrium, and the fountain makes it too difficult to hear speakers Thank you! 4NDCIJF 2017-05-05 - 23080 - Michael Kelley-contacted Sara. Informed he that the fountain is down due to leek. Stopped and checked out fountain with Michael Longton. Found leak. Shut down pump. - Michael Kelley | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-02 | 14816 | TMPE-235340 | !! 5/2/17 AC unit is not running properly. Thermostat reads 80 degrees. Bill to TL502001138 42A042B | NA | !! 5/2/17 AC unit is not running properly. Thermostat reads 80 degrees. Bill to TL502001138 42A042B NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-02 | 14836 | TMPE-235320 | Central Plant - remove and replace air filters in generator room. | 2017-05-02 - 30010 - Louis Ballejos-Completed - Lisa Anderson | Central Plant - remove and replace air filters in generator room. 2017-05-02 - 30010 - Louis Ballejos-Completed - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-02 | 154531 | RFMT-153800 | The vent connecting the hall to the lounge is severely caved in. 4NJO5E3 | 2017-05-05 - 10010 - Mike Guckian-CAR replaced 1- 18x32 vent grill. - Russell Peterson | The vent connecting the hall to the lounge is severely caved in. 4NJO5E3 2017-05-05 - 10010 - Mike Guckian-CAR replaced 1- 18x32 vent grill. - Russell Peterson | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-02 | 154537 | RFMT-153794 | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 | 2017-05-04 - 18010 - David Cates-Blowing out at 78, lineset not cold. Called for Simon and Thor to check it out, and they replaced the thermostat. - David Cates; 2017-05-04 - 18010 - Thor was copied on work order. - Gregory Stetka | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 2017-05-04 - 18010 - David Cates-Blowing out at 78, lineset not cold. Called for Simon and Thor to check it out, and they replaced the thermostat. - David Cates; 2017-05-04 - 18010 - Thor was copied on work order. - Gregory Stetka | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-05-02 | 154576 | RFMT-153755 | !! Our air conditioner is broken 4NE2A3M | 2017-05-02 - 18010 - Thor Millsaps-Replaced thermostat. Condensers were mislabeled so I also re-labeled condensers with correct room numbers. Part accounted for on David's WO. System up and running. - Thor Millsaps | !! Our air conditioner is broken 4NE2A3M 2017-05-02 - 18010 - Thor Millsaps-Replaced thermostat. Condensers were mislabeled so I also re-labeled condensers with correct room numbers. Part accounted for on David's WO. System up and running. - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-05-02 | 154579 | RFMT-153752 | !! GMM/Chet - Please replace the thermostat. 4NEI9DN | 2017-05-02 - 18010 - Chester Duncan-Replaced thermostat Tested unit Built replacement thermostat with harness - Chester Duncan | !! GMM/Chet - Please replace the thermostat. 4NEI9DN 2017-05-02 - 18010 - Chester Duncan-Replaced thermostat Tested unit Built replacement thermostat with harness - Chester Duncan | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-02 | 229257 | POLY-118941 | AC unit is blowing air but the air is not cool (resident says it gets down to 78 degrees but not the desired 72 degrees) The air filter needs to be replaced. Contact Name: Hannah smolinski Contact Phone Number: 3307306819 Contact Email: 4NFGA5O | NA | AC unit is blowing air but the air is not cool (resident says it gets down to 78 degrees but not the desired 72 degrees) The air filter needs to be replaced. Contact Name: Hannah smolinski Contact Phone Number: 3307306819 Contact Email: 4NFGA5O NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 14541 | TMPE-235615 | Send to HVAC shop. The reheat coil for Rm. L2-37A4 in the mezzanine area is not producing enough heat. Please flush. Thanks. 42C3NC4 | 2017-05-10 - 18090 - Jennifer Moyer-Called Duane, found out that this room has limited access and I probably do not have keys. He said a valve probably needs replaced. I will meet him to take care of this. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer- Called Duane.Issue resolved. - Jennifer Moyer [Modified: 2017-05-11 Jennifer Moyer] | Send to HVAC shop. The reheat coil for Rm. L2-37A4 in the mezzanine area is not producing enough heat. Please flush. Thanks. 42C3NC4 2017-05-10 - 18090 - Jennifer Moyer-Called Duane, found out that this room has limited access and I probably do not have keys. He said a valve probably needs replaced. I will meet him to take care of this. - Jennifer Moyer; 2017-05-11 - 18090 - Jennifer Moyer- Called Duane.Issue resolved. - Jennifer Moyer [Modified: 2017-05-11 Jennifer Moyer] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-05-03 | 14580 | TMPE-235576 | GGMA get information on providing water lines to seven evaporative coolers on the Promenade. He would like to have this done by 5/15/17 because we will have a show in the building and need to use the coolers at that time. EST-155868 | NA | GGMA get information on providing water lines to seven evaporative coolers on the Promenade. He would like to have this done by 5/15/17 because we will have a show in the building and need to use the coolers at that time. EST-155868 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-03 | 14589 | TMPE-235567 | Please turn on the swamp coolers for our warehouse. they currently are shut off because of winter Contact Name: Contact Phone Number: 602-639-1509 Contact Email: 42C7MH1 | 2017-05-16 - 18100 - Gail Jackson-Flush out coolers, check operation, found pump burned out on center cooler for up stairs. Replaced pump. - Gail Jackson; 2017-05-16 - 18100 - Thomas Gibble-Flush out coolers, check operation, found pump burned out on center cooler for up stairs. Replaced pump. - Gail Jackson | Please turn on the swamp coolers for our warehouse. they currently are shut off because of winter Contact Name: Contact Phone Number: 602-639-1509 Contact Email: 42C7MH1 2017-05-16 - 18100 - Gail Jackson-Flush out coolers, check operation, found pump burned out on center cooler for up stairs. Replaced pump. - Gail Jackson; 2017-05-16 - 18100 - Thomas Gibble-Flush out coolers, check operation, found pump burned out on center cooler for up stairs. Replaced pump. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-03 | 14610 | TMPE-235546 | MU - Pei Wei: Please have someone check out the walk in cooler next to PEI WEI located in the MU on the first floor It is running warm | 2017-05-12 - 18180 - Gail Jackson-Found low charge R22, found empty stop leak tube on floor, added 1# R22. Leak in low side core, changed, very hard to remove; full of stop leak, this unit has leaked for years, needs replaced. Dangerous place to work, not safe. - Gail Jackson; 2017-05-12 - 18180 - Thomas Gibble-Found low charge R22, found empty stop leak tube on floor, added 1# R22. Leak in low side core, changed, very hard to remove; full of stop leak, this unit has leaked for years, needs replaced. Dangerous place to work, not safe. - Gail Jackson | MU - Pei Wei: Please have someone check out the walk in cooler next to PEI WEI located in the MU on the first floor It is running warm 2017-05-12 - 18180 - Gail Jackson-Found low charge R22, found empty stop leak tube on floor, added 1# R22. Leak in low side core, changed, very hard to remove; full of stop leak, this unit has leaked for years, needs replaced. Dangerous place to work, not safe. - Gail Jackson; 2017-05-12 - 18180 - Thomas Gibble-Found low charge R22, found empty stop leak tube on floor, added 1# R22. Leak in low side core, changed, very hard to remove; full of stop leak, this unit has leaked for years, needs replaced. Dangerous place to work, not safe. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-03 | 14635 | TMPE-235521 | !! The AC unit that services the Home Clubhouse at Phx Muni has lines that have frozen. With the temperature in 100's and a series starting Friday, we need to have this repaired ASAP. PO is YG202004982. Thank you.it Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: Jam. . . | 2017-05-19 - 18010 - Mitchell Andrews-unit was frozen upon arrival defrosted unit and check all componets of this unit found no leaks...replaced 6 air filters for this unit and the fresh air filters also, set the thermostat to 76 degrees - Mitchell Andrews | !! The AC unit that services the Home Clubhouse at Phx Muni has lines that have frozen. With the temperature in 100's and a series starting Friday, we need to have this repaired ASAP. PO is YG202004982. Thank you.it Contact Name: James Vujs Contact Phone Number: 623-570-3014 Contact Email: Jam. . . 2017-05-19 - 18010 - Mitchell Andrews-unit was frozen upon arrival defrosted unit and check all componets of this unit found no leaks...replaced 6 air filters for this unit and the fresh air filters also, set the thermostat to 76 degrees - Mitchell Andrews | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-03 | 14641 | TMPE-235515 | UCENT C - 303: My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. The AC system in my office has been fixed; however, the temperature is now dramatically cold \\u2013 almost uncomfortably so. Is there a way to raise the thermostat. . . | 2017-05-04 - 18300 - Cheryl St. John-05.04.17 Replaced thermostat/base plate with newer Novar thermostat/base plate. Found duplicate address and had to reprogram unit so it would communicate and update graphics in the Novar system. Also, found two other thermostats that were bad (1 bad internal voltage, 1 bad sensor). Requested a quote from the vendor for 3 ea additional temperature sensors. Sent email to Karen letting her know the thermostat was changed and to let me know if she any issues with the temperature in her space, I also noted that the HP number had changed from HP 3-19 to HP 3-303. - Cheryl St. John | UCENT C - 303: My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. The AC system in my office has been fixed; however, the temperature is now dramatically cold \\u2013 almost uncomfortably so. Is there a way to raise the thermostat. . . 2017-05-04 - 18300 - Cheryl St. John-05.04.17 Replaced thermostat/base plate with newer Novar thermostat/base plate. Found duplicate address and had to reprogram unit so it would communicate and update graphics in the Novar system. Also, found two other thermostats that were bad (1 bad internal voltage, 1 bad sensor). Requested a quote from the vendor for 3 ea additional temperature sensors. Sent email to Karen letting her know the thermostat was changed and to let me know if she any issues with the temperature in her space, I also noted that the HP number had changed from HP 3-19 to HP 3-303. - Cheryl St. John | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 14737 | TMPE-235419 | BAC Starbucks: Please create a work order to sand and paint 6 refrigerator shelves that are rusty These are in the 2 door cooler at WPC Starbucks in the back room Charge to ARAMARK Gn7 | NA | BAC Starbucks: Please create a work order to sand and paint 6 refrigerator shelves that are rusty These are in the 2 door cooler at WPC Starbucks in the back room Charge to ARAMARK Gn7 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 154470 | RFMT-153861 | !! Air conditioner is not working... stuck on 80+ degrees for the past 24 hours. 4NL2M6K | 2017-05-04 - 18010 - David Cates-Resident said that the AC was working fine now - David Cates | !! Air conditioner is not working... stuck on 80+ degrees for the past 24 hours. 4NL2M6K 2017-05-04 - 18010 - David Cates-Resident said that the AC was working fine now - David Cates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 154484 | RFMT-153847 | !! my air conditioning is broken, it is extremely hot in my room 4NJ96H3 | 2017-05-04 - 18010 - David Cates-Unit up on roof not working. Thor to replace condensing fan motor - David Cates; 2017-05-04 - 18010 - Thor was copied on work order - Gregory Stetka | !! my air conditioning is broken, it is extremely hot in my room 4NJ96H3 2017-05-04 - 18010 - David Cates-Unit up on roof not working. Thor to replace condensing fan motor - David Cates; 2017-05-04 - 18010 - Thor was copied on work order - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-05-03 | 154510 | RFMT-153821 | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 | 2017-05-03 - 18010 - Simon Fernandez-replaced t-stat - Simon Fernandez; 2017-05-03 - 18010 - Thor Millsaps-replaced t-stat - Simon Fernandez | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 2017-05-03 - 18010 - Simon Fernandez-replaced t-stat - Simon Fernandez; 2017-05-03 - 18010 - Thor Millsaps-replaced t-stat - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-05-03 | 154545 | RFMT-153786 | Please repair HVAC mini split unit. | 2017-05-03 - 18010 - Simon Fernandez-checked a/c system for leaks ;tightened valve core recharged unit 1 lbs 8oz unit okay. - Simon Fernandez | Please repair HVAC mini split unit. 2017-05-03 - 18010 - Simon Fernandez-checked a/c system for leaks ;tightened valve core recharged unit 1 lbs 8oz unit okay. - Simon Fernandez | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2
2017-05-03 | 229186 | POLY-119012 | STEVE - Should this be a chargeable? If so, we may need to do an estimate. If Air handler has bad condenser fan (west fan). will not start and run at normal speed. Please evaluate and repair. 42B55N2 | NA | STEVE - Should this be a chargeable? If so, we may need to do an estimate. If Air handler has bad condenser fan (west fan). will not start and run at normal speed. Please evaluate and repair. 42B55N2 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-03 | 229189 | POLY-119009 | REPAIR MAU THAT IS ON TOP OF THE CHILLER MECHANICAL ROOM 4O216EO | NA | REPAIR MAU THAT IS ON TOP OF THE CHILLER MECHANICAL ROOM 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 229218 | POLY-118980 | !! Our a.c. is not working. The house is currently 80 + degrees. There is no cool air coming from the vents. The a.c. has been struggling to keep the house cool for a while and I guess today it decided to give out. Thanks. 4NCEEOE | NA | !! Our a.c. is not working. The house is currently 80 + degrees. There is no cool air coming from the vents. The a.c. has been struggling to keep the house cool for a while and I guess today it decided to give out. Thanks. 4NCEEOE NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-03 | 277 | WEST-110972 | AC unit at Deer Valley Preserve has two shorted compressors and Condenser fan motors Please provide estimate for repairs to Celeste. Emailed estimate. 5/16/17 CMR Estimate approved. DN1 1003 5/17/17 CMR | 2017-05-09 - 18010 - Chad T Ball-Escort vendor to site to quote repair - Thomas Wienand; 2017-05-18 - 18010 - Thomas Wienand-request approved, waiting for scheduling from vendor - Thomas Wienand | AC unit at Deer Valley Preserve has two shorted compressors and Condenser fan motors Please provide estimate for repairs to Celeste. Emailed estimate. 5/16/17 CMR Estimate approved. DN1 1003 5/17/17 CMR 2017-05-09 - 18010 - Chad T Ball-Escort vendor to site to quote repair - Thomas Wienand; 2017-05-18 - 18010 - Thomas Wienand-request approved, waiting for scheduling from vendor - Thomas Wienand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-03 | 249113 | DTPC-119425 | roam campus; Cronkite carpet, BCLS T-stat, Nurse North fan motor | 2017-05-05 - 13000 - Keith Griffin-roam campus; Cronkite carpet, BCLS T-stat, Nurse North fan motor - Keith Griffin | roam campus; Cronkite carpet, BCLS T-stat, Nurse North fan motor 2017-05-05 - 13000 - Keith Griffin-roam campus; Cronkite carpet, BCLS T-stat, Nurse North fan motor - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-03 | 249187 | DTPC-119351 | !! Good morning, the hydraulic unit on the door to the workout room in health south has a seal leaking fluid down the inside of the door. Thanks for investigating! Lisa 42B0B4F | 2017-05-04 - 13070 - Jose Acero-removed old door closer and Installed new closer and hardware - Jose Acero; 2017-05-04 - 13070 - Bruce Pickford-removed old door closer and Installed new closer and hardware - Jose Acero | !! Good morning, the hydraulic unit on the door to the workout room in health south has a seal leaking fluid down the inside of the door. Thanks for investigating! Lisa 42B0B4F 2017-05-04 - 13070 - Jose Acero-removed old door closer and Installed new closer and hardware - Jose Acero; 2017-05-04 - 13070 - Bruce Pickford-removed old door closer and Installed new closer and hardware - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-04 | 14498 | TMPE-235658 | !! The humidity alarm is going off in this room. Local control DX Unit. 4N7EAK5 | 2017-05-09 - 18010 - Jennifer Moyer-Located unit and notified PM crew that unit needed added to the system. Found unit in High Water Alarm on T-stat. Reset unit and observed normal operation. Contacted room occupant Liqing Chen to discuss unit history. Determined that unit was not draining properly and contacted management to proceed. - Jennifer Moyer; 2017-05-16 - 18010 - Jennifer Moyer-Obtain hot work permit,notify lab of hot work, notify fire team, get purchase order number, purchase parts,calculate drain size, dry fit copper, and solder copper. Unit has ice inside, so I will have to let it defrost overnight before I can solder the last joint. - Jennifer Moyer; 2017-05-16 - 18010 - Jennifer Moyer-Blow out condensate line, solder last joint, pick up insulation from CSB, pick up glue from Insulator, attach insulation, clean up. - Jennifer Moyer | !! The humidity alarm is going off in this room. Local control DX Unit. 4N7EAK5 2017-05-09 - 18010 - Jennifer Moyer-Located unit and notified PM crew that unit needed added to the system. Found unit in High Water Alarm on T-stat. Reset unit and observed normal operation. Contacted room occupant Liqing Chen to discuss unit history. Determined that unit was not draining properly and contacted management to proceed. - Jennifer Moyer; 2017-05-16 - 18010 - Jennifer Moyer-Obtain hot work permit,notify lab of hot work, notify fire team, get purchase order number, purchase parts,calculate drain size, dry fit copper, and solder copper. Unit has ice inside, so I will have to let it defrost overnight before I can solder the last joint. - Jennifer Moyer; 2017-05-16 - 18010 - Jennifer Moyer-Blow out condensate line, solder last joint, pick up insulation from CSB, pick up glue from Insulator, attach insulation, clean up. - Jennifer Moyer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-04 | 14513 | TMPE-235643 | A/C is not working in room 140. Thanks, Jim 42C4IO9 | 2017-05-09 - 18290 - Zhi Yu-We Replaced the condenser fan motor, contactor, cap, and check pressure. - Zhi Yu | A/C is not working in room 140. Thanks, Jim 42C4IO9 2017-05-09 - 18290 - Zhi Yu-We Replaced the condenser fan motor, contactor, cap, and check pressure. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-04 | 150226 | RNLD-101075 | Vent fan in the shower room is not working. Also the AC unit in the bedroom does not blow out cool air. 4NI0NCC | NA | Vent fan in the shower room is not working. Also the AC unit in the bedroom does not blow out cool air. 4NI0NCC NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-04 | 154426 | RFMT-153905 | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 | 2017-05-11 - 18010 - Thor has repaired unit and will add his results. - Gregory Stetka; 2017-05-15 - 18010 - Thor Millsaps-Replaced thermostat. (Part on previous WO) - Thor Millsaps | !! This is Pi Phi's chapter room(not sure what room number to put) and our air conditioning is broken! 4NJNOI0 2017-05-11 - 18010 - Thor has repaired unit and will add his results. - Gregory Stetka; 2017-05-15 - 18010 - Thor Millsaps-Replaced thermostat. (Part on previous WO) - Thor Millsaps | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-05-04 | 154427 | RFMT-153904 | !! my air conditioning is broken, it is extremely hot in my room 4NJ96H3 | 2017-05-05 - 18010 - Thor Millsaps-Checked ac. Student said ac has been working fine. - Thor Millsaps | !! my air conditioning is broken, it is extremely hot in my room 4NJ96H3 2017-05-05 - 18010 - Thor Millsaps-Checked ac. Student said ac has been working fine. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-05-04 | 154428 | RFMT-153903 | !! Air conditioner is not working... stuck on 80+ degrees for the past 24 hours. 4NL2M6K | 2017-05-05 - 18010 - Thor Millsaps-Found condenser fan motor not turning. Was able to start motor by hand to provide temporary cooling in room. Drove to Johnstone to pick up new motor (1/4HP, 825RPM, 208-230v). Replaced motor. System up and running. Part entered by Tino. - Thor Millsaps | !! Air conditioner is not working... stuck on 80+ degrees for the past 24 hours. 4NL2M6K 2017-05-05 - 18010 - Thor Millsaps-Found condenser fan motor not turning. Was able to start motor by hand to provide temporary cooling in room. Drove to Johnstone to pick up new motor (1/4HP, 825RPM, 208-230v). Replaced motor. System up and running. Part entered by Tino. - Thor Millsaps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-04 | 208369 | RAMA-100895 | !! Air conditioner is broken 4NF7D82 | NA | !! Air conditioner is broken 4NF7D82 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-05-04 | 229163 | POLY-119035 | leak check and top off with R134A chiller 1, compressor 1 4O216EO | NA | leak check and top off with R134A chiller 1, compressor 1 4O216EO NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-05 | 13372 | TMPE-236784 | ASUHC - Lori P. Description: AC is blowing hot air Dispatch: Roque Garcia Time of Dispatch: 5:06pm Left vm, will try other number ASUHC - Lori P. Spoke with Roque (5:08pm) and he will take care of it. | 2017-05-17 - 18290 - Roque Garcia-5-5-2017 I found the second stage not working, I was able to bypass so the unit would work. 5-8-2017 Returned to replace contactors, reversing solenoids, relays, defrost board, tstat, and rewired the controls and other wiring. Its a 1994 unit - Roque Garcia | ASUHC - Lori P. Description: AC is blowing hot air Dispatch: Roque Garcia Time of Dispatch: 5:06pm Left vm, will try other number ASUHC - Lori P. Spoke with Roque (5:08pm) and he will take care of it. 2017-05-17 - 18290 - Roque Garcia-5-5-2017 I found the second stage not working, I was able to bypass so the unit would work. 5-8-2017 Returned to replace contactors, reversing solenoids, relays, defrost board, tstat, and rewired the controls and other wiring. Its a 1994 unit - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-05 | 14250 | TMPE-235906 | 5/5/17 AC trouble again. The staff room - (109) - is really warm. It's currently reading 80 and won't cool off. Bill to TL502001138 42A042B | 2017-05-13 - 18290 - Robert Dauscher-found air handler for this area to be turned off. the disconnect(light switch) was in the up position, which is actually off per the switch. turned the switch on(down) and clearly marked the switch and unit to prevent this from happening again. - Robert Dauscher | 5/5/17 AC trouble again. The staff room - (109) - is really warm. It's currently reading 80 and won't cool off. Bill to TL502001138 42A042B 2017-05-13 - 18290 - Robert Dauscher-found air handler for this area to be turned off. the disconnect(light switch) was in the up position, which is actually off per the switch. turned the switch on(down) and clearly marked the switch and unit to prevent this from happening again. - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-05 | 14287 | TMPE-235869 | TOWERS B 118 Please send someone to check the a/c. It is blowing out hot air and we have a student working on an experiment. | 2017-05-13 - 18290 - Robert Dauscher-found compressor overheated.. needs to cool down to reset. lock and tag out disconnect will return in am on Saturday - Robert Dauscher; 2017-05-13 - 18290 - Robert Dauscher-returned found compressor rest. unit low on charge. added stop leak to system after unsuccessful leak search. added approx. 3.5 lbs R-22 UNIT IS VERY OLD RECOMMEND REPLACEMENT IF ANY FUTURE REPAIRS ARE NEEDED!!!!!!! - Robert Dauscher | TOWERS B 118 Please send someone to check the a/c. It is blowing out hot air and we have a student working on an experiment. 2017-05-13 - 18290 - Robert Dauscher-found compressor overheated.. needs to cool down to reset. lock and tag out disconnect will return in am on Saturday - Robert Dauscher; 2017-05-13 - 18290 - Robert Dauscher-returned found compressor rest. unit low on charge. added stop leak to system after unsuccessful leak search. added approx. 3.5 lbs R-22 UNIT IS VERY OLD RECOMMEND REPLACEMENT IF ANY FUTURE REPAIRS ARE NEEDED!!!!!!! - Robert Dauscher | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4
2017-05-05 | 14370 | TMPE-235786 | USB There is an AC Duct laying in the ceiling in the NE corner of RM#2464. The occupant is complaining that it is Hot. I found this issue when I opened the ceiling to tye in the lights for the display wall. Thank You, Eddie | 2017-05-12 - 18290 - Carl Karr-Fabricate and install end cap on trunk line. - Carl Karr | USB There is an AC Duct laying in the ceiling in the NE corner of RM#2464. The occupant is complaining that it is Hot. I found this issue when I opened the ceiling to tye in the lights for the display wall. Thank You, Eddie 2017-05-12 - 18290 - Carl Karr-Fabricate and install end cap on trunk line. - Carl Karr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-05-05 | 229134 | POLY-119064 | For Steve Clark to refurbish both swamp coolers at FM11 4O301G4 | 2017-05-17 - 18010 - Steve Clark-UNITS HAVE NO POWER TO THEM AND ARE NOT REPAIRABLE - ORDERED NEW PORTABLE EVAPORATOR COOLER FOR HIS SHOP USE - Steve Clark | For Steve Clark to refurbish both swamp coolers at FM11 4O301G4 2017-05-17 - 18010 - Steve Clark-UNITS HAVE NO POWER TO THEM AND ARE NOT REPAIRABLE - ORDERED NEW PORTABLE EVAPORATOR COOLER FOR HIS SHOP USE - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-05 | 249136 | DTPC-119402 | Look at Fan Coil Units for access for Dave Downing to clean coils. | 2017-05-05 - 18090 - Ross Hossack-Checked access for all 2nd floor fan coil units to see if we could access coils to clean them.Bruce assisted. - Ross Hossack; 2017-05-05 - 18090 - Bruce Pickford-Checked access for all 2nd floor fan coil units to see if we could access coils to clean them.Bruce assisted.Reported findings to Stephen. - Ross Hossack | Look at Fan Coil Units for access for Dave Downing to clean coils. 2017-05-05 - 18090 - Ross Hossack-Checked access for all 2nd floor fan coil units to see if we could access coils to clean them.Bruce assisted. - Ross Hossack; 2017-05-05 - 18090 - Bruce Pickford-Checked access for all 2nd floor fan coil units to see if we could access coils to clean them.Bruce assisted.Reported findings to Stephen. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-06 | 150113 | RNLD-101188 | Student Damage Billing: (no new damages! All of these damages were present at move-in and have yet to be fixed) -Broken outlet cover below a/c unit still present -Small chips on SE wall, low on wall, still present Student: Brianna Inda of room 274 Thank you! 4NK9MD8 | NA | Student Damage Billing: (no new damages! All of these damages were present at move-in and have yet to be fixed) -Broken outlet cover below a/c unit still present -Small chips on SE wall, low on wall, still present Student: Brianna Inda of room 274 Thank you! 4NK9MD8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-05-06 | 150151 | RNLD-101150 | - A 7-inch-dent on the wall under the air conditioner - Broken light bulb - A 7-inch scuff mark on the bathroom door (split by 2) Student Damage Billing 4NMDKI5 | NA | - A 7-inch-dent on the wall under the air conditioner - Broken light bulb - A 7-inch scuff mark on the bathroom door (split by 2) Student Damage Billing 4NMDKI5 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2
2017-05-06 | 150199 | RNLD-101102 | - Multiple brown stain under the air conditioner - Multiple tape residue on the top panel of the drawer unit - Dirty shower stand + Removed shower head Student Damage Billing 4NMDKI5 | NA | - Multiple brown stain under the air conditioner - Multiple tape residue on the top panel of the drawer unit - Dirty shower stand + Removed shower head Student Damage Billing 4NMDKI5 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-06 | 153720 | RFMT-154611 | !! Repeat Request. 15 quarter size duck tape residue spots on walls. Near the air vent, on the left room wall, and on the back wall next to room entrance door. 4O37768 | NA | !! Repeat Request. 15 quarter size duck tape residue spots on walls. Near the air vent, on the left room wall, and on the back wall next to room entrance door. 4O37768 NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-06 | 153843 | RFMT-154488 | !! Repeat Request. AC not working in lounge, please fix 4NK5D1E | 2017-05-09 - 18010 - Simon Fernandez-checked a/c unit found out door unit not operating. no voltage to unit.found breaker tripped possible water getting to breakers? reset unit,checked electric wiring found burnt contactor replaced, also #5 fuse. unit ops checked okay - Simon Fernandez; 2017-05-10 - 18010 - Contacted supervisor regarding possible needed roof repair - Gregory Stetka | !! Repeat Request. AC not working in lounge, please fix 4NK5D1E 2017-05-09 - 18010 - Simon Fernandez-checked a/c unit found out door unit not operating. no voltage to unit.found breaker tripped possible water getting to breakers? reset unit,checked electric wiring found burnt contactor replaced, also #5 fuse. unit ops checked okay - Simon Fernandez; 2017-05-10 - 18010 - Contacted supervisor regarding possible needed roof repair - Gregory Stetka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-06 | 154028 | RFMT-154303 | !! Thermostat does not activate the air conditioning. The AC conditioner pipe in the room is not connected and needs to be checked out. Contact Name: Matt Contact Phone Number: Contact Email: mwdavis3@asu.edu 4NKCFA2 | NA | !! Thermostat does not activate the air conditioning. The AC conditioner pipe in the room is not connected and needs to be checked out. Contact Name: Matt Contact Phone Number: Contact Email: mwdavis3@asu.edu 4NKCFA2 NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-07 | 13286 | TMPE-236870 | ASUHC-Agent: Nolan Ryan Description: Mike cozens called to report a Sewage Ejection Pump in the building ISTB 1. Time of alarm 9:15pm Mike does not service sewage pumps, so he asked me to call the Hvac stadnby (Roque Garcia) and have Roque call him (Mike) to see if there was anything that he (Mike). . . | 2017-05-10 - 23100 - Roque Garcia-Received call and listened to message from 1-855-278-5080. Nolan asked me to call Mike Cozens pertaining to ISTB 1 sewage injector pump #2. I called and spoke with Mike and we both decided to come check out the alarm with ISTB #1. Upon arrival and waited for Mike due to the fact I dont have access into the building. The keys nor badge would not work. Begay showed up and Begay only had access to the front door. Mike, Begay and myself checked the pump and found pump# 2 tripped at the breaker. Reset the breaker and the pump tripped the breaker immediately. Isolated pump #2 and turned on pump #1 and it worked. Reported the findings on 5-8-2017 at the morning meeting and Duane stop by to inquire, Duane said he would take care of pump #2 because it was a new pump. I have asked the the call center to call my cell 480-363-2863. Sounds like the the 1-855-278-5080 doesnt communicate with the call center. - Roque Garcia | ASUHC-Agent: Nolan Ryan Description: Mike cozens called to report a Sewage Ejection Pump in the building ISTB 1. Time of alarm 9:15pm Mike does not service sewage pumps, so he asked me to call the Hvac stadnby (Roque Garcia) and have Roque call him (Mike) to see if there was anything that he (Mike). . . 2017-05-10 - 23100 - Roque Garcia-Received call and listened to message from 1-855-278-5080. Nolan asked me to call Mike Cozens pertaining to ISTB 1 sewage injector pump #2. I called and spoke with Mike and we both decided to come check out the alarm with ISTB #1. Upon arrival and waited for Mike due to the fact I dont have access into the building. The keys nor badge would not work. Begay showed up and Begay only had access to the front door. Mike, Begay and myself checked the pump and found pump# 2 tripped at the breaker. Reset the breaker and the pump tripped the breaker immediately. Isolated pump #2 and turned on pump #1 and it worked. Reported the findings on 5-8-2017 at the morning meeting and Duane stop by to inquire, Duane said he would take care of pump #2 because it was a new pump. I have asked the the call center to call my cell 480-363-2863. Sounds like the the 1-855-278-5080 doesnt communicate with the call center. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-07 | 150075 | RNLD-101226 | Student Damage Billing: -Full room clean -Ethernet port is pushed in -Entry light is out in room -Front edging of dresser is off but still present -Only one Window cvring is present, split between rommate -Shower room vent needs to be fixed -Towel holder is loose next to shower Student: Sri Kena. . . | NA | Student Damage Billing: -Full room clean -Ethernet port is pushed in -Entry light is out in room -Front edging of dresser is off but still present -Only one Window cvring is present, split between rommate -Shower room vent needs to be fixed -Towel holder is loose next to shower Student: Sri Kena. . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-07 | 244 | WEST-111005 | ADA Door Weekly Inspection | 2017-05-09 - xPM-WC-ADADOOR - Tim Jowers-door operators are working properly, the compressor for the east side first floor is in bad shape. will need to be replaced soon. - Tim Jowers | ADA Door Weekly Inspection 2017-05-09 - xPM-WC-ADADOOR - Tim Jowers-door operators are working properly, the compressor for the east side first floor is in bad shape. will need to be replaced soon. - Tim Jowers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13265 | TMPE-236891 | The exhaust fan in the restroom (men) in fifth floor of ERC seems not working. The smell is often pretty bad. The restrooms in other floors are much better than the one in fifth floor. I think it is because of the exhaust fan. 4O152E7 | 2017-05-16 - 18160 - Mauricio Martinez Reyes-Completed. I checked the air flow on the exhaust vents and noticed it was low. I removed the grid on both ducts and noticed that the grid had been partially closed and that these were clogged with dist and debris forming a mud like layer on the inside of the grille. I scrapped it off and washed the grids and reinstalled it. The air flow is much better now. Labor: 1.0 Hrs. Materials:N/A - Mauricio Martinez Reyes | The exhaust fan in the restroom (men) in fifth floor of ERC seems not working. The smell is often pretty bad. The restrooms in other floors are much better than the one in fifth floor. I think it is because of the exhaust fan. 4O152E7 2017-05-16 - 18160 - Mauricio Martinez Reyes-Completed. I checked the air flow on the exhaust vents and noticed it was low. I removed the grid on both ducts and noticed that the grid had been partially closed and that these were clogged with dist and debris forming a mud like layer on the inside of the grille. I scrapped it off and washed the grids and reinstalled it. The air flow is much better now. Labor: 1.0 Hrs. Materials:N/A - Mauricio Martinez Reyes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-05-08 | 13270 | TMPE-236886 | CSB - Air Compressor Alarm HVAC to check compressor at CSB | 2017-05-08 - 18030 - Brian Qualls-Found that PM crew were PMing compressor and did not inform EMS that it would be down. - Brian Qualls | CSB - Air Compressor Alarm HVAC to check compressor at CSB 2017-05-08 - 18030 - Brian Qualls-Found that PM crew were PMing compressor and did not inform EMS that it would be down. - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-08 | 13411 | TMPE-236745 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13412 | TMPE-236744 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13413 | TMPE-236743 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13418 | TMPE-236738 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13419 | TMPE-236737 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13519 | TMPE-236637 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13520 | TMPE-236636 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13523 | TMPE-236633 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13832 | TMPE-236324 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13985 | TMPE-236171 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13986 | TMPE-236170 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13987 | TMPE-236169 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13988 | TMPE-236168 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13989 | TMPE-236167 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13990 | TMPE-236166 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 13991 | TMPE-236165 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-08 | 209415 | RACC-119195 | !! No AC in this room Submitted by 4O077C3 | 2017-05-10 - 10010 - Replaced fan relay - Jim Deal | !! No AC in this room Submitted by 4O077C3 2017-05-10 - 10010 - Replaced fan relay - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-08 | 229094 | POLY-119104 | Repeat Request. 2) the air conditioner is not working. It has been set to 80 and last Friday when it was 97+. The unit would not cool the house lower than 85. The unit ran all day. Then when it was cooling off in the evening, we decided to switch over to the fan to draw in the cooler air. 3) the . . . | NA | Repeat Request. 2) the air conditioner is not working. It has been set to 80 and last Friday when it was 97+. The unit would not cool the house lower than 85. The unit ran all day. Then when it was cooling off in the evening, we decided to switch over to the fan to draw in the cooler air. 3) the . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-08 | 229116 | POLY-119082 | The A/C is not Cooling. Request maintenance. 4O4CAI8 | NA | The A/C is not Cooling. Request maintenance. 4O4CAI8 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-08 | 248970 | DTPC-119568 | go to United Refrigeration to match and order a evap motor | 2017-05-12 - 10000 - Keith Griffin-go to United Refrigeration to match and order a evap nmotor - Keith Griffin; 2017-05-12 - 10000 - Jose Acero-go to United Refrigeration to match and order a evap nmotor - Keith Griffin | go to United Refrigeration to match and order a evap motor 2017-05-12 - 10000 - Keith Griffin-go to United Refrigeration to match and order a evap nmotor - Keith Griffin; 2017-05-12 - 10000 - Jose Acero-go to United Refrigeration to match and order a evap nmotor - Keith Griffin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-08 | 249061 | DTPC-119477 | went to get fan motor to United Refrigeration | 2017-05-08 - 18230 - Jose Acero-Went to United Refrigeration to get fan motor and run capacitor - Jose Acero | went to get fan motor to United Refrigeration 2017-05-08 - 18230 - Jose Acero-Went to United Refrigeration to get fan motor and run capacitor - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-08 | 249075 | DTPC-119463 | Evaporator Coils- Biannual | NA | Evaporator Coils- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-09 | 13019 | TMPE-237137 | Sign shop fix cord on Hermes Vepar; to repair piece of equipment. | 2017-05-15 - 15000 - David Riley-disassembled unit repaired cord and started reassembly. - David Riley; 2017-05-16 - 15000 - David Riley-Reassembled motor and tried to test, Unit does not work. - David Riley; 2017-05-18 - 15000 - David Riley-Send to motor shop please. - David Riley | Sign shop fix cord on Hermes Vepar; to repair piece of equipment. 2017-05-15 - 15000 - David Riley-disassembled unit repaired cord and started reassembly. - David Riley; 2017-05-16 - 15000 - David Riley-Reassembled motor and tried to test, Unit does not work. - David Riley; 2017-05-18 - 15000 - David Riley-Send to motor shop please. - David Riley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-09 | 13048 | TMPE-237108 | !! Repeat Request. Related to Finished WO TEMPE-230125- Water and oil still being pushed though system into building. Need HVAC to come back out and help problem solve to fix. Thank you. 4N354M4 | 2017-05-10 - 18030 - Brian Qualls-Moisture and coalescing filters are saturated. Also float drains are full of gunk. I have the parts on my desk, will repair tomorrow morning 5/11/17. - Brian Qualls; 2017-05-11 - 18030 - Brian Qualls-Changed moisture and coalescing filter elements. Refrigerated air dryer is defective, will order replacement shortly.(Today) - Brian Qualls | !! Repeat Request. Related to Finished WO TEMPE-230125- Water and oil still being pushed though system into building. Need HVAC to come back out and help problem solve to fix. Thank you. 4N354M4 2017-05-10 - 18030 - Brian Qualls-Moisture and coalescing filters are saturated. Also float drains are full of gunk. I have the parts on my desk, will repair tomorrow morning 5/11/17. - Brian Qualls; 2017-05-11 - 18030 - Brian Qualls-Changed moisture and coalescing filter elements. Refrigerated air dryer is defective, will order replacement shortly.(Today) - Brian Qualls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-09 | 13052 | TMPE-237104 | Can I get someone to go to the bakery in the MU. The freezer back there is running at 35 degrees. It's the large walk in | 2017-05-12 - 18180 - Zhi Yu-We diagnose the compressor grounded. KWLA-016E-TAC-100 I spoke to Jim Emmoms, got his permission go ahead for an replacement. - Zhi Yu; 2017-05-15 - 18180 - Zhi Yu-We pick up the compressor from ARS. Also Recovered the freons. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Chad Hargrave-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We vacuum to 500 micron. Charge R404a 12Lbs and adjustment Lpc, HPC. - Zhi Yu | Can I get someone to go to the bakery in the MU. The freezer back there is running at 35 degrees. It's the large walk in 2017-05-12 - 18180 - Zhi Yu-We diagnose the compressor grounded. KWLA-016E-TAC-100 I spoke to Jim Emmoms, got his permission go ahead for an replacement. - Zhi Yu; 2017-05-15 - 18180 - Zhi Yu-We pick up the compressor from ARS. Also Recovered the freons. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Chad Hargrave-We replaced Compressor, drier and sight glass. repipe water loop. - Zhi Yu; 2017-05-17 - 18180 - Zhi Yu-We vacuum to 500 micron. Charge R404a 12Lbs and adjustment Lpc, HPC. - Zhi Yu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-09 | 13077 | TMPE-237079 | circulating pump is off line, for unknown reason, needs to be check for proper operation and returned to operation. Sun Devil Fitness Complex Rm 229M1. any questions see Billy Jackson | NA | circulating pump is off line, for unknown reason, needs to be check for proper operation and returned to operation. Sun Devil Fitness Complex Rm 229M1. any questions see Billy Jackson NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-09 | 13120 | TMPE-237036 | !! We have a leak coming from a drain penetration into room 206. The penetration is for condensate drainage from the AHU/Humidifier on the third floor. Attached pictures showing the leaking pipe above/below. Thanks in advance! -Mike Attachment(s) 42BM6KM | 2017-05-19 - 18010 - Roque Garcia-Its a roof service needed to repair the roof drain that is inside the mechanical room. I asked the Brian to place a roofer on the work order. - Roque Garcia | !! We have a leak coming from a drain penetration into room 206. The penetration is for condensate drainage from the AHU/Humidifier on the third floor. Attached pictures showing the leaking pipe above/below. Thanks in advance! -Mike Attachment(s) 42BM6KM 2017-05-19 - 18010 - Roque Garcia-Its a roof service needed to repair the roof drain that is inside the mechanical room. I asked the Brian to place a roofer on the work order. - Roque Garcia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-09 | 209411 | RACC-119199 | !! Repeat Request. Main filter for the AC was removed and not replaced. Dust keeps collecting from the AC vent in the general area. 4NF9MMM | NA | !! Repeat Request. Main filter for the AC was removed and not replaced. Dust keeps collecting from the AC vent in the general area. 4NF9MMM NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-10 | 12955 | TMPE-237201 | Old main - room 102: The fan to the air conditioner and heater in room 102 has been excessively loud since Friday, May 5th. It is also sporadically making a humming sound in a very high pitch. Please look into this and adjust accordingly as it is very irritating, and a few of our senior guests and . . . | 2017-05-16 - 18010 - Gail Jackson-Supply Registrar is controlled by VAV box; called central plant Mike Cousins; he operated through entire range; very loud at 100% as expected. Mike said to have Dana Aguilar call if gets worse and he would go over. I will take closer look at registrar. - Gail Jackson | Old main - room 102: The fan to the air conditioner and heater in room 102 has been excessively loud since Friday, May 5th. It is also sporadically making a humming sound in a very high pitch. Please look into this and adjust accordingly as it is very irritating, and a few of our senior guests and . . . 2017-05-16 - 18010 - Gail Jackson-Supply Registrar is controlled by VAV box; called central plant Mike Cousins; he operated through entire range; very loud at 100% as expected. Mike said to have Dana Aguilar call if gets worse and he would go over. I will take closer look at registrar. - Gail Jackson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-10 | 12999 | TMPE-237157 | DN - 52U1: The refrigerated air dryer is restricted and not allowing control air to pass through. The dryer has been bypassed to restore bldg control air pressure. Need HVAC to check out and repair air dryer associated with control air compressor Y# 7356 ASAP. 42B213C | NA | DN - 52U1: The refrigerated air dryer is restricted and not allowing control air to pass through. The dryer has been bypassed to restore bldg control air pressure. Need HVAC to check out and repair air dryer associated with control air compressor Y# 7356 ASAP. 42B213C NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-10 | 209376 | RACC-119234 | !! Please route to ACC Maintenance for Villas. Student reports AC not working in first floor living room of VAV L1231. E-mail received states, "I am located in the Vista Villas apartment 1231 and we have a broken AC unit in our lowest level (living room). It is extremely hot in our place and if. . . | 2017-05-12 - 10010 - Replaced contactor - Jim Deal | !! Please route to ACC Maintenance for Villas. Student reports AC not working in first floor living room of VAV L1231. E-mail received states, "I am located in the Vista Villas apartment 1231 and we have a broken AC unit in our lowest level (living room). It is extremely hot in our place and if. . . 2017-05-12 - 10010 - Replaced contactor - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3
2017-05-10 | 249020 | DTPC-119518 | fan blower on heat pump 3-8 | 2017-05-10 - 18230 - Jose Acero-Troubleshoot heat pump Installed new blower motor, run cap and also new fuses - Jose Acero | fan blower on heat pump 3-8 2017-05-10 - 18230 - Jose Acero-Troubleshoot heat pump Installed new blower motor, run cap and also new fuses - Jose Acero | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-11 | 12712 | TMPE-237444 | 4 Swamp coolers in 502 Warehouse need to be repaired. 4O190HG | NA | 4 Swamp coolers in 502 Warehouse need to be repaired. 4O190HG NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-11 | 12724 | TMPE-237432 | Weatherup: AH#2 HVAC added to call, AH#2 wasn't running, EMS went over and reset the unit, 2A & 2B compressors came on 1A & 1B compressor's wont come on Please check 1A & 1B compressors. EMS WO#237410, HVAC WO#237432. Transferred call to HVAC, The AC is not running in the Weatherup Center . . . | 2017-05-12 - 18290 - Robert Ecabert-Chad and I went to Weatherup Center to find out why compressors 1A and 1B were not running,and we found out that compressor 1B was accidently shut off at the switch by someone so we turned it back on and circuit 1B runs just fine. Circuit 1A has shorted windings so I shut the switch off to that circuit and I also disconnected the wires that are attached to the compressor terminals and wire nut them off. New compressors are on order for this unit.05/12/2017 - Robert Ecabert; 2017-05-12 - 18290 - Chad Hargrave-Chad and I went to Weatherup Center to find out why compressors 1A and 1B were not running,and we found out that compressor 1B was accidently shut off at the switch by someone so we turned it back on and circuit 1B runs just fine. Circuit 1A has shorted windings so I shut the switch off to that circuit and I also disconnected the wires that are attached to the compressor terminals and wire nut them off. New compressors are on order for this unit.05/12/2017 - Robert Ecabert | Weatherup: AH#2 HVAC added to call, AH#2 wasn't running, EMS went over and reset the unit, 2A & 2B compressors came on 1A & 1B compressor's wont come on Please check 1A & 1B compressors. EMS WO#237410, HVAC WO#237432. Transferred call to HVAC, The AC is not running in the Weatherup Center . . . 2017-05-12 - 18290 - Robert Ecabert-Chad and I went to Weatherup Center to find out why compressors 1A and 1B were not running,and we found out that compressor 1B was accidently shut off at the switch by someone so we turned it back on and circuit 1B runs just fine. Circuit 1A has shorted windings so I shut the switch off to that circuit and I also disconnected the wires that are attached to the compressor terminals and wire nut them off. New compressors are on order for this unit.05/12/2017 - Robert Ecabert; 2017-05-12 - 18290 - Chad Hargrave-Chad and I went to Weatherup Center to find out why compressors 1A and 1B were not running,and we found out that compressor 1B was accidently shut off at the switch by someone so we turned it back on and circuit 1B runs just fine. Circuit 1A has shorted windings so I shut the switch off to that circuit and I also disconnected the wires that are attached to the compressor terminals and wire nut them off. New compressors are on order for this unit.05/12/2017 - Robert Ecabert | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-11 | 12783 | TMPE-237373 | UCENT C - 303: My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. The thermostat for my office is HP-3-303 I am having yet another issue with the AC in my office. While the temperature in my office is cool, the AC is coming . . . | NA | UCENT C - 303: My name is Karen Engler and I am located in the University Center C Building in the Univ Center Complex. I\\u2019m in Suite 303. The thermostat for my office is HP-3-303 I am having yet another issue with the AC in my office. While the temperature in my office is cool, the AC is coming . . . NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-11 | 12808 | TMPE-237348 | VFD's have been installed in the basement of Cowden for the chilled water pumps and for the motors on the Air Handlers. Billy's crew needs to get information of the units so that they can label the units and to put in there data base. This is both Mech rooms 8-81 42B2H2C | NA | VFD's have been installed in the basement of Cowden for the chilled water pumps and for the motors on the Air Handlers. Billy's crew needs to get information of the units so that they can label the units and to put in there data base. This is both Mech rooms 8-81 42B2H2C NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-11 | 209366 | RACC-119244 | !! Air Conditioning is leaking water all over the floor and the a/c keeps resetting itself. *****URGENT THIS NEED FIXING IMMEDIATELY ***** | 2017-05-12 - 10010 - Cleared condensation line for AC unit - Jim Deal | !! Air Conditioning is leaking water all over the floor and the a/c keeps resetting itself. *****URGENT THIS NEED FIXING IMMEDIATELY ***** 2017-05-12 - 10010 - Cleared condensation line for AC unit - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-11 | 249001 | DTPC-119537 | For Two Modine Unit Fan/Motor Assemblies from Sigler for Spares. | 2017-05-12 - 18230 - Ross Hossack-Ordered motors. - Ross Hossack | For Two Modine Unit Fan/Motor Assemblies from Sigler for Spares. 2017-05-12 - 18230 - Ross Hossack-Ordered motors. - Ross Hossack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-12 | 12573 | TMPE-237583 | LSC, room 326, Research Lab Hot Loss of control air due to air leak inside an abatement area, no thermostat control. Please create a MWO for HVAC to install a portable AC unit until repairs can be made. 42DIM5O | NA | LSC, room 326, Research Lab Hot Loss of control air due to air leak inside an abatement area, no thermostat control. Please create a MWO for HVAC to install a portable AC unit until repairs can be made. 42DIM5O NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-12 | 12581 | TMPE-237575 | Ac to pay for broken keys from HVAC Tech | NA | Ac to pay for broken keys from HVAC Tech NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-05-12 | 12584 | TMPE-237572 | !! Last week, we discovered that our Manitowoc ice machine was not producing ice. Pro Star Services, the company that services our machines, dispatched a technician to diagnose the problem. He suggested it was a fan motor. After requesting the fan motor and installing it, the issue was not resolved.. . . | 2017-05-17 - 18210 - Customer called in to cancel work order - Amanda Thomas | !! Last week, we discovered that our Manitowoc ice machine was not producing ice. Pro Star Services, the company that services our machines, dispatched a technician to diagnose the problem. He suggested it was a fan motor. After requesting the fan motor and installing it, the issue was not resolved.. . . 2017-05-17 - 18210 - Customer called in to cancel work order - Amanda Thomas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-12 | 12589 | TMPE-237567 | Central Plant - add oil to correct low sump level condition on chiller 10 | 2017-05-12 - 30010 - Kevin Graves-Work is complete. - Lisa Anderson | Central Plant - add oil to correct low sump level condition on chiller 10 2017-05-12 - 30010 - Kevin Graves-Work is complete. - Lisa Anderson | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-13 | 11973 | TMPE-238183 | LSC 326 HC-Sofia Robert needed a ticket create for him installing a portable A/C unit For freezers in life sciences due to construction. Dispatched: Robert Daucher Time: 4:44 | NA | LSC 326 HC-Sofia Robert needed a ticket create for him installing a portable A/C unit For freezers in life sciences due to construction. Dispatched: Robert Daucher Time: 4:44 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-13 | 248 | WEST-111001 | Air Compressor - Monthly Maintenance | NA | Air Compressor - Monthly Maintenance NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-13 | 208362 | RAMA-100902 | !! Thermostat not blowing cold air for air conditioning. 4NF0LME | NA | !! Thermostat not blowing cold air for air conditioning. 4NF0LME NA | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-13 | 209358 | RACC-119252 | !! Approximately one hour before this submission, part of the apartment unit lost power, specifically the two bedrooms and bathrooms as well as the kitchen refrigerator. Living room lights, air conditioning, and other appliances seem to be working properly. Called front desk at 12:40AM for assistanc. . . | NA | !! Approximately one hour before this submission, part of the apartment unit lost power, specifically the two bedrooms and bathrooms as well as the kitchen refrigerator. Living room lights, air conditioning, and other appliances seem to be working properly. Called front desk at 12:40AM for assistanc. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-13 | 209359 | RACC-119251 | !! The air conditioning unit isn't working properly...the whole apartment has been at 80+ degrees with no sign of relenting. This is in apartment 2017 of Vista building C. Contact Name: Contact Phone Number: 4246750851 Contact Email: 4NJAMEO | 2017-05-15 - 10010 - Changed out capacitor, and placed super booster-Richard 5/13/17 - Jim Deal | !! The air conditioning unit isn't working properly...the whole apartment has been at 80+ degrees with no sign of relenting. This is in apartment 2017 of Vista building C. Contact Name: Contact Phone Number: 4246750851 Contact Email: 4NJAMEO 2017-05-15 - 10010 - Changed out capacitor, and placed super booster-Richard 5/13/17 - Jim Deal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-15 | 11886 | TMPE-238270 | Please put a new work order in the queue for the HVAC Shop to pick up a new Manitowoc Ice Machine at the main receiving dock and install it in LSE S-62 (when it comes in ~ expected week of 05.29.17 but they may need to purchase an inline filter system or new filters in advance), All charges for thi. . . | NA | Please put a new work order in the queue for the HVAC Shop to pick up a new Manitowoc Ice Machine at the main receiving dock and install it in LSE S-62 (when it comes in ~ expected week of 05.29.17 but they may need to purchase an inline filter system or new filters in advance), All charges for thi. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-15 | 11955 | TMPE-238201 | Bookstore - Starbucks: Will you have someone remove the swinging door at the Starbucks Bookstore so we can get a 2 door cooler out of that space | NA | Bookstore - Starbucks: Will you have someone remove the swinging door at the Starbucks Bookstore so we can get a 2 door cooler out of that space NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-15 | 12016 | TMPE-238140 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12017 | TMPE-238139 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12083 | TMPE-238073 | Air Handler-Biannual | 2017-05-19 - xPM-0300.03-B - Matthew Smith-Washed the condenser and checked the capacitors. Inspected the unit and discovered that it had ice on it up to the compressors. Checked the evaporative section and found that 3/4 of the evaporator coil was covered in ice. Defrosted the coil and restarted the unit. Troubleshot why coil had ice on it and found the probable cause to be a refrigerant issue. Spoke with James about the coil being iced over and discovered that this was the second time it happened in the past month. Found that work order was still open for the last time it happened. Submitted the information to my supervisor who then passed it on to the supervisor of the HVAC Shop. - Matthew Smith | Air Handler-Biannual 2017-05-19 - xPM-0300.03-B - Matthew Smith-Washed the condenser and checked the capacitors. Inspected the unit and discovered that it had ice on it up to the compressors. Checked the evaporative section and found that 3/4 of the evaporator coil was covered in ice. Defrosted the coil and restarted the unit. Troubleshot why coil had ice on it and found the probable cause to be a refrigerant issue. Spoke with James about the coil being iced over and discovered that this was the second time it happened in the past month. Found that work order was still open for the last time it happened. Submitted the information to my supervisor who then passed it on to the supervisor of the HVAC Shop. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
2017-05-15 | 12169 | TMPE-237987 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12175 | TMPE-237981 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12176 | TMPE-237980 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12177 | TMPE-237979 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12178 | TMPE-237978 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12179 | TMPE-237977 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12180 | TMPE-237976 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12181 | TMPE-237975 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12182 | TMPE-237974 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12183 | TMPE-237973 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12184 | TMPE-237972 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12185 | TMPE-237971 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-15 | 12225 | TMPE-237931 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-15 | 12279 | TMPE-237877 | Air Handler-Biannual | 2017-05-18 - xPM-0300.03-B - Matthew Smith-Changed the belt and greased the shaft bearings on the on the indoor blower. Inspected the unit and discovered that 3/4 of the evaporator coil was covered in ice. Defrosted the coil and restarted the unit. Troubleshot why coil had ice on it and found the probable cause to be a refrigerant issue. Spoke with James about the coil being iced over and discovered that this was the second time it happened in the past month. Found that work order was still open for the last time it happened. Submitted the information to my supervisor who then passed it on to the supervisor of the HVAC Shop. - Matthew Smith | Air Handler-Biannual 2017-05-18 - xPM-0300.03-B - Matthew Smith-Changed the belt and greased the shaft bearings on the on the indoor blower. Inspected the unit and discovered that 3/4 of the evaporator coil was covered in ice. Defrosted the coil and restarted the unit. Troubleshot why coil had ice on it and found the probable cause to be a refrigerant issue. Spoke with James about the coil being iced over and discovered that this was the second time it happened in the past month. Found that work order was still open for the last time it happened. Submitted the information to my supervisor who then passed it on to the supervisor of the HVAC Shop. - Matthew Smith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-05-15 | 12331 | TMPE-237825 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-15 | 12332 | TMPE-237824 | Evaporative Cooler- Biannual | NA | Evaporative Cooler- Biannual NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-15 | 228775 | POLY-119423 | SERVICE BOTH UNITS THAT SERVE THE GYM 4O216EO | 2017-05-17 - 18010 - Allan Blair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Suresh Nair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Darusman Amin-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Esli Arvizo-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Allan Blair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Darusman Amin-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark | SERVICE BOTH UNITS THAT SERVE THE GYM 4O216EO 2017-05-17 - 18010 - Allan Blair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Suresh Nair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Darusman Amin-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Esli Arvizo-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Allan Blair-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark; 2017-05-17 - 18010 - Darusman Amin-CHECKED BOTH UNITS FOR COOLING AND HEATING - REPLACED AIR FILTERS - Steve Clark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-16 | 11738 | TMPE-238418 | USB need WO for Robert the auto mechanic: to PM/repair 2 portable generators Honda 3500 Honda 3000 | NA | USB need WO for Robert the auto mechanic: to PM/repair 2 portable generators Honda 3500 Honda 3000 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-16 | 11755 | TMPE-238401 | ADD AC shop: to look at the motor - David Riley from EL shop is the contact Sign shop fix cord on Hermes Vepar; to repair piece of equipment. | NA | ADD AC shop: to look at the motor - David Riley from EL shop is the contact Sign shop fix cord on Hermes Vepar; to repair piece of equipment. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-16 | 209329 | RACC-119281 | !! Air conditioning unit leaking. Please inspect. 4NG4NMF | NA | !! Air conditioning unit leaking. Please inspect. 4NG4NMF NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-17 | 44 | WEST-111205 | There is a Simplex duct detector alarm issue in this room. | 2017-05-18 - 30000 - David Valentine-assist Ron - David Valentine; 2017-05-18 - 30000 - Ronald Chaffee-trouble shooting duct detector in room 246 - Ronald Chaffee; 2017-05-18 - 30000 - Ronald Chaffee-Removed detector and blew out dust, still in trouble. Replaced detector with new detector, still in trouble. Will call for service from Simplex. - Ronald Chaffee; 2017-05-18 - 30000 - Ronald Chaffee-Assisted Simplex tech with repair of duct detector. After checking the test switch tech replaced the printed circuit board. Tech also found trouble in L1-70U1 fan room on a separate trouble. - Ronald Chaffee | There is a Simplex duct detector alarm issue in this room. 2017-05-18 - 30000 - David Valentine-assist Ron - David Valentine; 2017-05-18 - 30000 - Ronald Chaffee-trouble shooting duct detector in room 246 - Ronald Chaffee; 2017-05-18 - 30000 - Ronald Chaffee-Removed detector and blew out dust, still in trouble. Replaced detector with new detector, still in trouble. Will call for service from Simplex. - Ronald Chaffee; 2017-05-18 - 30000 - Ronald Chaffee-Assisted Simplex tech with repair of duct detector. After checking the test switch tech replaced the printed circuit board. Tech also found trouble in L1-70U1 fan room on a separate trouble. - Ronald Chaffee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6
2017-05-17 | 11516 | TMPE-238640 | 5/17/17 Fan coil above ceiling in PSF74 is receiving power but fan is not turning. Motor is hot. I turned off the switch on the outside of the unit for now. This FCU needs to be operational to support a research instrument in the room that produces a lot of heat, building A/C does not appear to . . . | NA | 5/17/17 Fan coil above ceiling in PSF74 is receiving power but fan is not turning. Motor is hot. I turned off the switch on the outside of the unit for now. This FCU needs to be operational to support a research instrument in the room that produces a lot of heat, building A/C does not appear to . . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-05-17 | 11568 | TMPE-238588 | DISCVRY EQ Room Chilled water unit Y-00372 has a high amp draw, and bad bearings. Please fix. Thank you. | NA | DISCVRY EQ Room Chilled water unit Y-00372 has a high amp draw, and bad bearings. Please fix. Thank you. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-17 | 11594 | TMPE-238562 | PSB At least the 1st and second floors are without compressed air | 2017-05-17 - 18030 - Called out to Steve - Amanda Thomas; 2017-05-17 - 18030 - Derek Gittings-one has oil leak restarted other compressor. - Derek Gittings | PSB At least the 1st and second floors are without compressed air 2017-05-17 - 18030 - Called out to Steve - Amanda Thomas; 2017-05-17 - 18030 - Derek Gittings-one has oil leak restarted other compressor. - Derek Gittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-17 | 11612 | TMPE-238544 | LSC L2-74 !! Please initiate a work order for HVAC to thoroughly clean the ductwork and air vents in LSC L2-74 by end-of-day on Friday, 05/19, in preparation for installation of a new highly sensitive laser scope arriving on Monday, 10/22. If billable, all charges for this request may be billed . . . | NA | LSC L2-74 !! Please initiate a work order for HVAC to thoroughly clean the ductwork and air vents in LSC L2-74 by end-of-day on Friday, 05/19, in preparation for installation of a new highly sensitive laser scope arriving on Monday, 10/22. If billable, all charges for this request may be billed . . . NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2
2017-05-17 | 11628 | TMPE-238528 | UCENT B - 110A: Need HVAC to see why compressor is not coming on - the unit is located in room 108. Also a piece of duct work had fallen down and needs to be secured - Mike placed it back in place but he figures it will not hold for long. please contact the customer Lisa at 5-5511 when completed. | NA | UCENT B - 110A: Need HVAC to see why compressor is not coming on - the unit is located in room 108. Also a piece of duct work had fallen down and needs to be secured - Mike placed it back in place but he figures it will not hold for long. please contact the customer Lisa at 5-5511 when completed. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-05-17 | 11667 | TMPE-238489 | Need tech assist-Fire crew-disable smoke alarm LSD 102 !! Environmental chamber 102D is unable to cool. Could HVAC shop or someone familiar with these units take a look? This is a restricted access area, please call me (Mike 480-227-3476) if access is needed. Thanks! Contact Name. . . | 2017-05-18 - 17000 - Kevin Cunningham-Re-enable duct detector after ac shop worked in area..5hrs, 5/18/2017 - Kevin Cunningham | Need tech assist-Fire crew-disable smoke alarm LSD 102 !! Environmental chamber 102D is unable to cool. Could HVAC shop or someone familiar with these units take a look? This is a restricted access area, please call me (Mike 480-227-3476) if access is needed. Thanks! Contact Name. . . 2017-05-18 - 17000 - Kevin Cunningham-Re-enable duct detector after ac shop worked in area..5hrs, 5/18/2017 - Kevin Cunningham | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3
2017-05-17 | 45 | WEST-111204 | replace watchkeeper relays with sq d lighting contactors in nw parking lot cabinet. rr. | NA | replace watchkeeper relays with sq d lighting contactors in nw parking lot cabinet. rr. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2017-05-17 | 209325 | RACC-119285 | Broken A/C 4NOL044 | NA | Broken A/C 4NOL044 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
2017-05-17 | 248791 | DTPC-119747 | Change oil in air compressor. | 2017-05-17 - 18030 - Robert Bartels-Change oil in air compressor. - Robert Bartels | Change oil in air compressor. 2017-05-17 - 18030 - Robert Bartels-Change oil in air compressor. - Robert Bartels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-18 | 11398 | TMPE-238758 | ASUHC: Amy Rideout-Major Description of issue: AC Machine is not working at the Phoenix Municipal Stadium in the umpires locker room. AC Machine is set to 74 degrees and is pumping out to 81 degrees. Dispatched to: Robert Zaller, Robert said EMS did not handle Phoenix Municipal. Dispatched then to. . . | 2017-05-19 - 18290 - Roque Garcia-Check operation of air conditioner for this area. Found broken wire on outdoor motor. Replace wire and check operation. Unit is cooling properly. - Steve Palombo | ASUHC: Amy Rideout-Major Description of issue: AC Machine is not working at the Phoenix Municipal Stadium in the umpires locker room. AC Machine is set to 74 degrees and is pumping out to 81 degrees. Dispatched to: Robert Zaller, Robert said EMS did not handle Phoenix Municipal. Dispatched then to. . . 2017-05-19 - 18290 - Roque Garcia-Check operation of air conditioner for this area. Found broken wire on outdoor motor. Replace wire and check operation. Unit is cooling properly. - Steve Palombo | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 6
2017-05-18 | 11499 | TMPE-238657 | PSE E7 !! 5/18/17 Air compressor Y-9094 is in alarm (indicates overload alarm, not sure what that means) and not operational, remaining air compressor is having trouble keeping up and air pressure is slightly below normal. These two compressors serve all of the Physical Sciences complex other t. . . | NA | PSE E7 !! 5/18/17 Air compressor Y-9094 is in alarm (indicates overload alarm, not sure what that means) and not operational, remaining air compressor is having trouble keeping up and air pressure is slightly below normal. These two compressors serve all of the Physical Sciences complex other t. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-19 | 11271 | TMPE-238885 | PEW Roof - Newly installed evaporative cooler leaking water from inlet; all of these were installed April 2017, and leaking unit is at the SEC. Contact BT Eduardo with any questions: 480-825-9045 4O705G9 | NA | PEW Roof - Newly installed evaporative cooler leaking water from inlet; all of these were installed April 2017, and leaking unit is at the SEC. Contact BT Eduardo with any questions: 480-825-9045 4O705G9 NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
2017-05-19 | 11325 | TMPE-238831 | : LSC L2-45 Details: water chiller in utility room L2-45 has some sort of problem--unit kept blowing circuit breaker last week so breaker amperage was increased, now compressor is shutting down and causing unit to overheat. Please request HVAC for evaluation. I would appreciate having them contact m. . . | NA | : LSC L2-45 Details: water chiller in utility room L2-45 has some sort of problem--unit kept blowing circuit breaker last week so breaker amperage was increased, now compressor is shutting down and causing unit to overheat. Please request HVAC for evaluation. I would appreciate having them contact m. . . NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5
2017-05-19 | 11375 | TMPE-238781 | Hayden South - 142: The Air handler turns on but motor is not running. | NA | Hayden South - 142: The Air handler turns on but motor is not running. NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-19 | 248765 | DTPC-119773 | UCent 4th Fl WRR - The 3 soap dispensers sitting on the counter are not good. If these need to be in here, they need to be checked. These are brown and smell bad. Please replace with new soap or new dispensers. | 2017-05-19 - 14000 - We replaced the dispensers with the new product. Now it is dispensing properly. - Shiran Halpe | UCent 4th Fl WRR - The 3 soap dispensers sitting on the counter are not good. If these need to be in here, they need to be checked. These are brown and smell bad. Please replace with new soap or new dispensers. 2017-05-19 - 14000 - We replaced the dispensers with the new product. Now it is dispensing properly. - Shiran Halpe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
2017-05-22 | 12055 | TMPE-238101 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-22 | 12170 | TMPE-237986 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-22 | 12171 | TMPE-237985 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-22 | 12172 | TMPE-237984 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-22 | 12173 | TMPE-237983 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-22 | 12174 | TMPE-237982 | Air Compressor-Quarterly | NA | Air Compressor-Quarterly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2017-05-23 | 27 | WEST-111222 | Portable Generator Maintenance-Monthly | NA | Portable Generator Maintenance-Monthly NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
2017-11-12 | 49724 | TMPE-200433 | MWO PE West: Cindy Luna 11/12/2016 12:40 - Caller said that the basketball gym in PE West is too hot and there will be an event until 4:30pm today. 12:43pm - Dispatched Mike Cozens @ 480-330-3235. Update 1:03pm - Mike Cozens called in advised to have HVAC dispatched and to have them call him be. . . | 2016-11-18 - 18290 - Robert Dauscher-Found all 8 swamp coolers shut down improperly for the season. disconnects turned off on most, water turned off on all. pumps not unplugged, most of which were dead. was able to get 3 units running after running for parts. All other units not able to run. ALL UNITS NEED REPLACED! Gave Steve P. info for replacing units. - Robert Dauscher | MWO PE West: Cindy Luna 11/12/2016 12:40 - Caller said that the basketball gym in PE West is too hot and there will be an event until 4:30pm today. 12:43pm - Dispatched Mike Cozens @ 480-330-3235. Update 1:03pm - Mike Cozens called in advised to have HVAC dispatched and to have them call him be. . . 2016-11-18 - 18290 - Robert Dauscher-Found all 8 swamp coolers shut down improperly for the season. disconnects turned off on most, water turned off on all. pumps not unplugged, most of which were dead. was able to get 3 units running after running for parts. All other units not able to run. ALL UNITS NEED REPLACED! Gave Steve P. info for replacing units. - Robert Dauscher | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3